2017-12-03 01:00 | 307.2784 | 0.91587 |  | 322.6622 | 0.056876 | 0 | 0 | 0.11375 | 331.7293 | 0.076543 | 0 | 0 | 0.15309 | 339.1479 | 0.092633 | 0 | 0 | 0.18527 | 339.4227 | 0.093229 | 0 | 0 | 0.18646 | 339.6058 | 0.093627 | 0 | 0 | 0.18725 | 339.8806 | 0.094223 | 0 | 0 | 0.18845 | 340.1554 | 0.094819 | 0 | 0 | 0.18964 | 340.4301 | 0.095415 | 0 | 0 | 0.19083 | 340.7965 | 0.096209 | 0 | 0 | 0.19242 | 341.0712 | 0.096805 | 0 | 0 | 0.19361 | 341.2544 | 0.097202 | 0 | 0 | 0.1944 | 341.5292 | 0.097798 | 0 | 0 | 0.1956 | 341.7123 | 0.098196 | 0 | 0 | 0.19639 | 341.9871 | 0.098792 | 0 | 0 | 0.19758 | 342.2619 | 0.099388 | 0 | 0 | 0.19878 | 342.445 | 0.099785 | 0 | 0 | 0.19957 | 342.7198 | 0.10038 | 0 | 0 | 0.20076 | 342.9946 | 0.10098 | 0 | 0 | 0.20195 | 343.0861 | 0.10118 | 0 | 0 | 0.20235 | 343.3609 | 0.10177 | 0 | 0 | 0.20354 | 343.6357 | 0.10237 | 0 | 0 | 0.20473 | 343.8188 | 0.10276 | 0 | 0 | 0.20553 | 344.0936 | 0.10336 | 0 | 0 | 0.20672 | 344.2768 | 0.10376 | 0 | 0 | 0.20752 | 344.46 | 0.10416 | 0 | 0 | 0.20831
2017-12-03 02:00 | 307.327 | 0.91602 |  | 322.7133 | 0.056987 | 0 | 0 | 0.11397 | 331.7819 | 0.076657 | 0 | 0 | 0.15331 | 339.2016 | 0.09275 | 0 | 0 | 0.1855 | 339.4764 | 0.093346 | 0 | 0 | 0.18669 | 339.6596 | 0.093743 | 0 | 0 | 0.18749 | 339.9344 | 0.094339 | 0 | 0 | 0.18868 | 340.2092 | 0.094935 | 0 | 0 | 0.18987 | 340.484 | 0.095532 | 0 | 0 | 0.19106 | 340.8505 | 0.096326 | 0 | 0 | 0.19265 | 341.1253 | 0.096922 | 0 | 0 | 0.19384 | 341.3085 | 0.09732 | 0 | 0 | 0.19464 | 341.5833 | 0.097916 | 0 | 0 | 0.19583 | 341.7665 | 0.098313 | 0 | 0 | 0.19663 | 342.0413 | 0.098909 | 0 | 0 | 0.19782 | 342.3161 | 0.099505 | 0 | 0 | 0.19901 | 342.4993 | 0.099903 | 0 | 0 | 0.19981 | 342.7741 | 0.1005 | 0 | 0 | 0.201 | 343.0489 | 0.10109 | 0 | 0 | 0.20219 | 343.1405 | 0.10129 | 0 | 0 | 0.20259 | 343.4153 | 0.10189 | 0 | 0 | 0.20378 | 343.6901 | 0.10249 | 0 | 0 | 0.20497 | 343.8733 | 0.10288 | 0 | 0 | 0.20577 | 344.1481 | 0.10348 | 0 | 0 | 0.20696 | 344.3313 | 0.10388 | 0 | 0 | 0.20775 | 344.5145 | 0.10427 | 0 | 0 | 0.20855
2017-12-03 03:00 | 302.3698 | 0.90124 |  | 317.5079 | 0.045696 | 0 | 0 | 0.091392 | 326.4302 | 0.065049 | 0 | 0 | 0.1301 | 333.7302 | 0.080883 | 0 | 0 | 0.16177 | 334.0006 | 0.081469 | 0 | 0 | 0.16294 | 334.1809 | 0.08186 | 0 | 0 | 0.16372 | 334.4512 | 0.082446 | 0 | 0 | 0.16489 | 334.7216 | 0.083033 | 0 | 0 | 0.16607 | 334.992 | 0.083619 | 0 | 0 | 0.16724 | 335.3525 | 0.084401 | 0 | 0 | 0.1688 | 335.6229 | 0.084988 | 0 | 0 | 0.16998 | 335.8031 | 0.085379 | 0 | 0 | 0.17076 | 336.0735 | 0.085965 | 0 | 0 | 0.17193 | 336.2537 | 0.086356 | 0 | 0 | 0.17271 | 336.5241 | 0.086942 | 0 | 0 | 0.17388 | 336.7945 | 0.087529 | 0 | 0 | 0.17506 | 336.9747 | 0.08792 | 0 | 0 | 0.17584 | 337.2451 | 0.088506 | 0 | 0 | 0.17701 | 337.5155 | 0.089093 | 0 | 0 | 0.17819 | 337.6056 | 0.089288 | 0 | 0 | 0.17858 | 337.876 | 0.089875 | 0 | 0 | 0.17975 | 338.1463 | 0.090461 | 0 | 0 | 0.18092 | 338.3266 | 0.090852 | 0 | 0 | 0.1817 | 338.597 | 0.091438 | 0 | 0 | 0.18288 | 338.7772 | 0.091829 | 0 | 0 | 0.18366 | 338.9575 | 0.09222 | 0 | 0 | 0.18444
2017-12-03 04:00 | 310.5781 | 0.92571 |  | 326.1271 | 0.064391 | 0 | 0 | 0.12878 | 335.2916 | 0.084269 | 0 | 0 | 0.16854 | 342.7899 | 0.10053 | 0 | 0 | 0.20107 | 343.0676 | 0.10114 | 0 | 0 | 0.20227 | 343.2527 | 0.10154 | 0 | 0 | 0.20307 | 343.5305 | 0.10214 | 0 | 0 | 0.20428 | 343.8082 | 0.10274 | 0 | 0 | 0.20548 | 344.0859 | 0.10334 | 0 | 0 | 0.20669 | 344.4562 | 0.10415 | 0 | 0 | 0.20829 | 344.7339 | 0.10475 | 0 | 0 | 0.2095 | 344.919 | 0.10515 | 0 | 0 | 0.2103 | 345.1967 | 0.10575 | 0 | 0 | 0.21151 | 345.3819 | 0.10615 | 0 | 0 | 0.21231 | 345.6596 | 0.10676 | 0 | 0 | 0.21351 | 345.9373 | 0.10736 | 0 | 0 | 0.21472 | 346.1224 | 0.10776 | 0 | 0 | 0.21552 | 346.4002 | 0.10836 | 0 | 0 | 0.21673 | 346.6779 | 0.10897 | 0 | 0 | 0.21793 | 346.7704 | 0.10917 | 0 | 0 | 0.21833 | 347.0481 | 0.10977 | 0 | 0 | 0.21954 | 347.3259 | 0.11037 | 0 | 0 | 0.22074 | 347.511 | 0.11077 | 0 | 0 | 0.22155 | 347.7887 | 0.11138 | 0 | 0 | 0.22275 | 347.9739 | 0.11178 | 0 | 0 | 0.22355 | 348.159 | 0.11218 | 0 | 0 | 0.22436
2017-12-03 05:00 | 309.9657 | 0.92388 |  | 325.484 | 0.062996 | 0 | 0 | 0.12599 | 334.6304 | 0.082835 | 0 | 0 | 0.16567 | 342.1139 | 0.099067 | 0 | 0 | 0.19813 | 342.3911 | 0.099668 | 0 | 0 | 0.19934 | 342.5758 | 0.10007 | 0 | 0 | 0.20014 | 342.853 | 0.10067 | 0 | 0 | 0.20134 | 343.1302 | 0.10127 | 0 | 0 | 0.20254 | 343.4073 | 0.10187 | 0 | 0 | 0.20374 | 343.7769 | 0.10267 | 0 | 0 | 0.20535 | 344.0541 | 0.10327 | 0 | 0 | 0.20655 | 344.2388 | 0.10368 | 0 | 0 | 0.20735 | 344.516 | 0.10428 | 0 | 0 | 0.20855 | 344.7008 | 0.10468 | 0 | 0 | 0.20936 | 344.9779 | 0.10528 | 0 | 0 | 0.21056 | 345.2551 | 0.10588 | 0 | 0 | 0.21176 | 345.4399 | 0.10628 | 0 | 0 | 0.21256 | 345.717 | 0.10688 | 0 | 0 | 0.21376 | 345.9942 | 0.10748 | 0 | 0 | 0.21497 | 346.0866 | 0.10768 | 0 | 0 | 0.21537 | 346.3638 | 0.10828 | 0 | 0 | 0.21657 | 346.6409 | 0.10889 | 0 | 0 | 0.21777 | 346.8257 | 0.10929 | 0 | 0 | 0.21857 | 347.1029 | 0.10989 | 0 | 0 | 0.21978 | 347.2876 | 0.11029 | 0 | 0 | 0.22058 | 347.4724 | 0.11069 | 0 | 0 | 0.22138
2017-12-03 06:00 | 304.063 | 0.90629 |  | 319.2858 | 0.049553 | 0 | 0 | 0.099105 | 328.2581 | 0.069013 | 0 | 0 | 0.13803 | 335.599 | 0.084936 | 0 | 0 | 0.16987 | 335.8709 | 0.085526 | 0 | 0 | 0.17105 | 336.0522 | 0.085919 | 0 | 0 | 0.17184 | 336.3241 | 0.086509 | 0 | 0 | 0.17302 | 336.596 | 0.087098 | 0 | 0 | 0.1742 | 336.8679 | 0.087688 | 0 | 0 | 0.17538 | 337.2304 | 0.088474 | 0 | 0 | 0.17695 | 337.5023 | 0.089064 | 0 | 0 | 0.17813 | 337.6835 | 0.089457 | 0 | 0 | 0.17891 | 337.9554 | 0.090047 | 0 | 0 | 0.18009 | 338.1367 | 0.09044 | 0 | 0 | 0.18088 | 338.4085 | 0.09103 | 0 | 0 | 0.18206 | 338.6804 | 0.091619 | 0 | 0 | 0.18324 | 338.8617 | 0.092013 | 0 | 0 | 0.18403 | 339.1336 | 0.092602 | 0 | 0 | 0.1852 | 339.4055 | 0.093192 | 0 | 0 | 0.18638 | 339.4961 | 0.093389 | 0 | 0 | 0.18678 | 339.768 | 0.093978 | 0 | 0 | 0.18796 | 340.0399 | 0.094568 | 0 | 0 | 0.18914 | 340.2211 | 0.094961 | 0 | 0 | 0.18992 | 340.493 | 0.095551 | 0 | 0 | 0.1911 | 340.6743 | 0.095944 | 0 | 0 | 0.19189 | 340.8555 | 0.096337 | 0 | 0 | 0.19267
2017-12-03 07:00 | 311.0396 | 0.92708 |  | 326.6117 | 0.065442 | 0 | 0 | 0.13088 | 335.7898 | 0.08535 | 0 | 0 | 0.1707 | 343.2992 | 0.10164 | 0 | 0 | 0.20328 | 343.5773 | 0.10224 | 0 | 0 | 0.20448 | 343.7627 | 0.10264 | 0 | 0 | 0.20529 | 344.0409 | 0.10325 | 0 | 0 | 0.20649 | 344.319 | 0.10385 | 0 | 0 | 0.2077 | 344.5971 | 0.10445 | 0 | 0 | 0.20891 | 344.968 | 0.10526 | 0 | 0 | 0.21051 | 345.2461 | 0.10586 | 0 | 0 | 0.21172 | 345.4315 | 0.10626 | 0 | 0 | 0.21253 | 345.7096 | 0.10687 | 0 | 0 | 0.21373 | 345.895 | 0.10727 | 0 | 0 | 0.21454 | 346.1732 | 0.10787 | 0 | 0 | 0.21574 | 346.4513 | 0.10847 | 0 | 0 | 0.21695 | 346.6367 | 0.10888 | 0 | 0 | 0.21775 | 346.9148 | 0.10948 | 0 | 0 | 0.21896 | 347.193 | 0.11008 | 0 | 0 | 0.22017 | 347.2857 | 0.11028 | 0 | 0 | 0.22057 | 347.5638 | 0.11089 | 0 | 0 | 0.22178 | 347.8419 | 0.11149 | 0 | 0 | 0.22298 | 348.0273 | 0.11189 | 0 | 0 | 0.22379 | 348.3055 | 0.1125 | 0 | 0 | 0.22499 | 348.4909 | 0.1129 | 0 | 0 | 0.2258 | 348.6763 | 0.1133 | 0 | 0 | 0.2266
2017-12-03 08:00 | 290.3518 | 0.86542 |  | 304.8882 | 0.018324 | 0 | 0 | 0.036648 | 313.4558 | 0.036907 | 0 | 0 | 0.073815 | 320.4658 | 0.052112 | 0 | 0 | 0.10422 | 320.7254 | 0.052675 | 0 | 0 | 0.10535 | 320.8985 | 0.05305 | 0 | 0 | 0.1061 | 321.1581 | 0.053614 | 0 | 0 | 0.10723 | 321.4177 | 0.054177 | 0 | 0 | 0.10835 | 321.6773 | 0.05474 | 0 | 0 | 0.10948 | 322.0235 | 0.055491 | 0 | 0 | 0.11098 | 322.2831 | 0.056054 | 0 | 0 | 0.11211 | 322.4562 | 0.056429 | 0 | 0 | 0.11286 | 322.7159 | 0.056992 | 0 | 0 | 0.11398 | 322.8889 | 0.057368 | 0 | 0 | 0.11474 | 323.1486 | 0.057931 | 0 | 0 | 0.11586 | 323.4082 | 0.058494 | 0 | 0 | 0.11699 | 323.5813 | 0.058869 | 0 | 0 | 0.11774 | 323.8409 | 0.059433 | 0 | 0 | 0.11887 | 324.1005 | 0.059996 | 0 | 0 | 0.11999 | 324.1871 | 0.060183 | 0 | 0 | 0.12037 | 324.4467 | 0.060747 | 0 | 0 | 0.12149 | 324.7063 | 0.06131 | 0 | 0 | 0.12262 | 324.8794 | 0.061685 | 0 | 0 | 0.12337 | 325.139 | 0.062248 | 0 | 0 | 0.1245 | 325.3121 | 0.062624 | 0 | 0 | 0.12525 | 325.4852 | 0.062999 | 0 | 0 | 0.126
2017-12-03 09:00 | 286.0776 | 0.85268 |  | 300.4 | 0.0085893 | 0 | 0 | 0.017179 | 308.8416 | 0.026899 | 0 | 0 | 0.053798 | 315.7483 | 0.04188 | 0 | 0 | 0.083759 | 316.0041 | 0.042435 | 0 | 0 | 0.084869 | 316.1747 | 0.042804 | 0 | 0 | 0.085609 | 316.4305 | 0.043359 | 0 | 0 | 0.086719 | 316.6863 | 0.043914 | 0 | 0 | 0.087828 | 316.9421 | 0.044469 | 0 | 0 | 0.088938 | 317.2831 | 0.045209 | 0 | 0 | 0.090418 | 317.539 | 0.045764 | 0 | 0 | 0.091527 | 317.7095 | 0.046134 | 0 | 0 | 0.092267 | 317.9653 | 0.046688 | 0 | 0 | 0.093377 | 318.1358 | 0.047058 | 0 | 0 | 0.094117 | 318.3916 | 0.047613 | 0 | 0 | 0.095226 | 318.6474 | 0.048168 | 0 | 0 | 0.096336 | 318.818 | 0.048538 | 0 | 0 | 0.097076 | 319.0738 | 0.049093 | 0 | 0 | 0.098185 | 319.3296 | 0.049648 | 0 | 0 | 0.099295 | 319.4149 | 0.049832 | 0 | 0 | 0.099665 | 319.6707 | 0.050387 | 0 | 0 | 0.10077 | 319.9265 | 0.050942 | 0 | 0 | 0.10188 | 320.097 | 0.051312 | 0 | 0 | 0.10262 | 320.3528 | 0.051867 | 0 | 0 | 0.10373 | 320.5233 | 0.052237 | 0 | 0 | 0.10447 | 320.6939 | 0.052607 | 0 | 0 | 0.10521
2017-12-03 10:00 | 273.4262 | 0.81497 |  | 287.1152 | 0 | 0 | 0 | 0 | 295.1835 | 0 | 0 | 0 | 0 | 301.7848 | 0.011593 | 0 | 0 | 0.023186 | 302.0293 | 0.012123 | 0 | 0 | 0.024246 | 302.1923 | 0.012477 | 0 | 0 | 0.024953 | 302.4367 | 0.013007 | 0 | 0 | 0.026014 | 302.6812 | 0.013537 | 0 | 0 | 0.027074 | 302.9257 | 0.014068 | 0 | 0 | 0.028135 | 303.2517 | 0.014775 | 0 | 0 | 0.029549 | 303.4962 | 0.015305 | 0 | 0 | 0.03061 | 303.6592 | 0.015658 | 0 | 0 | 0.031317 | 303.9037 | 0.016189 | 0 | 0 | 0.032378 | 304.0667 | 0.016542 | 0 | 0 | 0.033085 | 304.3112 | 0.017073 | 0 | 0 | 0.034145 | 304.5557 | 0.017603 | 0 | 0 | 0.035206 | 304.7187 | 0.017956 | 0 | 0 | 0.035913 | 304.9632 | 0.018487 | 0 | 0 | 0.036973 | 305.2077 | 0.019017 | 0 | 0 | 0.038034 | 305.2892 | 0.019194 | 0 | 0 | 0.038388 | 305.5336 | 0.019724 | 0 | 0 | 0.039448 | 305.7781 | 0.020254 | 0 | 0 | 0.040509 | 305.9411 | 0.020608 | 0 | 0 | 0.041216 | 306.1856 | 0.021138 | 0 | 0 | 0.042277 | 306.3486 | 0.021492 | 0 | 0 | 0.042984 | 306.5116 | 0.021845 | 0 | 0 | 0.043691
2017-12-03 11:00 | 274.2062 | 0.8173 |  | 287.9342 | 0 | 0 | 0 | 0 | 296.0255 | 0 | 0 | 0 | 0 | 302.6456 | 0.01346 | 0 | 0 | 0.02692 | 302.8908 | 0.013992 | 0 | 0 | 0.027983 | 303.0542 | 0.014346 | 0 | 0 | 0.028693 | 303.2994 | 0.014878 | 0 | 0 | 0.029756 | 303.5446 | 0.01541 | 0 | 0 | 0.03082 | 303.7898 | 0.015942 | 0 | 0 | 0.031883 | 304.1167 | 0.016651 | 0 | 0 | 0.033302 | 304.3619 | 0.017183 | 0 | 0 | 0.034365 | 304.5254 | 0.017537 | 0 | 0 | 0.035074 | 304.7706 | 0.018069 | 0 | 0 | 0.036138 | 304.934 | 0.018424 | 0 | 0 | 0.036847 | 305.1792 | 0.018955 | 0 | 0 | 0.037911 | 305.4244 | 0.019487 | 0 | 0 | 0.038974 | 305.5879 | 0.019842 | 0 | 0 | 0.039683 | 305.8331 | 0.020374 | 0 | 0 | 0.040747 | 306.0782 | 0.020905 | 0 | 0 | 0.041811 | 306.16 | 0.021083 | 0 | 0 | 0.042165 | 306.4052 | 0.021614 | 0 | 0 | 0.043229 | 306.6504 | 0.022146 | 0 | 0 | 0.044293 | 306.8138 | 0.022501 | 0 | 0 | 0.045002 | 307.059 | 0.023033 | 0 | 0 | 0.046065 | 307.2225 | 0.023387 | 0 | 0 | 0.046774 | 307.3859 | 0.023742 | 0 | 0 | 0.047483
2017-12-03 12:00 | 270.8257 | 0.80722 |  | 284.3845 | 0 | 0 | 0 | 0 | 292.376 | 0 | 0 | 0 | 0 | 298.9145 | 0.0053673 | 0 | 0 | 0.010735 | 299.1567 | 0.0058926 | 0 | 0 | 0.011785 | 299.3182 | 0.0062427 | 0 | 0 | 0.012485 | 299.5603 | 0.006768 | 0 | 0 | 0.013536 | 299.8025 | 0.0072932 | 0 | 0 | 0.014586 | 300.0447 | 0.0078185 | 0 | 0 | 0.015637 | 300.3675 | 0.0085189 | 0 | 0 | 0.017038 | 300.6097 | 0.0090441 | 0 | 0 | 0.018088 | 300.7712 | 0.0093943 | 0 | 0 | 0.018789 | 301.0133 | 0.0099195 | 0 | 0 | 0.019839 | 301.1748 | 0.01027 | 0 | 0 | 0.020539 | 301.4169 | 0.010795 | 0 | 0 | 0.02159 | 301.6591 | 0.01132 | 0 | 0 | 0.02264 | 301.8206 | 0.01167 | 0 | 0 | 0.023341 | 302.0627 | 0.012196 | 0 | 0 | 0.024391 | 302.3049 | 0.012721 | 0 | 0 | 0.025442 | 302.3856 | 0.012896 | 0 | 0 | 0.025792 | 302.6278 | 0.013421 | 0 | 0 | 0.026843 | 302.8699 | 0.013947 | 0 | 0 | 0.027893 | 303.0314 | 0.014297 | 0 | 0 | 0.028593 | 303.2736 | 0.014822 | 0 | 0 | 0.029644 | 303.435 | 0.015172 | 0 | 0 | 0.030344 | 303.5964 | 0.015522 | 0 | 0 | 0.031045
2017-12-03 13:00 | 267.6832 | 0.79786 |  | 281.0847 | 0 | 0 | 0 | 0 | 288.9835 | 0 | 0 | 0 | 0 | 295.4461 | 0 | 0 | 0 | 0 | 295.6855 | 0 | 0 | 0 | 0 | 295.8451 | 0 | 0 | 0 | 0 | 296.0844 | 0 | 0 | 0 | 0 | 296.3238 | 0 | 0 | 0 | 0 | 296.5631 | 0.00026709 | 0 | 0 | 0.00053418 | 296.8823 | 0.00095931 | 0 | 0 | 0.0019186 | 297.1216 | 0.0014785 | 0 | 0 | 0.002957 | 297.2812 | 0.0018246 | 0 | 0 | 0.0036492 | 297.5206 | 0.0023438 | 0 | 0 | 0.0046875 | 297.6801 | 0.0026899 | 0 | 0 | 0.0053797 | 297.9195 | 0.003209 | 0 | 0 | 0.0064181 | 298.1589 | 0.0037282 | 0 | 0 | 0.0074564 | 298.3184 | 0.0040743 | 0 | 0 | 0.0081486 | 298.5578 | 0.0045935 | 0 | 0 | 0.0091869 | 298.7971 | 0.0051126 | 0 | 0 | 0.010225 | 298.8769 | 0.0052857 | 0 | 0 | 0.010571 | 299.1163 | 0.0058049 | 0 | 0 | 0.01161 | 299.3556 | 0.006324 | 0 | 0 | 0.012648 | 299.5152 | 0.0066701 | 0 | 0 | 0.01334 | 299.7546 | 0.0071893 | 0 | 0 | 0.014379 | 299.9141 | 0.0075354 | 0 | 0 | 0.015071 | 300.0737 | 0.0078815 | 0 | 0 | 0.015763
2017-12-03 14:00 | 275.5995 | 0.82145 |  | 289.3974 | 0 | 0 | 0 | 0 | 297.5297 | 0.0023636 | 0 | 0 | 0.0047273 | 304.1835 | 0.016796 | 0 | 0 | 0.033591 | 304.4299 | 0.01733 | 0 | 0 | 0.03466 | 304.5942 | 0.017686 | 0 | 0 | 0.035373 | 304.8407 | 0.018221 | 0 | 0 | 0.036442 | 305.0871 | 0.018756 | 0 | 0 | 0.037511 | 305.3335 | 0.01929 | 0 | 0 | 0.03858 | 305.6621 | 0.020003 | 0 | 0 | 0.040005 | 305.9085 | 0.020537 | 0 | 0 | 0.041075 | 306.0728 | 0.020894 | 0 | 0 | 0.041787 | 306.3193 | 0.021428 | 0 | 0 | 0.042856 | 306.4836 | 0.021784 | 0 | 0 | 0.043569 | 306.73 | 0.022319 | 0 | 0 | 0.044638 | 306.9764 | 0.022854 | 0 | 0 | 0.045707 | 307.1407 | 0.02321 | 0 | 0 | 0.04642 | 307.3872 | 0.023744 | 0 | 0 | 0.047489 | 307.6336 | 0.024279 | 0 | 0 | 0.048558 | 307.7157 | 0.024457 | 0 | 0 | 0.048914 | 307.9622 | 0.024992 | 0 | 0 | 0.049983 | 308.2086 | 0.025526 | 0 | 0 | 0.051052 | 308.3729 | 0.025882 | 0 | 0 | 0.051765 | 308.6193 | 0.026417 | 0 | 0 | 0.052834 | 308.7836 | 0.026773 | 0 | 0 | 0.053547 | 308.9479 | 0.02713 | 0 | 0 | 0.054259
2017-12-03 15:00 | 271.9349 | 0.81053 |  | 285.5493 | 0 | 0 | 0 | 0 | 293.5735 | 0 | 0 | 0 | 0 | 300.1388 | 0.0080227 | 0 | 0 | 0.016045 | 300.3819 | 0.0085501 | 0 | 0 | 0.0171 | 300.544 | 0.0089017 | 0 | 0 | 0.017803 | 300.7872 | 0.0094291 | 0 | 0 | 0.018858 | 301.0304 | 0.0099565 | 0 | 0 | 0.019913 | 301.2735 | 0.010484 | 0 | 0 | 0.020968 | 301.5977 | 0.011187 | 0 | 0 | 0.022374 | 301.8409 | 0.011715 | 0 | 0 | 0.023429 | 302.003 | 0.012066 | 0 | 0 | 0.024132 | 302.2462 | 0.012594 | 0 | 0 | 0.025187 | 302.4083 | 0.012945 | 0 | 0 | 0.02589 | 302.6514 | 0.013473 | 0 | 0 | 0.026945 | 302.8946 | 0.014 | 0 | 0 | 0.028 | 303.0567 | 0.014352 | 0 | 0 | 0.028703 | 303.2998 | 0.014879 | 0 | 0 | 0.029758 | 303.543 | 0.015406 | 0 | 0 | 0.030813 | 303.6241 | 0.015582 | 0 | 0 | 0.031164 | 303.8672 | 0.01611 | 0 | 0 | 0.032219 | 304.1104 | 0.016637 | 0 | 0 | 0.033274 | 304.2725 | 0.016989 | 0 | 0 | 0.033977 | 304.5156 | 0.017516 | 0 | 0 | 0.035032 | 304.6777 | 0.017868 | 0 | 0 | 0.035735 | 304.8399 | 0.018219 | 0 | 0 | 0.036439
2017-12-03 16:00 | 263.6551 | 0.78585 |  | 276.8549 | 0 | 0 | 0 | 0 | 284.6348 | 0 | 0 | 0 | 0 | 291.0002 | 0 | 0 | 0 | 0 | 291.236 | 0 | 0 | 0 | 0 | 291.3931 | 0 | 0 | 0 | 0 | 291.6289 | 0 | 0 | 0 | 0 | 291.8646 | 0 | 0 | 0 | 0 | 292.1004 | 0 | 0 | 0 | 0 | 292.4147 | 0 | 0 | 0 | 0 | 292.6505 | 0 | 0 | 0 | 0 | 292.8077 | 0 | 0 | 0 | 0 | 293.0434 | 0 | 0 | 0 | 0 | 293.2006 | 0 | 0 | 0 | 0 | 293.4363 | 0 | 0 | 0 | 0 | 293.6721 | 0 | 0 | 0 | 0 | 293.8293 | 0 | 0 | 0 | 0 | 294.065 | 0 | 0 | 0 | 0 | 294.3008 | 0 | 0 | 0 | 0 | 294.3794 | 0 | 0 | 0 | 0 | 294.6151 | 0 | 0 | 0 | 0 | 294.8509 | 0 | 0 | 0 | 0 | 295.008 | 0 | 0 | 0 | 0 | 295.2438 | 0 | 0 | 0 | 0 | 295.401 | 0 | 0 | 0 | 0 | 295.5581 | 0 | 0 | 0 | 0
2017-12-03 17:00 | 266.9056 | 0.79554 |  | 280.2681 | 0 | 0 | 0 | 0 | 288.144 | 0 | 0 | 0 | 0 | 294.5878 | 0 | 0 | 0 | 0 | 294.8265 | 0 | 0 | 0 | 0 | 294.9856 | 0 | 0 | 0 | 0 | 295.2242 | 0 | 0 | 0 | 0 | 295.4629 | 0 | 0 | 0 | 0 | 295.7016 | 0 | 0 | 0 | 0 | 296.0198 | 0 | 0 | 0 | 0 | 296.2584 | 0 | 0 | 0 | 0 | 296.4176 | 0 | 0 | 0 | 0 | 296.6562 | 0.00046897 | 0 | 0 | 0.00093793 | 296.8153 | 0.00081407 | 0 | 0 | 0.0016281 | 297.054 | 0.0013317 | 0 | 0 | 0.0026635 | 297.2926 | 0.0018494 | 0 | 0 | 0.0036988 | 297.4518 | 0.0021945 | 0 | 0 | 0.004389 | 297.6904 | 0.0027121 | 0 | 0 | 0.0054243 | 297.9291 | 0.0032298 | 0 | 0 | 0.0064596 | 298.0086 | 0.0034024 | 0 | 0 | 0.0068047 | 298.2473 | 0.00392 | 0 | 0 | 0.00784 | 298.486 | 0.0044377 | 0 | 0 | 0.0088753 | 298.6451 | 0.0047828 | 0 | 0 | 0.0095655 | 298.8837 | 0.0053004 | 0 | 0 | 0.010601 | 299.0428 | 0.0056455 | 0 | 0 | 0.011291 | 299.2019 | 0.0059906 | 0 | 0 | 0.011981
2017-12-03 18:00 | 262.9215 | 0.78366 |  | 276.0846 | 0 | 0 | 0 | 0 | 283.8429 | 0 | 0 | 0 | 0 | 290.1905 | 0 | 0 | 0 | 0 | 290.4256 | 0 | 0 | 0 | 0 | 290.5824 | 0 | 0 | 0 | 0 | 290.8175 | 0 | 0 | 0 | 0 | 291.0526 | 0 | 0 | 0 | 0 | 291.2877 | 0 | 0 | 0 | 0 | 291.6011 | 0 | 0 | 0 | 0 | 291.8362 | 0 | 0 | 0 | 0 | 291.993 | 0 | 0 | 0 | 0 | 292.2281 | 0 | 0 | 0 | 0 | 292.3848 | 0 | 0 | 0 | 0 | 292.6199 | 0 | 0 | 0 | 0 | 292.855 | 0 | 0 | 0 | 0 | 293.0117 | 0 | 0 | 0 | 0 | 293.2468 | 0 | 0 | 0 | 0 | 293.4819 | 0 | 0 | 0 | 0 | 293.5603 | 0 | 0 | 0 | 0 | 293.7954 | 0 | 0 | 0 | 0 | 294.0305 | 0 | 0 | 0 | 0 | 294.1872 | 0 | 0 | 0 | 0 | 294.4223 | 0 | 0 | 0 | 0 | 294.5791 | 0 | 0 | 0 | 0 | 294.7358 | 0 | 0 | 0 | 0
2017-12-03 19:00 | 262.6908 | 0.78298 |  | 275.8424 | 0 | 0 | 0 | 0 | 283.5938 | 0 | 0 | 0 | 0 | 289.9359 | 0 | 0 | 0 | 0 | 290.1708 | 0 | 0 | 0 | 0 | 290.3274 | 0 | 0 | 0 | 0 | 290.5623 | 0 | 0 | 0 | 0 | 290.7972 | 0 | 0 | 0 | 0 | 291.0321 | 0 | 0 | 0 | 0 | 291.3453 | 0 | 0 | 0 | 0 | 291.5802 | 0 | 0 | 0 | 0 | 291.7368 | 0 | 0 | 0 | 0 | 291.9717 | 0 | 0 | 0 | 0 | 292.1283 | 0 | 0 | 0 | 0 | 292.3632 | 0 | 0 | 0 | 0 | 292.5981 | 0 | 0 | 0 | 0 | 292.7547 | 0 | 0 | 0 | 0 | 292.9895 | 0 | 0 | 0 | 0 | 293.2244 | 0 | 0 | 0 | 0 | 293.3027 | 0 | 0 | 0 | 0 | 293.5376 | 0 | 0 | 0 | 0 | 293.7725 | 0 | 0 | 0 | 0 | 293.9291 | 0 | 0 | 0 | 0 | 294.164 | 0 | 0 | 0 | 0 | 294.3206 | 0 | 0 | 0 | 0 | 294.4772 | 0 | 0 | 0 | 0
2017-12-03 20:00 | 259.7751 | 0.77429 |  | 272.7807 | 0 | 0 | 0 | 0 | 280.4461 | 0 | 0 | 0 | 0 | 286.7178 | 0 | 0 | 0 | 0 | 286.9501 | 0 | 0 | 0 | 0 | 287.105 | 0 | 0 | 0 | 0 | 287.3373 | 0 | 0 | 0 | 0 | 287.5696 | 0 | 0 | 0 | 0 | 287.8018 | 0 | 0 | 0 | 0 | 288.1116 | 0 | 0 | 0 | 0 | 288.3438 | 0 | 0 | 0 | 0 | 288.4987 | 0 | 0 | 0 | 0 | 288.731 | 0 | 0 | 0 | 0 | 288.8858 | 0 | 0 | 0 | 0 | 289.1181 | 0 | 0 | 0 | 0 | 289.3504 | 0 | 0 | 0 | 0 | 289.5053 | 0 | 0 | 0 | 0 | 289.7376 | 0 | 0 | 0 | 0 | 289.9698 | 0 | 0 | 0 | 0 | 290.0473 | 0 | 0 | 0 | 0 | 290.2796 | 0 | 0 | 0 | 0 | 290.5118 | 0 | 0 | 0 | 0 | 290.6667 | 0 | 0 | 0 | 0 | 290.899 | 0 | 0 | 0 | 0 | 291.0538 | 0 | 0 | 0 | 0 | 291.2087 | 0 | 0 | 0 | 0
2017-12-03 21:00 | 270.2367 | 0.80547 |  | 283.766 | 0 | 0 | 0 | 0 | 291.7401 | 0 | 0 | 0 | 0 | 298.2644 | 0.0039572 | 0 | 0 | 0.0079144 | 298.5061 | 0.0044813 | 0 | 0 | 0.0089626 | 298.6672 | 0.0048307 | 0 | 0 | 0.0096614 | 298.9088 | 0.0053548 | 0 | 0 | 0.01071 | 299.1504 | 0.0058789 | 0 | 0 | 0.011758 | 299.3921 | 0.0064031 | 0 | 0 | 0.012806 | 299.7143 | 0.0071019 | 0 | 0 | 0.014204 | 299.9559 | 0.007626 | 0 | 0 | 0.015252 | 300.117 | 0.0079754 | 0 | 0 | 0.015951 | 300.3586 | 0.0084995 | 0 | 0 | 0.016999 | 300.5197 | 0.0088489 | 0 | 0 | 0.017698 | 300.7614 | 0.0093731 | 0 | 0 | 0.018746 | 301.003 | 0.0098972 | 0 | 0 | 0.019794 | 301.1641 | 0.010247 | 0 | 0 | 0.020493 | 301.4057 | 0.010771 | 0 | 0 | 0.021541 | 301.6474 | 0.011295 | 0 | 0 | 0.02259 | 301.7279 | 0.01147 | 0 | 0 | 0.022939 | 301.9696 | 0.011994 | 0 | 0 | 0.023987 | 302.2112 | 0.012518 | 0 | 0 | 0.025036 | 302.3723 | 0.012867 | 0 | 0 | 0.025734 | 302.6139 | 0.013391 | 0 | 0 | 0.026783 | 302.775 | 0.013741 | 0 | 0 | 0.027481 | 302.9361 | 0.01409 | 0 | 0 | 0.02818
2017-12-03 22:00 | 269.1515 | 0.80223 |  | 282.6265 | 0 | 0 | 0 | 0 | 290.5686 | 0 | 0 | 0 | 0 | 297.0667 | 0.0013594 | 0 | 0 | 0.0027187 | 297.3074 | 0.0018814 | 0 | 0 | 0.0037627 | 297.4678 | 0.0022294 | 0 | 0 | 0.0044587 | 297.7085 | 0.0027514 | 0 | 0 | 0.0055028 | 297.9492 | 0.0032734 | 0 | 0 | 0.0065468 | 298.1898 | 0.0037954 | 0 | 0 | 0.0075908 | 298.5107 | 0.0044914 | 0 | 0 | 0.0089829 | 298.7514 | 0.0050134 | 0 | 0 | 0.010027 | 298.9119 | 0.0053615 | 0 | 0 | 0.010723 | 299.1525 | 0.0058835 | 0 | 0 | 0.011767 | 299.313 | 0.0062315 | 0 | 0 | 0.012463 | 299.5536 | 0.0067535 | 0 | 0 | 0.013507 | 299.7943 | 0.0072755 | 0 | 0 | 0.014551 | 299.9548 | 0.0076235 | 0 | 0 | 0.015247 | 300.1954 | 0.0081455 | 0 | 0 | 0.016291 | 300.4361 | 0.0086675 | 0 | 0 | 0.017335 | 300.5163 | 0.0088415 | 0 | 0 | 0.017683 | 300.757 | 0.0093635 | 0 | 0 | 0.018727 | 300.9977 | 0.0098856 | 0 | 0 | 0.019771 | 301.1581 | 0.010234 | 0 | 0 | 0.020467 | 301.3988 | 0.010756 | 0 | 0 | 0.021511 | 301.5592 | 0.011104 | 0 | 0 | 0.022207 | 301.7197 | 0.011452 | 0 | 0 | 0.022903
2017-12-03 23:00 | 274.3294 | 0.81767 |  | 288.0636 | 0 | 0 | 0 | 0 | 296.1585 | 0 | 0 | 0 | 0 | 302.7816 | 0.013755 | 0 | 0 | 0.02751 | 303.0269 | 0.014287 | 0 | 0 | 0.028574 | 303.1905 | 0.014642 | 0 | 0 | 0.029284 | 303.4358 | 0.015174 | 0 | 0 | 0.030348 | 303.6811 | 0.015706 | 0 | 0 | 0.031412 | 303.9264 | 0.016238 | 0 | 0 | 0.032476 | 304.2534 | 0.016947 | 0 | 0 | 0.033895 | 304.4987 | 0.017479 | 0 | 0 | 0.034959 | 304.6623 | 0.017834 | 0 | 0 | 0.035668 | 304.9076 | 0.018366 | 0 | 0 | 0.036732 | 305.0711 | 0.018721 | 0 | 0 | 0.037442 | 305.3164 | 0.019253 | 0 | 0 | 0.038506 | 305.5617 | 0.019785 | 0 | 0 | 0.03957 | 305.7252 | 0.02014 | 0 | 0 | 0.040279 | 305.9705 | 0.020672 | 0 | 0 | 0.041343 | 306.2158 | 0.021204 | 0 | 0 | 0.042408 | 306.2976 | 0.021381 | 0 | 0 | 0.042762 | 306.5429 | 0.021913 | 0 | 0 | 0.043826 | 306.7882 | 0.022445 | 0 | 0 | 0.04489 | 306.9517 | 0.0228 | 0 | 0 | 0.0456 | 307.197 | 0.023332 | 0 | 0 | 0.046664 | 307.3606 | 0.023687 | 0 | 0 | 0.047373 | 307.5241 | 0.024041 | 0 | 0 | 0.048083
2017-12-04 | 270.7411 | 0.80697 |  | 284.2957 | 0 | 0 | 0 | 0 | 292.2847 | 0 | 0 | 0 | 0 | 298.8211 | 0.0051647 | 0 | 0 | 0.010329 | 299.0632 | 0.0056898 | 0 | 0 | 0.01138 | 299.2246 | 0.0060398 | 0 | 0 | 0.01208 | 299.4667 | 0.0065649 | 0 | 0 | 0.01313 | 299.7088 | 0.00709 | 0 | 0 | 0.01418 | 299.9509 | 0.0076151 | 0 | 0 | 0.01523 | 300.2737 | 0.0083153 | 0 | 0 | 0.016631 | 300.5158 | 0.0088404 | 0 | 0 | 0.017681 | 300.6772 | 0.0091904 | 0 | 0 | 0.018381 | 300.9193 | 0.0097155 | 0 | 0 | 0.019431 | 301.0807 | 0.010066 | 0 | 0 | 0.020131 | 301.3227 | 0.010591 | 0 | 0 | 0.021181 | 301.5648 | 0.011116 | 0 | 0 | 0.022232 | 301.7262 | 0.011466 | 0 | 0 | 0.022932 | 301.9683 | 0.011991 | 0 | 0 | 0.023982 | 302.2104 | 0.012516 | 0 | 0 | 0.025032 | 302.2911 | 0.012691 | 0 | 0 | 0.025382 | 302.5332 | 0.013216 | 0 | 0 | 0.026432 | 302.7753 | 0.013741 | 0 | 0 | 0.027483 | 302.9367 | 0.014091 | 0 | 0 | 0.028183 | 303.1788 | 0.014616 | 0 | 0 | 0.029233 | 303.3402 | 0.014966 | 0 | 0 | 0.029933 | 303.5016 | 0.015317 | 0 | 0 | 0.030633
2017-12-04 01:00 | 269.8103 | 0.8042 |  | 283.3183 | 0 | 0 | 0 | 0 | 291.2799 | 0 | 0 | 0 | 0 | 297.7939 | 0.0029365 | 0 | 0 | 0.005873 | 298.0351 | 0.0034598 | 0 | 0 | 0.0069196 | 298.196 | 0.0038087 | 0 | 0 | 0.0076173 | 298.4372 | 0.0043319 | 0 | 0 | 0.0086639 | 298.6785 | 0.0048552 | 0 | 0 | 0.0097105 | 298.9197 | 0.0053785 | 0 | 0 | 0.010757 | 299.2414 | 0.0060763 | 0 | 0 | 0.012153 | 299.4827 | 0.0065995 | 0 | 0 | 0.013199 | 299.6435 | 0.0069484 | 0 | 0 | 0.013897 | 299.8848 | 0.0074717 | 0 | 0 | 0.014943 | 300.0456 | 0.0078206 | 0 | 0 | 0.015641 | 300.2869 | 0.0083438 | 0 | 0 | 0.016688 | 300.5281 | 0.0088671 | 0 | 0 | 0.017734 | 300.689 | 0.009216 | 0 | 0 | 0.018432 | 300.9302 | 0.0097393 | 0 | 0 | 0.019479 | 301.1715 | 0.010263 | 0 | 0 | 0.020525 | 301.2519 | 0.010437 | 0 | 0 | 0.020874 | 301.4932 | 0.01096 | 0 | 0 | 0.021921 | 301.7344 | 0.011484 | 0 | 0 | 0.022967 | 301.8953 | 0.011832 | 0 | 0 | 0.023665 | 302.1365 | 0.012356 | 0 | 0 | 0.024711 | 302.2974 | 0.012705 | 0 | 0 | 0.025409 | 302.4582 | 0.013053 | 0 | 0 | 0.026107
2017-12-04 02:00 | 270.127 | 0.80514 |  | 283.6508 | 0 | 0 | 0 | 0 | 291.6217 | 0 | 0 | 0 | 0 | 298.1434 | 0.0036946 | 0 | 0 | 0.0073892 | 298.3849 | 0.0042185 | 0 | 0 | 0.008437 | 298.5459 | 0.0045678 | 0 | 0 | 0.0091355 | 298.7875 | 0.0050917 | 0 | 0 | 0.010183 | 299.029 | 0.0056156 | 0 | 0 | 0.011231 | 299.2706 | 0.0061395 | 0 | 0 | 0.012279 | 299.5926 | 0.006838 | 0 | 0 | 0.013676 | 299.8342 | 0.0073619 | 0 | 0 | 0.014724 | 299.9952 | 0.0077112 | 0 | 0 | 0.015422 | 300.2367 | 0.0082351 | 0 | 0 | 0.01647 | 300.3978 | 0.0085844 | 0 | 0 | 0.017169 | 300.6393 | 0.0091083 | 0 | 0 | 0.018217 | 300.8808 | 0.0096322 | 0 | 0 | 0.019264 | 301.0419 | 0.0099814 | 0 | 0 | 0.019963 | 301.2834 | 0.010505 | 0 | 0 | 0.021011 | 301.525 | 0.011029 | 0 | 0 | 0.022059 | 301.6055 | 0.011204 | 0 | 0 | 0.022408 | 301.847 | 0.011728 | 0 | 0 | 0.023456 | 302.0885 | 0.012252 | 0 | 0 | 0.024503 | 302.2496 | 0.012601 | 0 | 0 | 0.025202 | 302.4911 | 0.013125 | 0 | 0 | 0.02625 | 302.6521 | 0.013474 | 0 | 0 | 0.026948 | 302.8132 | 0.013823 | 0 | 0 | 0.027647
2017-12-04 03:00 | 276.6499 | 0.82458 |  | 290.5003 | 0 | 0 | 0 | 0 | 298.6637 | 0.0048231 | 0 | 0 | 0.0096462 | 305.3428 | 0.01931 | 0 | 0 | 0.03862 | 305.5901 | 0.019847 | 0 | 0 | 0.039693 | 305.7551 | 0.020204 | 0 | 0 | 0.040409 | 306.0024 | 0.020741 | 0 | 0 | 0.041482 | 306.2498 | 0.021277 | 0 | 0 | 0.042555 | 306.4972 | 0.021814 | 0 | 0 | 0.043628 | 306.827 | 0.022529 | 0 | 0 | 0.045059 | 307.0744 | 0.023066 | 0 | 0 | 0.046132 | 307.2393 | 0.023424 | 0 | 0 | 0.046847 | 307.4867 | 0.02396 | 0 | 0 | 0.047921 | 307.6516 | 0.024318 | 0 | 0 | 0.048636 | 307.899 | 0.024855 | 0 | 0 | 0.049709 | 308.1463 | 0.025391 | 0 | 0 | 0.050782 | 308.3113 | 0.025749 | 0 | 0 | 0.051498 | 308.5586 | 0.026285 | 0 | 0 | 0.052571 | 308.806 | 0.026822 | 0 | 0 | 0.053644 | 308.8885 | 0.027001 | 0 | 0 | 0.054001 | 309.1358 | 0.027537 | 0 | 0 | 0.055075 | 309.3832 | 0.028074 | 0 | 0 | 0.056148 | 309.5481 | 0.028432 | 0 | 0 | 0.056863 | 309.7955 | 0.028968 | 0 | 0 | 0.057936 | 309.9604 | 0.029326 | 0 | 0 | 0.058652 | 310.1253 | 0.029684 | 0 | 0 | 0.059367
2017-12-04 04:00 | 274.5728 | 0.81839 |  | 288.3192 | 0 | 0 | 0 | 0 | 296.4213 | 0 | 0 | 0 | 0 | 303.0502 | 0.014338 | 0 | 0 | 0.028675 | 303.2957 | 0.01487 | 0 | 0 | 0.02974 | 303.4594 | 0.015225 | 0 | 0 | 0.03045 | 303.7049 | 0.015758 | 0 | 0 | 0.031515 | 303.9505 | 0.01629 | 0 | 0 | 0.03258 | 304.196 | 0.016823 | 0 | 0 | 0.033645 | 304.5233 | 0.017533 | 0 | 0 | 0.035065 | 304.7688 | 0.018065 | 0 | 0 | 0.036131 | 304.9325 | 0.01842 | 0 | 0 | 0.036841 | 305.178 | 0.018953 | 0 | 0 | 0.037906 | 305.3417 | 0.019308 | 0 | 0 | 0.038616 | 305.5872 | 0.01984 | 0 | 0 | 0.039681 | 305.8328 | 0.020373 | 0 | 0 | 0.040746 | 305.9964 | 0.020728 | 0 | 0 | 0.041456 | 306.242 | 0.02126 | 0 | 0 | 0.042521 | 306.4875 | 0.021793 | 0 | 0 | 0.043586 | 306.5693 | 0.02197 | 0 | 0 | 0.043941 | 306.8148 | 0.022503 | 0 | 0 | 0.045006 | 307.0603 | 0.023036 | 0 | 0 | 0.046071 | 307.224 | 0.023391 | 0 | 0 | 0.046781 | 307.4695 | 0.023923 | 0 | 0 | 0.047846 | 307.6332 | 0.024278 | 0 | 0 | 0.048556 | 307.7969 | 0.024633 | 0 | 0 | 0.049266
2017-12-04 05:00 | 276.9244 | 0.8254 |  | 290.7885 | 0 | 0 | 0 | 0 | 298.96 | 0.0054658 | 0 | 0 | 0.010932 | 305.6457 | 0.019967 | 0 | 0 | 0.039934 | 305.8933 | 0.020504 | 0 | 0 | 0.041009 | 306.0584 | 0.020862 | 0 | 0 | 0.041725 | 306.306 | 0.021399 | 0 | 0 | 0.042799 | 306.5536 | 0.021936 | 0 | 0 | 0.043873 | 306.8013 | 0.022474 | 0 | 0 | 0.044947 | 307.1314 | 0.02319 | 0 | 0 | 0.046379 | 307.379 | 0.023727 | 0 | 0 | 0.047454 | 307.5441 | 0.024085 | 0 | 0 | 0.04817 | 307.7917 | 0.024622 | 0 | 0 | 0.049244 | 307.9568 | 0.02498 | 0 | 0 | 0.04996 | 308.2044 | 0.025517 | 0 | 0 | 0.051034 | 308.4521 | 0.026054 | 0 | 0 | 0.052108 | 308.6171 | 0.026412 | 0 | 0 | 0.052824 | 308.8648 | 0.026949 | 0 | 0 | 0.053899 | 309.1124 | 0.027486 | 0 | 0 | 0.054973 | 309.1949 | 0.027665 | 0 | 0 | 0.055331 | 309.4425 | 0.028203 | 0 | 0 | 0.056405 | 309.6902 | 0.02874 | 0 | 0 | 0.057479 | 309.8552 | 0.029098 | 0 | 0 | 0.058195 | 310.1029 | 0.029635 | 0 | 0 | 0.059269 | 310.2679 | 0.029993 | 0 | 0 | 0.059986 | 310.433 | 0.030351 | 0 | 0 | 0.060702
2017-12-04 06:00 | 285.5703 | 0.85117 |  | 299.8673 | 0.0074339 | 0 | 0 | 0.014868 | 308.2939 | 0.025711 | 0 | 0 | 0.051422 | 315.1884 | 0.040665 | 0 | 0 | 0.081331 | 315.4438 | 0.041219 | 0 | 0 | 0.082438 | 315.614 | 0.041588 | 0 | 0 | 0.083177 | 315.8693 | 0.042142 | 0 | 0 | 0.084285 | 316.1247 | 0.042696 | 0 | 0 | 0.085392 | 316.3801 | 0.04325 | 0 | 0 | 0.0865 | 316.7205 | 0.043988 | 0 | 0 | 0.087977 | 316.9759 | 0.044542 | 0 | 0 | 0.089085 | 317.1461 | 0.044912 | 0 | 0 | 0.089823 | 317.4015 | 0.045465 | 0 | 0 | 0.090931 | 317.5717 | 0.045835 | 0 | 0 | 0.091669 | 317.827 | 0.046388 | 0 | 0 | 0.092777 | 318.0824 | 0.046942 | 0 | 0 | 0.093885 | 318.2526 | 0.047312 | 0 | 0 | 0.094623 | 318.508 | 0.047865 | 0 | 0 | 0.095731 | 318.7633 | 0.048419 | 0 | 0 | 0.096839 | 318.8484 | 0.048604 | 0 | 0 | 0.097208 | 319.1038 | 0.049158 | 0 | 0 | 0.098316 | 319.3591 | 0.049712 | 0 | 0 | 0.099423 | 319.5294 | 0.050081 | 0 | 0 | 0.10016 | 319.7847 | 0.050635 | 0 | 0 | 0.10127 | 319.955 | 0.051004 | 0 | 0 | 0.10201 | 320.1252 | 0.051373 | 0 | 0 | 0.10275
2017-12-04 07:00 | 286.448 | 0.85379 |  | 300.7889 | 0.0094328 | 0 | 0 | 0.018866 | 309.2414 | 0.027766 | 0 | 0 | 0.055532 | 316.1571 | 0.042766 | 0 | 0 | 0.085533 | 316.4132 | 0.043322 | 0 | 0 | 0.086644 | 316.584 | 0.043692 | 0 | 0 | 0.087385 | 316.8401 | 0.044248 | 0 | 0 | 0.088496 | 317.0962 | 0.044803 | 0 | 0 | 0.089607 | 317.3524 | 0.045359 | 0 | 0 | 0.090718 | 317.6939 | 0.0461 | 0 | 0 | 0.092199 | 317.95 | 0.046655 | 0 | 0 | 0.09331 | 318.1208 | 0.047026 | 0 | 0 | 0.094051 | 318.3769 | 0.047581 | 0 | 0 | 0.095162 | 318.5477 | 0.047952 | 0 | 0 | 0.095903 | 318.8038 | 0.048507 | 0 | 0 | 0.097014 | 319.0599 | 0.049063 | 0 | 0 | 0.098125 | 319.2307 | 0.049433 | 0 | 0 | 0.098866 | 319.4868 | 0.049989 | 0 | 0 | 0.099977 | 319.743 | 0.050544 | 0 | 0 | 0.10109 | 319.8283 | 0.050729 | 0 | 0 | 0.10146 | 320.0845 | 0.051285 | 0 | 0 | 0.10257 | 320.3406 | 0.05184 | 0 | 0 | 0.10368 | 320.5114 | 0.052211 | 0 | 0 | 0.10442 | 320.7675 | 0.052766 | 0 | 0 | 0.10553 | 320.9383 | 0.053137 | 0 | 0 | 0.10627 | 321.109 | 0.053507 | 0 | 0 | 0.10701
2017-12-04 08:00 | 281.9735 | 0.84045 |  | 296.0904 | 0 | 0 | 0 | 0 | 304.4109 | 0.017289 | 0 | 0 | 0.034578 | 311.2185 | 0.032055 | 0 | 0 | 0.064109 | 311.4707 | 0.032602 | 0 | 0 | 0.065203 | 311.6388 | 0.032966 | 0 | 0 | 0.065932 | 311.8909 | 0.033513 | 0 | 0 | 0.067026 | 312.143 | 0.03406 | 0 | 0 | 0.06812 | 312.3952 | 0.034607 | 0 | 0 | 0.069214 | 312.7314 | 0.035336 | 0 | 0 | 0.070672 | 312.9835 | 0.035883 | 0 | 0 | 0.071766 | 313.1516 | 0.036247 | 0 | 0 | 0.072495 | 313.4037 | 0.036794 | 0 | 0 | 0.073589 | 313.5718 | 0.037159 | 0 | 0 | 0.074318 | 313.8239 | 0.037706 | 0 | 0 | 0.075412 | 314.0761 | 0.038253 | 0 | 0 | 0.076505 | 314.2442 | 0.038617 | 0 | 0 | 0.077234 | 314.4963 | 0.039164 | 0 | 0 | 0.078328 | 314.7484 | 0.039711 | 0 | 0 | 0.079422 | 314.8325 | 0.039893 | 0 | 0 | 0.079787 | 315.0846 | 0.04044 | 0 | 0 | 0.08088 | 315.3367 | 0.040987 | 0 | 0 | 0.081974 | 315.5048 | 0.041352 | 0 | 0 | 0.082703 | 315.757 | 0.041899 | 0 | 0 | 0.083797 | 315.9251 | 0.042263 | 0 | 0 | 0.084526 | 316.0931 | 0.042628 | 0 | 0 | 0.085255
2017-12-04 09:00 | 289.7412 | 0.8636 |  | 304.247 | 0.016933 | 0 | 0 | 0.033867 | 312.7967 | 0.035478 | 0 | 0 | 0.070955 | 319.7919 | 0.05065 | 0 | 0 | 0.1013 | 320.051 | 0.051212 | 0 | 0 | 0.10242 | 320.2237 | 0.051587 | 0 | 0 | 0.10317 | 320.4828 | 0.052149 | 0 | 0 | 0.1043 | 320.7418 | 0.052711 | 0 | 0 | 0.10542 | 321.0009 | 0.053273 | 0 | 0 | 0.10655 | 321.3464 | 0.054022 | 0 | 0 | 0.10804 | 321.6054 | 0.054584 | 0 | 0 | 0.10917 | 321.7782 | 0.054958 | 0 | 0 | 0.10992 | 322.0372 | 0.05552 | 0 | 0 | 0.11104 | 322.21 | 0.055895 | 0 | 0 | 0.11179 | 322.469 | 0.056457 | 0 | 0 | 0.11291 | 322.7281 | 0.057019 | 0 | 0 | 0.11404 | 322.9008 | 0.057394 | 0 | 0 | 0.11479 | 323.1599 | 0.057956 | 0 | 0 | 0.11591 | 323.419 | 0.058517 | 0 | 0 | 0.11703 | 323.5054 | 0.058705 | 0 | 0 | 0.11741 | 323.7644 | 0.059267 | 0 | 0 | 0.11853 | 324.0235 | 0.059829 | 0 | 0 | 0.11966 | 324.1963 | 0.060203 | 0 | 0 | 0.12041 | 324.4553 | 0.060765 | 0 | 0 | 0.12153 | 324.6281 | 0.06114 | 0 | 0 | 0.12228 | 324.8008 | 0.061515 | 0 | 0 | 0.12303
2017-12-04 10:00 | 290.5643 | 0.86606 |  | 305.1114 | 0.018808 | 0 | 0 | 0.037616 | 313.6853 | 0.037405 | 0 | 0 | 0.07481 | 320.7004 | 0.052621 | 0 | 0 | 0.10524 | 320.9602 | 0.053184 | 0 | 0 | 0.10637 | 321.1334 | 0.05356 | 0 | 0 | 0.10712 | 321.3932 | 0.054123 | 0 | 0 | 0.10825 | 321.653 | 0.054687 | 0 | 0 | 0.10937 | 321.9128 | 0.055251 | 0 | 0 | 0.1105 | 322.2593 | 0.056002 | 0 | 0 | 0.112 | 322.5191 | 0.056566 | 0 | 0 | 0.11313 | 322.6923 | 0.056941 | 0 | 0 | 0.11388 | 322.9521 | 0.057505 | 0 | 0 | 0.11501 | 323.1253 | 0.05788 | 0 | 0 | 0.11576 | 323.3851 | 0.058444 | 0 | 0 | 0.11689 | 323.6449 | 0.059008 | 0 | 0 | 0.11802 | 323.8182 | 0.059383 | 0 | 0 | 0.11877 | 324.078 | 0.059947 | 0 | 0 | 0.11989 | 324.3378 | 0.06051 | 0 | 0 | 0.12102 | 324.4244 | 0.060698 | 0 | 0 | 0.1214 | 324.6842 | 0.061262 | 0 | 0 | 0.12252 | 324.944 | 0.061825 | 0 | 0 | 0.12365 | 325.1172 | 0.062201 | 0 | 0 | 0.1244 | 325.3771 | 0.062764 | 0 | 0 | 0.12553 | 325.5503 | 0.06314 | 0 | 0 | 0.12628 | 325.7235 | 0.063516 | 0 | 0 | 0.12703
2017-12-04 11:00 | 283.879 | 0.84613 |  | 298.0913 | 0.0035818 | 0 | 0 | 0.0071635 | 306.468 | 0.021751 | 0 | 0 | 0.043502 | 313.3217 | 0.036616 | 0 | 0 | 0.073233 | 313.5755 | 0.037167 | 0 | 0 | 0.074334 | 313.7447 | 0.037534 | 0 | 0 | 0.075068 | 313.9986 | 0.038085 | 0 | 0 | 0.076169 | 314.2524 | 0.038635 | 0 | 0 | 0.07727 | 314.5062 | 0.039186 | 0 | 0 | 0.078371 | 314.8447 | 0.03992 | 0 | 0 | 0.07984 | 315.0985 | 0.04047 | 0 | 0 | 0.080941 | 315.2678 | 0.040837 | 0 | 0 | 0.081675 | 315.5216 | 0.041388 | 0 | 0 | 0.082776 | 315.6908 | 0.041755 | 0 | 0 | 0.08351 | 315.9447 | 0.042306 | 0 | 0 | 0.084611 | 316.1985 | 0.042856 | 0 | 0 | 0.085712 | 316.3677 | 0.043223 | 0 | 0 | 0.086446 | 316.6216 | 0.043774 | 0 | 0 | 0.087548 | 316.8754 | 0.044324 | 0 | 0 | 0.088649 | 316.96 | 0.044508 | 0 | 0 | 0.089016 | 317.2139 | 0.045059 | 0 | 0 | 0.090117 | 317.4677 | 0.045609 | 0 | 0 | 0.091218 | 317.6369 | 0.045976 | 0 | 0 | 0.091952 | 317.8908 | 0.046527 | 0 | 0 | 0.093053 | 318.06 | 0.046894 | 0 | 0 | 0.093788 | 318.2292 | 0.047261 | 0 | 0 | 0.094522
2017-12-04 12:00 | 278.8962 | 0.83128 |  | 292.8591 | 0 | 0 | 0 | 0 | 301.0888 | 0.010083 | 0 | 0 | 0.020166 | 307.8221 | 0.024688 | 0 | 0 | 0.049376 | 308.0715 | 0.025229 | 0 | 0 | 0.050457 | 308.2377 | 0.025589 | 0 | 0 | 0.051179 | 308.4871 | 0.02613 | 0 | 0 | 0.05226 | 308.7365 | 0.026671 | 0 | 0 | 0.053342 | 308.9859 | 0.027212 | 0 | 0 | 0.054424 | 309.3184 | 0.027933 | 0 | 0 | 0.055867 | 309.5678 | 0.028474 | 0 | 0 | 0.056948 | 309.734 | 0.028835 | 0 | 0 | 0.05767 | 309.9834 | 0.029376 | 0 | 0 | 0.058751 | 310.1497 | 0.029736 | 0 | 0 | 0.059473 | 310.3991 | 0.030277 | 0 | 0 | 0.060554 | 310.6484 | 0.030818 | 0 | 0 | 0.061636 | 310.8147 | 0.031179 | 0 | 0 | 0.062357 | 311.0641 | 0.03172 | 0 | 0 | 0.063439 | 311.3135 | 0.032261 | 0 | 0 | 0.064521 | 311.3966 | 0.032441 | 0 | 0 | 0.064882 | 311.646 | 0.032982 | 0 | 0 | 0.065964 | 311.8954 | 0.033523 | 0 | 0 | 0.067045 | 312.0616 | 0.033883 | 0 | 0 | 0.067767 | 312.311 | 0.034424 | 0 | 0 | 0.068848 | 312.4773 | 0.034785 | 0 | 0 | 0.06957 | 312.6435 | 0.035145 | 0 | 0 | 0.070291
2017-12-04 13:00 | 284.5625 | 0.84817 |  | 298.8091 | 0.0051385 | 0 | 0 | 0.010277 | 307.2059 | 0.023351 | 0 | 0 | 0.046703 | 314.0761 | 0.038253 | 0 | 0 | 0.076505 | 314.3305 | 0.038805 | 0 | 0 | 0.077609 | 314.5002 | 0.039172 | 0 | 0 | 0.078345 | 314.7546 | 0.039724 | 0 | 0 | 0.079449 | 315.0091 | 0.040276 | 0 | 0 | 0.080553 | 315.2635 | 0.040828 | 0 | 0 | 0.081656 | 315.6028 | 0.041564 | 0 | 0 | 0.083128 | 315.8572 | 0.042116 | 0 | 0 | 0.084232 | 316.0269 | 0.042484 | 0 | 0 | 0.084968 | 316.2813 | 0.043036 | 0 | 0 | 0.086072 | 316.4509 | 0.043404 | 0 | 0 | 0.086807 | 316.7054 | 0.043956 | 0 | 0 | 0.087911 | 316.9598 | 0.044508 | 0 | 0 | 0.089015 | 317.1295 | 0.044875 | 0 | 0 | 0.089751 | 317.3839 | 0.045427 | 0 | 0 | 0.090855 | 317.6384 | 0.045979 | 0 | 0 | 0.091959 | 317.7232 | 0.046163 | 0 | 0 | 0.092326 | 317.9776 | 0.046715 | 0 | 0 | 0.09343 | 318.2321 | 0.047267 | 0 | 0 | 0.094534 | 318.4017 | 0.047635 | 0 | 0 | 0.09527 | 318.6562 | 0.048187 | 0 | 0 | 0.096374 | 318.8258 | 0.048555 | 0 | 0 | 0.09711 | 318.9954 | 0.048923 | 0 | 0 | 0.097845
2017-12-04 14:00 | 285.2681 | 0.85027 |  | 299.55 | 0.0067456 | 0 | 0 | 0.013491 | 307.9677 | 0.025004 | 0 | 0 | 0.050007 | 314.8549 | 0.039942 | 0 | 0 | 0.079884 | 315.1099 | 0.040495 | 0 | 0 | 0.08099 | 315.28 | 0.040864 | 0 | 0 | 0.081728 | 315.5351 | 0.041417 | 0 | 0 | 0.082834 | 315.7902 | 0.04197 | 0 | 0 | 0.083941 | 316.0452 | 0.042524 | 0 | 0 | 0.085048 | 316.3853 | 0.043261 | 0 | 0 | 0.086523 | 316.6404 | 0.043815 | 0 | 0 | 0.087629 | 316.8105 | 0.044184 | 0 | 0 | 0.088367 | 317.0656 | 0.044737 | 0 | 0 | 0.089474 | 317.2356 | 0.045106 | 0 | 0 | 0.090211 | 317.4907 | 0.045659 | 0 | 0 | 0.091318 | 317.7458 | 0.046212 | 0 | 0 | 0.092424 | 317.9158 | 0.046581 | 0 | 0 | 0.093162 | 318.1709 | 0.047134 | 0 | 0 | 0.094269 | 318.426 | 0.047688 | 0 | 0 | 0.095375 | 318.511 | 0.047872 | 0 | 0 | 0.095744 | 318.7661 | 0.048425 | 0 | 0 | 0.096851 | 319.0212 | 0.048979 | 0 | 0 | 0.097957 | 319.1912 | 0.049347 | 0 | 0 | 0.098695 | 319.4463 | 0.049901 | 0 | 0 | 0.099801 | 319.6164 | 0.05027 | 0 | 0 | 0.10054 | 319.7864 | 0.050638 | 0 | 0 | 0.10128
2017-12-04 15:00 | 277.6438 | 0.82754 |  | 291.5439 | 0 | 0 | 0 | 0 | 299.7366 | 0.0071504 | 0 | 0 | 0.014301 | 306.4397 | 0.021689 | 0 | 0 | 0.043379 | 306.688 | 0.022228 | 0 | 0 | 0.044456 | 306.8535 | 0.022587 | 0 | 0 | 0.045174 | 307.1018 | 0.023125 | 0 | 0 | 0.046251 | 307.35 | 0.023664 | 0 | 0 | 0.047328 | 307.5983 | 0.024202 | 0 | 0 | 0.048405 | 307.9293 | 0.02492 | 0 | 0 | 0.049841 | 308.1776 | 0.025459 | 0 | 0 | 0.050918 | 308.3431 | 0.025818 | 0 | 0 | 0.051636 | 308.5914 | 0.026356 | 0 | 0 | 0.052713 | 308.7569 | 0.026715 | 0 | 0 | 0.053431 | 309.0051 | 0.027254 | 0 | 0 | 0.054508 | 309.2534 | 0.027792 | 0 | 0 | 0.055585 | 309.4189 | 0.028151 | 0 | 0 | 0.056302 | 309.6672 | 0.02869 | 0 | 0 | 0.057379 | 309.9154 | 0.029228 | 0 | 0 | 0.058456 | 309.9982 | 0.029408 | 0 | 0 | 0.058815 | 310.2465 | 0.029946 | 0 | 0 | 0.059892 | 310.4947 | 0.030485 | 0 | 0 | 0.060969 | 310.6602 | 0.030844 | 0 | 0 | 0.061687 | 310.9085 | 0.031382 | 0 | 0 | 0.062764 | 311.074 | 0.031741 | 0 | 0 | 0.063482 | 311.2395 | 0.0321 | 0 | 0 | 0.0642
2017-12-04 16:00 | 271.3953 | 0.80892 |  | 284.9827 | 0 | 0 | 0 | 0 | 292.991 | 0 | 0 | 0 | 0 | 299.5432 | 0.0067309 | 0 | 0 | 0.013462 | 299.7859 | 0.0072573 | 0 | 0 | 0.014515 | 299.9477 | 0.0076082 | 0 | 0 | 0.015216 | 300.1904 | 0.0081346 | 0 | 0 | 0.016269 | 300.4331 | 0.0086609 | 0 | 0 | 0.017322 | 300.6757 | 0.0091873 | 0 | 0 | 0.018375 | 300.9993 | 0.0098891 | 0 | 0 | 0.019778 | 301.242 | 0.010415 | 0 | 0 | 0.020831 | 301.4038 | 0.010766 | 0 | 0 | 0.021533 | 301.6464 | 0.011293 | 0 | 0 | 0.022586 | 301.8082 | 0.011644 | 0 | 0 | 0.023287 | 302.0509 | 0.01217 | 0 | 0 | 0.02434 | 302.2936 | 0.012696 | 0 | 0 | 0.025393 | 302.4554 | 0.013047 | 0 | 0 | 0.026095 | 302.698 | 0.013574 | 0 | 0 | 0.027147 | 302.9407 | 0.0141 | 0 | 0 | 0.0282 | 303.0216 | 0.014275 | 0 | 0 | 0.028551 | 303.2643 | 0.014802 | 0 | 0 | 0.029604 | 303.507 | 0.015328 | 0 | 0 | 0.030656 | 303.6687 | 0.015679 | 0 | 0 | 0.031358 | 303.9114 | 0.016206 | 0 | 0 | 0.032411 | 304.0732 | 0.016556 | 0 | 0 | 0.033113 | 304.235 | 0.016907 | 0 | 0 | 0.033815
2017-12-04 17:00 | 281.0593 | 0.83772 |  | 295.1305 | 0 | 0 | 0 | 0 | 303.424 | 0.015148 | 0 | 0 | 0.030296 | 310.2095 | 0.029866 | 0 | 0 | 0.059732 | 310.4609 | 0.030411 | 0 | 0 | 0.060823 | 310.6284 | 0.030775 | 0 | 0 | 0.061549 | 310.8797 | 0.03132 | 0 | 0 | 0.06264 | 311.131 | 0.031865 | 0 | 0 | 0.06373 | 311.3824 | 0.03241 | 0 | 0 | 0.06482 | 311.7175 | 0.033137 | 0 | 0 | 0.066274 | 311.9688 | 0.033682 | 0 | 0 | 0.067364 | 312.1363 | 0.034045 | 0 | 0 | 0.068091 | 312.3876 | 0.03459 | 0 | 0 | 0.069181 | 312.5552 | 0.034954 | 0 | 0 | 0.069908 | 312.8065 | 0.035499 | 0 | 0 | 0.070998 | 313.0578 | 0.036044 | 0 | 0 | 0.072088 | 313.2254 | 0.036407 | 0 | 0 | 0.072815 | 313.4767 | 0.036953 | 0 | 0 | 0.073905 | 313.728 | 0.037498 | 0 | 0 | 0.074995 | 313.8118 | 0.037679 | 0 | 0 | 0.075359 | 314.0631 | 0.038224 | 0 | 0 | 0.076449 | 314.3144 | 0.03877 | 0 | 0 | 0.077539 | 314.4819 | 0.039133 | 0 | 0 | 0.078266 | 314.7333 | 0.039678 | 0 | 0 | 0.079356 | 314.9008 | 0.040041 | 0 | 0 | 0.080083 | 315.0684 | 0.040405 | 0 | 0 | 0.08081
2017-12-04 18:00 | 280.1001 | 0.83487 |  | 294.1233 | 0 | 0 | 0 | 0 | 302.3884 | 0.012902 | 0 | 0 | 0.025804 | 309.1509 | 0.02757 | 0 | 0 | 0.05514 | 309.4013 | 0.028113 | 0 | 0 | 0.056226 | 309.5683 | 0.028475 | 0 | 0 | 0.05695 | 309.8187 | 0.029018 | 0 | 0 | 0.058037 | 310.0692 | 0.029562 | 0 | 0 | 0.059123 | 310.3197 | 0.030105 | 0 | 0 | 0.06021 | 310.6536 | 0.030829 | 0 | 0 | 0.061659 | 310.9041 | 0.031373 | 0 | 0 | 0.062745 | 311.071 | 0.031735 | 0 | 0 | 0.063469 | 311.3215 | 0.032278 | 0 | 0 | 0.064556 | 311.4885 | 0.03264 | 0 | 0 | 0.06528 | 311.7389 | 0.033183 | 0 | 0 | 0.066367 | 311.9894 | 0.033727 | 0 | 0 | 0.067453 | 312.1564 | 0.034089 | 0 | 0 | 0.068178 | 312.4068 | 0.034632 | 0 | 0 | 0.069264 | 312.6573 | 0.035175 | 0 | 0 | 0.070351 | 312.7408 | 0.035356 | 0 | 0 | 0.070713 | 312.9912 | 0.0359 | 0 | 0 | 0.071799 | 313.2417 | 0.036443 | 0 | 0 | 0.072886 | 313.4087 | 0.036805 | 0 | 0 | 0.07361 | 313.6591 | 0.037348 | 0 | 0 | 0.074697 | 313.8261 | 0.03771 | 0 | 0 | 0.075421 | 313.9931 | 0.038073 | 0 | 0 | 0.076145
2017-12-04 19:00 | 282.888 | 0.84318 |  | 297.0507 | 0.0013246 | 0 | 0 | 0.0026492 | 305.3981 | 0.01943 | 0 | 0 | 0.03886 | 312.2279 | 0.034244 | 0 | 0 | 0.068488 | 312.4808 | 0.034793 | 0 | 0 | 0.069585 | 312.6494 | 0.035158 | 0 | 0 | 0.070317 | 312.9024 | 0.035707 | 0 | 0 | 0.071414 | 313.1554 | 0.036256 | 0 | 0 | 0.072511 | 313.4083 | 0.036804 | 0 | 0 | 0.073609 | 313.7456 | 0.037536 | 0 | 0 | 0.075072 | 313.9985 | 0.038084 | 0 | 0 | 0.076169 | 314.1672 | 0.03845 | 0 | 0 | 0.0769 | 314.4201 | 0.038999 | 0 | 0 | 0.077998 | 314.5888 | 0.039365 | 0 | 0 | 0.078729 | 314.8417 | 0.039913 | 0 | 0 | 0.079827 | 315.0947 | 0.040462 | 0 | 0 | 0.080924 | 315.2633 | 0.040828 | 0 | 0 | 0.081655 | 315.5162 | 0.041376 | 0 | 0 | 0.082753 | 315.7692 | 0.041925 | 0 | 0 | 0.08385 | 315.8535 | 0.042108 | 0 | 0 | 0.084216 | 316.1065 | 0.042657 | 0 | 0 | 0.085313 | 316.3594 | 0.043205 | 0 | 0 | 0.08641 | 316.5281 | 0.043571 | 0 | 0 | 0.087142 | 316.781 | 0.04412 | 0 | 0 | 0.088239 | 316.9496 | 0.044485 | 0 | 0 | 0.088971 | 317.1183 | 0.044851 | 0 | 0 | 0.089702
2017-12-04 20:00 | 278.0477 | 0.82875 |  | 291.968 | 0 | 0 | 0 | 0 | 300.1726 | 0.0080961 | 0 | 0 | 0.016192 | 306.8855 | 0.022656 | 0 | 0 | 0.045313 | 307.1341 | 0.023196 | 0 | 0 | 0.046391 | 307.2999 | 0.023555 | 0 | 0 | 0.04711 | 307.5485 | 0.024094 | 0 | 0 | 0.048189 | 307.7971 | 0.024634 | 0 | 0 | 0.049267 | 308.0458 | 0.025173 | 0 | 0 | 0.050346 | 308.3773 | 0.025892 | 0 | 0 | 0.051784 | 308.6259 | 0.026431 | 0 | 0 | 0.052862 | 308.7916 | 0.026791 | 0 | 0 | 0.053581 | 309.0403 | 0.02733 | 0 | 0 | 0.05466 | 309.206 | 0.027689 | 0 | 0 | 0.055379 | 309.4546 | 0.028229 | 0 | 0 | 0.056457 | 309.7033 | 0.028768 | 0 | 0 | 0.057536 | 309.869 | 0.029128 | 0 | 0 | 0.058255 | 310.1176 | 0.029667 | 0 | 0 | 0.059334 | 310.3663 | 0.030206 | 0 | 0 | 0.060412 | 310.4491 | 0.030386 | 0 | 0 | 0.060772 | 310.6978 | 0.030925 | 0 | 0 | 0.06185 | 310.9464 | 0.031464 | 0 | 0 | 0.062929 | 311.1121 | 0.031824 | 0 | 0 | 0.063648 | 311.3608 | 0.032363 | 0 | 0 | 0.064726 | 311.5265 | 0.032723 | 0 | 0 | 0.065445 | 311.6923 | 0.033082 | 0 | 0 | 0.066164
2017-12-04 21:00 | 274.2994 | 0.81758 |  | 288.0321 | 0 | 0 | 0 | 0 | 296.1261 | 0 | 0 | 0 | 0 | 302.7485 | 0.013683 | 0 | 0 | 0.027366 | 302.9937 | 0.014215 | 0 | 0 | 0.02843 | 303.1573 | 0.01457 | 0 | 0 | 0.029139 | 303.4025 | 0.015102 | 0 | 0 | 0.030203 | 303.6478 | 0.015634 | 0 | 0 | 0.031267 | 303.8931 | 0.016166 | 0 | 0 | 0.032331 | 304.2201 | 0.016875 | 0 | 0 | 0.03375 | 304.4654 | 0.017407 | 0 | 0 | 0.034814 | 304.6289 | 0.017762 | 0 | 0 | 0.035523 | 304.8742 | 0.018294 | 0 | 0 | 0.036587 | 305.0377 | 0.018648 | 0 | 0 | 0.037297 | 305.283 | 0.01918 | 0 | 0 | 0.038361 | 305.5282 | 0.019712 | 0 | 0 | 0.039425 | 305.6917 | 0.020067 | 0 | 0 | 0.040134 | 305.937 | 0.020599 | 0 | 0 | 0.041198 | 306.1823 | 0.021131 | 0 | 0 | 0.042262 | 306.2641 | 0.021308 | 0 | 0 | 0.042617 | 306.5093 | 0.02184 | 0 | 0 | 0.043681 | 306.7546 | 0.022372 | 0 | 0 | 0.044745 | 306.9181 | 0.022727 | 0 | 0 | 0.045454 | 307.1634 | 0.023259 | 0 | 0 | 0.046518 | 307.3269 | 0.023614 | 0 | 0 | 0.047227 | 307.4904 | 0.023968 | 0 | 0 | 0.047937
2017-12-04 22:00 | 277.6719 | 0.82763 |  | 291.5734 | 0 | 0 | 0 | 0 | 299.7669 | 0.0072161 | 0 | 0 | 0.014432 | 306.4707 | 0.021757 | 0 | 0 | 0.043513 | 306.719 | 0.022295 | 0 | 0 | 0.04459 | 306.8845 | 0.022654 | 0 | 0 | 0.045308 | 307.1328 | 0.023193 | 0 | 0 | 0.046386 | 307.3811 | 0.023731 | 0 | 0 | 0.047463 | 307.6294 | 0.02427 | 0 | 0 | 0.04854 | 307.9605 | 0.024988 | 0 | 0 | 0.049976 | 308.2088 | 0.025526 | 0 | 0 | 0.051053 | 308.3743 | 0.025885 | 0 | 0 | 0.051771 | 308.6226 | 0.026424 | 0 | 0 | 0.052848 | 308.7881 | 0.026783 | 0 | 0 | 0.053566 | 309.0364 | 0.027322 | 0 | 0 | 0.054643 | 309.2847 | 0.02786 | 0 | 0 | 0.05572 | 309.4502 | 0.028219 | 0 | 0 | 0.056438 | 309.6985 | 0.028758 | 0 | 0 | 0.057515 | 309.9468 | 0.029296 | 0 | 0 | 0.058592 | 310.0295 | 0.029476 | 0 | 0 | 0.058951 | 310.2778 | 0.030014 | 0 | 0 | 0.060028 | 310.5261 | 0.030553 | 0 | 0 | 0.061106 | 310.6916 | 0.030912 | 0 | 0 | 0.061824 | 310.9399 | 0.03145 | 0 | 0 | 0.062901 | 311.1055 | 0.031809 | 0 | 0 | 0.063619 | 311.271 | 0.032168 | 0 | 0 | 0.064337
2017-12-04 23:00 | 282.0672 | 0.84073 |  | 296.1889 | 0 | 0 | 0 | 0 | 304.5121 | 0.017508 | 0 | 0 | 0.035017 | 311.322 | 0.032279 | 0 | 0 | 0.064558 | 311.5742 | 0.032826 | 0 | 0 | 0.065652 | 311.7424 | 0.033191 | 0 | 0 | 0.066382 | 311.9946 | 0.033738 | 0 | 0 | 0.067476 | 312.2468 | 0.034285 | 0 | 0 | 0.06857 | 312.499 | 0.034832 | 0 | 0 | 0.069664 | 312.8353 | 0.035561 | 0 | 0 | 0.071123 | 313.0875 | 0.036108 | 0 | 0 | 0.072217 | 313.2557 | 0.036473 | 0 | 0 | 0.072946 | 313.5079 | 0.03702 | 0 | 0 | 0.07404 | 313.676 | 0.037385 | 0 | 0 | 0.07477 | 313.9282 | 0.037932 | 0 | 0 | 0.075864 | 314.1805 | 0.038479 | 0 | 0 | 0.076958 | 314.3486 | 0.038844 | 0 | 0 | 0.077688 | 314.6008 | 0.039391 | 0 | 0 | 0.078782 | 314.8531 | 0.039938 | 0 | 0 | 0.079876 | 314.9371 | 0.04012 | 0 | 0 | 0.080241 | 315.1893 | 0.040667 | 0 | 0 | 0.081335 | 315.4416 | 0.041214 | 0 | 0 | 0.082429 | 315.6097 | 0.041579 | 0 | 0 | 0.083158 | 315.8619 | 0.042126 | 0 | 0 | 0.084252 | 316.0301 | 0.042491 | 0 | 0 | 0.084982 | 316.1982 | 0.042856 | 0 | 0 | 0.085711
2017-12-05 | 284.2931 | 0.84736 |  | 298.5261 | 0.0045249 | 0 | 0 | 0.0090497 | 306.915 | 0.02272 | 0 | 0 | 0.045441 | 313.7787 | 0.037608 | 0 | 0 | 0.075215 | 314.0329 | 0.038159 | 0 | 0 | 0.076318 | 314.2024 | 0.038527 | 0 | 0 | 0.077053 | 314.4566 | 0.039078 | 0 | 0 | 0.078156 | 314.7108 | 0.039629 | 0 | 0 | 0.079259 | 314.965 | 0.040181 | 0 | 0 | 0.080361 | 315.3039 | 0.040916 | 0 | 0 | 0.081832 | 315.5582 | 0.041467 | 0 | 0 | 0.082935 | 315.7276 | 0.041835 | 0 | 0 | 0.08367 | 315.9818 | 0.042386 | 0 | 0 | 0.084772 | 316.1513 | 0.042754 | 0 | 0 | 0.085508 | 316.4055 | 0.043305 | 0 | 0 | 0.08661 | 316.6597 | 0.043857 | 0 | 0 | 0.087713 | 316.8292 | 0.044224 | 0 | 0 | 0.088448 | 317.0834 | 0.044776 | 0 | 0 | 0.089551 | 317.3376 | 0.045327 | 0 | 0 | 0.090654 | 317.4224 | 0.045511 | 0 | 0 | 0.091021 | 317.6766 | 0.046062 | 0 | 0 | 0.092124 | 317.9308 | 0.046613 | 0 | 0 | 0.093227 | 318.1002 | 0.046981 | 0 | 0 | 0.093962 | 318.3545 | 0.047532 | 0 | 0 | 0.095065 | 318.5239 | 0.0479 | 0 | 0 | 0.0958 | 318.6934 | 0.048268 | 0 | 0 | 0.096535
2017-12-05 01:00 | 286.296 | 0.85333 |  | 300.6293 | 0.0090866 | 0 | 0 | 0.018173 | 309.0773 | 0.02741 | 0 | 0 | 0.054821 | 315.9893 | 0.042402 | 0 | 0 | 0.084805 | 316.2453 | 0.042958 | 0 | 0 | 0.085915 | 316.416 | 0.043328 | 0 | 0 | 0.086656 | 316.672 | 0.043883 | 0 | 0 | 0.087766 | 316.928 | 0.044438 | 0 | 0 | 0.088877 | 317.184 | 0.044994 | 0 | 0 | 0.089987 | 317.5253 | 0.045734 | 0 | 0 | 0.091468 | 317.7813 | 0.046289 | 0 | 0 | 0.092579 | 317.952 | 0.046659 | 0 | 0 | 0.093319 | 318.208 | 0.047215 | 0 | 0 | 0.09443 | 318.3787 | 0.047585 | 0 | 0 | 0.09517 | 318.6347 | 0.04814 | 0 | 0 | 0.09628 | 318.8907 | 0.048695 | 0 | 0 | 0.097391 | 319.0613 | 0.049066 | 0 | 0 | 0.098131 | 319.3173 | 0.049621 | 0 | 0 | 0.099242 | 319.5733 | 0.050176 | 0 | 0 | 0.10035 | 319.6587 | 0.050361 | 0 | 0 | 0.10072 | 319.9147 | 0.050917 | 0 | 0 | 0.10183 | 320.1707 | 0.051472 | 0 | 0 | 0.10294 | 320.3413 | 0.051842 | 0 | 0 | 0.10368 | 320.5973 | 0.052397 | 0 | 0 | 0.10479 | 320.768 | 0.052767 | 0 | 0 | 0.10553 | 320.9387 | 0.053138 | 0 | 0 | 0.10628
2017-12-05 02:00 | 290.9135 | 0.8671 |  | 305.478 | 0.019603 | 0 | 0 | 0.039207 | 314.0622 | 0.038223 | 0 | 0 | 0.076445 | 321.0857 | 0.053456 | 0 | 0 | 0.10691 | 321.3458 | 0.054021 | 0 | 0 | 0.10804 | 321.5192 | 0.054397 | 0 | 0 | 0.10879 | 321.7794 | 0.054961 | 0 | 0 | 0.10992 | 322.0395 | 0.055525 | 0 | 0 | 0.11105 | 322.2996 | 0.05609 | 0 | 0 | 0.11218 | 322.6465 | 0.056842 | 0 | 0 | 0.11368 | 322.9066 | 0.057406 | 0 | 0 | 0.11481 | 323.08 | 0.057782 | 0 | 0 | 0.11556 | 323.3401 | 0.058346 | 0 | 0 | 0.11669 | 323.5136 | 0.058723 | 0 | 0 | 0.11745 | 323.7737 | 0.059287 | 0 | 0 | 0.11857 | 324.0338 | 0.059851 | 0 | 0 | 0.1197 | 324.2072 | 0.060227 | 0 | 0 | 0.12045 | 324.4674 | 0.060791 | 0 | 0 | 0.12158 | 324.7275 | 0.061356 | 0 | 0 | 0.12271 | 324.8142 | 0.061544 | 0 | 0 | 0.12309 | 325.0743 | 0.062108 | 0 | 0 | 0.12422 | 325.3345 | 0.062672 | 0 | 0 | 0.12534 | 325.5079 | 0.063048 | 0 | 0 | 0.1261 | 325.768 | 0.063612 | 0 | 0 | 0.12722 | 325.9414 | 0.063989 | 0 | 0 | 0.12798 | 326.1148 | 0.064365 | 0 | 0 | 0.12873
2017-12-05 03:00 | 290.9916 | 0.86733 |  | 305.56 | 0.019781 | 0 | 0 | 0.039562 | 314.1465 | 0.038405 | 0 | 0 | 0.076811 | 321.1719 | 0.053643 | 0 | 0 | 0.10729 | 321.4321 | 0.054208 | 0 | 0 | 0.10842 | 321.6056 | 0.054584 | 0 | 0 | 0.10917 | 321.8658 | 0.055148 | 0 | 0 | 0.1103 | 322.126 | 0.055713 | 0 | 0 | 0.11143 | 322.3862 | 0.056277 | 0 | 0 | 0.11255 | 322.7331 | 0.05703 | 0 | 0 | 0.11406 | 322.9933 | 0.057594 | 0 | 0 | 0.11519 | 323.1668 | 0.05797 | 0 | 0 | 0.11594 | 323.427 | 0.058535 | 0 | 0 | 0.11707 | 323.6004 | 0.058911 | 0 | 0 | 0.11782 | 323.8606 | 0.059475 | 0 | 0 | 0.11895 | 324.1208 | 0.06004 | 0 | 0 | 0.12008 | 324.2943 | 0.060416 | 0 | 0 | 0.12083 | 324.5545 | 0.06098 | 0 | 0 | 0.12196 | 324.8147 | 0.061545 | 0 | 0 | 0.12309 | 324.9014 | 0.061733 | 0 | 0 | 0.12347 | 325.1616 | 0.062297 | 0 | 0 | 0.12459 | 325.4218 | 0.062862 | 0 | 0 | 0.12572 | 325.5953 | 0.063238 | 0 | 0 | 0.12648 | 325.8555 | 0.063802 | 0 | 0 | 0.1276 | 326.0289 | 0.064178 | 0 | 0 | 0.12836 | 326.2024 | 0.064555 | 0 | 0 | 0.12911
2017-12-05 04:00 | 294.0084 | 0.87632 |  | 308.7278 | 0.026652 | 0 | 0 | 0.053305 | 317.4034 | 0.04547 | 0 | 0 | 0.090939 | 324.5016 | 0.060866 | 0 | 0 | 0.12173 | 324.7645 | 0.061436 | 0 | 0 | 0.12287 | 324.9398 | 0.061816 | 0 | 0 | 0.12363 | 325.2026 | 0.062386 | 0 | 0 | 0.12477 | 325.4655 | 0.062956 | 0 | 0 | 0.12591 | 325.7284 | 0.063527 | 0 | 0 | 0.12705 | 326.079 | 0.064287 | 0 | 0 | 0.12857 | 326.3419 | 0.064857 | 0 | 0 | 0.12971 | 326.5171 | 0.065237 | 0 | 0 | 0.13047 | 326.78 | 0.065808 | 0 | 0 | 0.13162 | 326.9553 | 0.066188 | 0 | 0 | 0.13238 | 327.2182 | 0.066758 | 0 | 0 | 0.13352 | 327.4811 | 0.067328 | 0 | 0 | 0.13466 | 327.6563 | 0.067708 | 0 | 0 | 0.13542 | 327.9192 | 0.068278 | 0 | 0 | 0.13656 | 328.1821 | 0.068849 | 0 | 0 | 0.1377 | 328.2698 | 0.069039 | 0 | 0 | 0.13808 | 328.5327 | 0.069609 | 0 | 0 | 0.13922 | 328.7956 | 0.070179 | 0 | 0 | 0.14036 | 328.9708 | 0.070559 | 0 | 0 | 0.14112 | 329.2337 | 0.07113 | 0 | 0 | 0.14226 | 329.409 | 0.07151 | 0 | 0 | 0.14302 | 329.5843 | 0.07189 | 0 | 0 | 0.14378
2017-12-05 05:00 | 297.9518 | 0.88807 |  | 312.8687 | 0.035634 | 0 | 0 | 0.071268 | 321.6606 | 0.054704 | 0 | 0 | 0.10941 | 328.854 | 0.070306 | 0 | 0 | 0.14061 | 329.1205 | 0.070884 | 0 | 0 | 0.14177 | 329.2981 | 0.071269 | 0 | 0 | 0.14254 | 329.5645 | 0.071847 | 0 | 0 | 0.14369 | 329.8309 | 0.072425 | 0 | 0 | 0.14485 | 330.0973 | 0.073003 | 0 | 0 | 0.14601 | 330.4526 | 0.073773 | 0 | 0 | 0.14755 | 330.719 | 0.074351 | 0 | 0 | 0.1487 | 330.8966 | 0.074736 | 0 | 0 | 0.14947 | 331.163 | 0.075314 | 0 | 0 | 0.15063 | 331.3406 | 0.075699 | 0 | 0 | 0.1514 | 331.6071 | 0.076277 | 0 | 0 | 0.15255 | 331.8735 | 0.076855 | 0 | 0 | 0.15371 | 332.0511 | 0.07724 | 0 | 0 | 0.15448 | 332.3175 | 0.077818 | 0 | 0 | 0.15564 | 332.5839 | 0.078396 | 0 | 0 | 0.15679 | 332.6728 | 0.078589 | 0 | 0 | 0.15718 | 332.9392 | 0.079167 | 0 | 0 | 0.15833 | 333.2056 | 0.079745 | 0 | 0 | 0.15949 | 333.3832 | 0.08013 | 0 | 0 | 0.16026 | 333.6496 | 0.080708 | 0 | 0 | 0.16142 | 333.8272 | 0.081093 | 0 | 0 | 0.16219 | 334.0049 | 0.081478 | 0 | 0 | 0.16296
2017-12-05 06:00 | 301.0069 | 0.89718 |  | 316.0767 | 0.042592 | 0 | 0 | 0.085184 | 324.9588 | 0.061857 | 0 | 0 | 0.12371 | 332.226 | 0.07762 | 0 | 0 | 0.15524 | 332.4951 | 0.078204 | 0 | 0 | 0.15641 | 332.6746 | 0.078593 | 0 | 0 | 0.15719 | 332.9437 | 0.079177 | 0 | 0 | 0.15835 | 333.2129 | 0.07976 | 0 | 0 | 0.15952 | 333.482 | 0.080344 | 0 | 0 | 0.16069 | 333.8409 | 0.081123 | 0 | 0 | 0.16225 | 334.1101 | 0.081706 | 0 | 0 | 0.16341 | 334.2895 | 0.082096 | 0 | 0 | 0.16419 | 334.5587 | 0.082679 | 0 | 0 | 0.16536 | 334.7381 | 0.083069 | 0 | 0 | 0.16614 | 335.0072 | 0.083652 | 0 | 0 | 0.1673 | 335.2764 | 0.084236 | 0 | 0 | 0.16847 | 335.4558 | 0.084625 | 0 | 0 | 0.16925 | 335.725 | 0.085209 | 0 | 0 | 0.17042 | 335.9941 | 0.085793 | 0 | 0 | 0.17159 | 336.0839 | 0.085988 | 0 | 0 | 0.17198 | 336.353 | 0.086571 | 0 | 0 | 0.17314 | 336.6222 | 0.087155 | 0 | 0 | 0.17431 | 336.8016 | 0.087544 | 0 | 0 | 0.17509 | 337.0708 | 0.088128 | 0 | 0 | 0.17626 | 337.2502 | 0.088517 | 0 | 0 | 0.17703 | 337.4296 | 0.088907 | 0 | 0 | 0.17781
2017-12-05 07:00 | 299.5928 | 0.89297 |  | 314.5918 | 0.039371 | 0 | 0 | 0.078742 | 323.4322 | 0.058546 | 0 | 0 | 0.11709 | 330.6652 | 0.074234 | 0 | 0 | 0.14847 | 330.9331 | 0.074815 | 0 | 0 | 0.14963 | 331.1117 | 0.075203 | 0 | 0 | 0.15041 | 331.3795 | 0.075784 | 0 | 0 | 0.15157 | 331.6474 | 0.076365 | 0 | 0 | 0.15273 | 331.9153 | 0.076946 | 0 | 0 | 0.15389 | 332.2725 | 0.077721 | 0 | 0 | 0.15544 | 332.5404 | 0.078302 | 0 | 0 | 0.1566 | 332.719 | 0.078689 | 0 | 0 | 0.15738 | 332.9869 | 0.07927 | 0 | 0 | 0.15854 | 333.1655 | 0.079658 | 0 | 0 | 0.15932 | 333.4334 | 0.080239 | 0 | 0 | 0.16048 | 333.7013 | 0.08082 | 0 | 0 | 0.16164 | 333.8799 | 0.081207 | 0 | 0 | 0.16241 | 334.1477 | 0.081788 | 0 | 0 | 0.16358 | 334.4156 | 0.082369 | 0 | 0 | 0.16474 | 334.5049 | 0.082563 | 0 | 0 | 0.16513 | 334.7728 | 0.083144 | 0 | 0 | 0.16629 | 335.0407 | 0.083725 | 0 | 0 | 0.16745 | 335.2193 | 0.084112 | 0 | 0 | 0.16822 | 335.4872 | 0.084693 | 0 | 0 | 0.16939 | 335.6658 | 0.085081 | 0 | 0 | 0.17016 | 335.8444 | 0.085468 | 0 | 0 | 0.17094
2017-12-05 08:00 | 294.1739 | 0.87681 |  | 308.9017 | 0.027029 | 0 | 0 | 0.054059 | 317.5821 | 0.045857 | 0 | 0 | 0.091715 | 324.6843 | 0.061262 | 0 | 0 | 0.12252 | 324.9474 | 0.061832 | 0 | 0 | 0.12366 | 325.1227 | 0.062213 | 0 | 0 | 0.12443 | 325.3858 | 0.062783 | 0 | 0 | 0.12557 | 325.6488 | 0.063354 | 0 | 0 | 0.12671 | 325.9119 | 0.063924 | 0 | 0 | 0.12785 | 326.2626 | 0.064685 | 0 | 0 | 0.12937 | 326.5256 | 0.065256 | 0 | 0 | 0.13051 | 326.701 | 0.065636 | 0 | 0 | 0.13127 | 326.964 | 0.066207 | 0 | 0 | 0.13241 | 327.1394 | 0.066587 | 0 | 0 | 0.13317 | 327.4024 | 0.067158 | 0 | 0 | 0.13432 | 327.6655 | 0.067728 | 0 | 0 | 0.13546 | 327.8408 | 0.068108 | 0 | 0 | 0.13622 | 328.1039 | 0.068679 | 0 | 0 | 0.13736 | 328.3669 | 0.06925 | 0 | 0 | 0.1385 | 328.4546 | 0.06944 | 0 | 0 | 0.13888 | 328.7177 | 0.07001 | 0 | 0 | 0.14002 | 328.9807 | 0.070581 | 0 | 0 | 0.14116 | 329.1561 | 0.070961 | 0 | 0 | 0.14192 | 329.4191 | 0.071532 | 0 | 0 | 0.14306 | 329.5945 | 0.071912 | 0 | 0 | 0.14382 | 329.7698 | 0.072292 | 0 | 0 | 0.14458
2017-12-05 09:00 | 286.8864 | 0.85509 |  | 301.2493 | 0.010431 | 0 | 0 | 0.020863 | 309.7147 | 0.028793 | 0 | 0 | 0.057586 | 316.641 | 0.043816 | 0 | 0 | 0.087632 | 316.8975 | 0.044372 | 0 | 0 | 0.088745 | 317.0685 | 0.044743 | 0 | 0 | 0.089487 | 317.3251 | 0.0453 | 0 | 0 | 0.090599 | 317.5816 | 0.045856 | 0 | 0 | 0.091712 | 317.8381 | 0.046413 | 0 | 0 | 0.092825 | 318.1802 | 0.047154 | 0 | 0 | 0.094309 | 318.4367 | 0.047711 | 0 | 0 | 0.095422 | 318.6077 | 0.048082 | 0 | 0 | 0.096164 | 318.8642 | 0.048638 | 0 | 0 | 0.097276 | 319.0353 | 0.049009 | 0 | 0 | 0.098018 | 319.2918 | 0.049566 | 0 | 0 | 0.099131 | 319.5483 | 0.050122 | 0 | 0 | 0.10024 | 319.7193 | 0.050493 | 0 | 0 | 0.10099 | 319.9759 | 0.051049 | 0 | 0 | 0.1021 | 320.2324 | 0.051606 | 0 | 0 | 0.10321 | 320.3179 | 0.051791 | 0 | 0 | 0.10358 | 320.5744 | 0.052348 | 0 | 0 | 0.1047 | 320.831 | 0.052904 | 0 | 0 | 0.10581 | 321.002 | 0.053275 | 0 | 0 | 0.10655 | 321.2585 | 0.053831 | 0 | 0 | 0.10766 | 321.4295 | 0.054202 | 0 | 0 | 0.1084 | 321.6005 | 0.054573 | 0 | 0 | 0.10915
2017-12-05 10:00 | 289.1775 | 0.86192 |  | 303.6551 | 0.01565 | 0 | 0 | 0.031299 | 312.1881 | 0.034158 | 0 | 0 | 0.068315 | 319.1697 | 0.049301 | 0 | 0 | 0.098601 | 319.4283 | 0.049862 | 0 | 0 | 0.099723 | 319.6007 | 0.050235 | 0 | 0 | 0.10047 | 319.8592 | 0.050796 | 0 | 0 | 0.10159 | 320.1178 | 0.051357 | 0 | 0 | 0.10271 | 320.3764 | 0.051918 | 0 | 0 | 0.10384 | 320.7212 | 0.052666 | 0 | 0 | 0.10533 | 320.9797 | 0.053227 | 0 | 0 | 0.10645 | 321.1521 | 0.053601 | 0 | 0 | 0.1072 | 321.4107 | 0.054161 | 0 | 0 | 0.10832 | 321.5831 | 0.054535 | 0 | 0 | 0.10907 | 321.8417 | 0.055096 | 0 | 0 | 0.11019 | 322.1002 | 0.055657 | 0 | 0 | 0.11131 | 322.2726 | 0.056031 | 0 | 0 | 0.11206 | 322.5312 | 0.056592 | 0 | 0 | 0.11318 | 322.7898 | 0.057153 | 0 | 0 | 0.11431 | 322.876 | 0.05734 | 0 | 0 | 0.11468 | 323.1345 | 0.0579 | 0 | 0 | 0.1158 | 323.3931 | 0.058461 | 0 | 0 | 0.11692 | 323.5655 | 0.058835 | 0 | 0 | 0.11767 | 323.8241 | 0.059396 | 0 | 0 | 0.11879 | 323.9965 | 0.05977 | 0 | 0 | 0.11954 | 324.1688 | 0.060144 | 0 | 0 | 0.12029
2017-12-05 11:00 | 296.5546 | 0.88391 |  | 311.4015 | 0.032452 | 0 | 0 | 0.064903 | 320.1523 | 0.051432 | 0 | 0 | 0.10286 | 327.3119 | 0.066961 | 0 | 0 | 0.13392 | 327.5771 | 0.067536 | 0 | 0 | 0.13507 | 327.7539 | 0.06792 | 0 | 0 | 0.13584 | 328.0191 | 0.068495 | 0 | 0 | 0.13699 | 328.2842 | 0.06907 | 0 | 0 | 0.13814 | 328.5494 | 0.069645 | 0 | 0 | 0.13929 | 328.903 | 0.070412 | 0 | 0 | 0.14082 | 329.1681 | 0.070987 | 0 | 0 | 0.14197 | 329.3449 | 0.071371 | 0 | 0 | 0.14274 | 329.6101 | 0.071946 | 0 | 0 | 0.14389 | 329.7869 | 0.072329 | 0 | 0 | 0.14466 | 330.052 | 0.072905 | 0 | 0 | 0.14581 | 330.3172 | 0.07348 | 0 | 0 | 0.14696 | 330.494 | 0.073863 | 0 | 0 | 0.14773 | 330.7592 | 0.074438 | 0 | 0 | 0.14888 | 331.0243 | 0.075013 | 0 | 0 | 0.15003 | 331.1127 | 0.075205 | 0 | 0 | 0.15041 | 331.3779 | 0.07578 | 0 | 0 | 0.15156 | 331.6431 | 0.076355 | 0 | 0 | 0.15271 | 331.8199 | 0.076739 | 0 | 0 | 0.15348 | 332.085 | 0.077314 | 0 | 0 | 0.15463 | 332.2618 | 0.077698 | 0 | 0 | 0.1554 | 332.4386 | 0.078081 | 0 | 0 | 0.15616
2017-12-05 12:00 | 292.3598 | 0.87141 |  | 306.9967 | 0.022898 | 0 | 0 | 0.045795 | 315.6237 | 0.041609 | 0 | 0 | 0.083219 | 322.6821 | 0.056919 | 0 | 0 | 0.11384 | 322.9435 | 0.057486 | 0 | 0 | 0.11497 | 323.1178 | 0.057864 | 0 | 0 | 0.11573 | 323.3792 | 0.058431 | 0 | 0 | 0.11686 | 323.6406 | 0.058998 | 0 | 0 | 0.118 | 323.902 | 0.059565 | 0 | 0 | 0.11913 | 324.2506 | 0.060321 | 0 | 0 | 0.12064 | 324.512 | 0.060888 | 0 | 0 | 0.12178 | 324.6863 | 0.061266 | 0 | 0 | 0.12253 | 324.9477 | 0.061833 | 0 | 0 | 0.12367 | 325.122 | 0.062211 | 0 | 0 | 0.12442 | 325.3834 | 0.062778 | 0 | 0 | 0.12556 | 325.6448 | 0.063345 | 0 | 0 | 0.12669 | 325.8191 | 0.063723 | 0 | 0 | 0.12745 | 326.0805 | 0.06429 | 0 | 0 | 0.12858 | 326.342 | 0.064857 | 0 | 0 | 0.12971 | 326.4291 | 0.065046 | 0 | 0 | 0.13009 | 326.6905 | 0.065613 | 0 | 0 | 0.13123 | 326.952 | 0.06618 | 0 | 0 | 0.13236 | 327.1262 | 0.066558 | 0 | 0 | 0.13312 | 327.3877 | 0.067125 | 0 | 0 | 0.13425 | 327.5619 | 0.067503 | 0 | 0 | 0.13501 | 327.7362 | 0.067882 | 0 | 0 | 0.13576
2017-12-05 13:00 | 287.0886 | 0.8557 |  | 301.4616 | 0.010892 | 0 | 0 | 0.021784 | 309.933 | 0.029266 | 0 | 0 | 0.058533 | 316.8641 | 0.0443 | 0 | 0 | 0.0886 | 317.1208 | 0.044857 | 0 | 0 | 0.089714 | 317.292 | 0.045228 | 0 | 0 | 0.090456 | 317.5487 | 0.045785 | 0 | 0 | 0.09157 | 317.8054 | 0.046342 | 0 | 0 | 0.092683 | 318.0621 | 0.046898 | 0 | 0 | 0.093797 | 318.4044 | 0.047641 | 0 | 0 | 0.095282 | 318.6611 | 0.048198 | 0 | 0 | 0.096395 | 318.8322 | 0.048569 | 0 | 0 | 0.097138 | 319.0889 | 0.049126 | 0 | 0 | 0.098251 | 319.2601 | 0.049497 | 0 | 0 | 0.098994 | 319.5168 | 0.050054 | 0 | 0 | 0.10011 | 319.7735 | 0.05061 | 0 | 0 | 0.10122 | 319.9446 | 0.050982 | 0 | 0 | 0.10196 | 320.2013 | 0.051538 | 0 | 0 | 0.10308 | 320.4581 | 0.052095 | 0 | 0 | 0.10419 | 320.5436 | 0.052281 | 0 | 0 | 0.10456 | 320.8003 | 0.052838 | 0 | 0 | 0.10568 | 321.057 | 0.053394 | 0 | 0 | 0.10679 | 321.2282 | 0.053766 | 0 | 0 | 0.10753 | 321.4849 | 0.054322 | 0 | 0 | 0.10864 | 321.656 | 0.054694 | 0 | 0 | 0.10939 | 321.8272 | 0.055065 | 0 | 0 | 0.11013
2017-12-05 14:00 | 280.29 | 0.83543 |  | 294.3226 | 0 | 0 | 0 | 0 | 302.5934 | 0.013347 | 0 | 0 | 0.026693 | 309.3604 | 0.028024 | 0 | 0 | 0.056049 | 309.611 | 0.028568 | 0 | 0 | 0.057136 | 309.7781 | 0.02893 | 0 | 0 | 0.057861 | 310.0288 | 0.029474 | 0 | 0 | 0.058948 | 310.2794 | 0.030018 | 0 | 0 | 0.060035 | 310.53 | 0.030561 | 0 | 0 | 0.061122 | 310.8642 | 0.031286 | 0 | 0 | 0.062572 | 311.1148 | 0.03183 | 0 | 0 | 0.063659 | 311.2819 | 0.032192 | 0 | 0 | 0.064384 | 311.5325 | 0.032736 | 0 | 0 | 0.065471 | 311.6996 | 0.033098 | 0 | 0 | 0.066196 | 311.9502 | 0.033642 | 0 | 0 | 0.067283 | 312.2009 | 0.034185 | 0 | 0 | 0.068371 | 312.368 | 0.034548 | 0 | 0 | 0.069096 | 312.6186 | 0.035091 | 0 | 0 | 0.070183 | 312.8692 | 0.035635 | 0 | 0 | 0.07127 | 312.9528 | 0.035816 | 0 | 0 | 0.071632 | 313.2034 | 0.03636 | 0 | 0 | 0.07272 | 313.454 | 0.036903 | 0 | 0 | 0.073807 | 313.6211 | 0.037266 | 0 | 0 | 0.074532 | 313.8717 | 0.037809 | 0 | 0 | 0.075619 | 314.0388 | 0.038172 | 0 | 0 | 0.076344 | 314.2059 | 0.038534 | 0 | 0 | 0.077069
2017-12-05 15:00 | 279.1156 | 0.83193 |  | 293.0894 | 0 | 0 | 0 | 0 | 301.3255 | 0.010597 | 0 | 0 | 0.021193 | 308.0642 | 0.025213 | 0 | 0 | 0.050426 | 308.3137 | 0.025754 | 0 | 0 | 0.051508 | 308.4801 | 0.026115 | 0 | 0 | 0.05223 | 308.7297 | 0.026656 | 0 | 0 | 0.053313 | 308.9793 | 0.027198 | 0 | 0 | 0.054395 | 309.2289 | 0.027739 | 0 | 0 | 0.055478 | 309.5616 | 0.028461 | 0 | 0 | 0.056922 | 309.8112 | 0.029002 | 0 | 0 | 0.058004 | 309.9776 | 0.029363 | 0 | 0 | 0.058726 | 310.2272 | 0.029904 | 0 | 0 | 0.059809 | 310.3936 | 0.030265 | 0 | 0 | 0.060531 | 310.6432 | 0.030807 | 0 | 0 | 0.061613 | 310.8927 | 0.031348 | 0 | 0 | 0.062696 | 311.0591 | 0.031709 | 0 | 0 | 0.063418 | 311.3087 | 0.03225 | 0 | 0 | 0.0645 | 311.5583 | 0.032792 | 0 | 0 | 0.065583 | 311.6415 | 0.032972 | 0 | 0 | 0.065944 | 311.8911 | 0.033513 | 0 | 0 | 0.067027 | 312.1406 | 0.034055 | 0 | 0 | 0.068109 | 312.307 | 0.034416 | 0 | 0 | 0.068831 | 312.5566 | 0.034957 | 0 | 0 | 0.069914 | 312.723 | 0.035318 | 0 | 0 | 0.070636 | 312.8894 | 0.035679 | 0 | 0 | 0.071357
2017-12-05 16:00 | 271.8896 | 0.81039 |  | 285.5017 | 0 | 0 | 0 | 0 | 293.5246 | 0 | 0 | 0 | 0 | 300.0888 | 0.0079142 | 0 | 0 | 0.015828 | 300.3319 | 0.0084415 | 0 | 0 | 0.016883 | 300.494 | 0.0087931 | 0 | 0 | 0.017586 | 300.7371 | 0.0093204 | 0 | 0 | 0.018641 | 300.9802 | 0.0098477 | 0 | 0 | 0.019695 | 301.2233 | 0.010375 | 0 | 0 | 0.02075 | 301.5475 | 0.011078 | 0 | 0 | 0.022156 | 301.7906 | 0.011605 | 0 | 0 | 0.023211 | 301.9527 | 0.011957 | 0 | 0 | 0.023914 | 302.1958 | 0.012484 | 0 | 0 | 0.024969 | 302.3579 | 0.012836 | 0 | 0 | 0.025672 | 302.601 | 0.013363 | 0 | 0 | 0.026726 | 302.8441 | 0.013891 | 0 | 0 | 0.027781 | 303.0062 | 0.014242 | 0 | 0 | 0.028484 | 303.2493 | 0.014769 | 0 | 0 | 0.029539 | 303.4924 | 0.015297 | 0 | 0 | 0.030593 | 303.5735 | 0.015473 | 0 | 0 | 0.030945 | 303.8166 | 0.016 | 0 | 0 | 0.032 | 304.0597 | 0.016527 | 0 | 0 | 0.033054 | 304.2218 | 0.016879 | 0 | 0 | 0.033757 | 304.4649 | 0.017406 | 0 | 0 | 0.034812 | 304.627 | 0.017758 | 0 | 0 | 0.035515 | 304.7891 | 0.018109 | 0 | 0 | 0.036218
2017-12-05 17:00 | 268.3126 | 0.79973 |  | 281.7456 | 0 | 0 | 0 | 0 | 289.6629 | 0 | 0 | 0 | 0 | 296.1408 | 0 | 0 | 0 | 0 | 296.3807 | 0 | 0 | 0 | 0 | 296.5406 | 0.00021825 | 0 | 0 | 0.0004365 | 296.7805 | 0.00073863 | 0 | 0 | 0.0014773 | 297.0205 | 0.001259 | 0 | 0 | 0.002518 | 297.2604 | 0.0017794 | 0 | 0 | 0.0035588 | 297.5803 | 0.0024733 | 0 | 0 | 0.0049465 | 297.8202 | 0.0029936 | 0 | 0 | 0.0059873 | 297.9801 | 0.0033406 | 0 | 0 | 0.0066811 | 298.2201 | 0.0038609 | 0 | 0 | 0.0077219 | 298.38 | 0.0042079 | 0 | 0 | 0.0084157 | 298.6199 | 0.0047283 | 0 | 0 | 0.0094565 | 298.8598 | 0.0052486 | 0 | 0 | 0.010497 | 299.0198 | 0.0055956 | 0 | 0 | 0.011191 | 299.2597 | 0.006116 | 0 | 0 | 0.012232 | 299.4996 | 0.0066363 | 0 | 0 | 0.013273 | 299.5796 | 0.0068098 | 0 | 0 | 0.01362 | 299.8195 | 0.0073302 | 0 | 0 | 0.01466 | 300.0594 | 0.0078506 | 0 | 0 | 0.015701 | 300.2194 | 0.0081975 | 0 | 0 | 0.016395 | 300.4593 | 0.0087179 | 0 | 0 | 0.017436 | 300.6193 | 0.0090648 | 0 | 0 | 0.01813 | 300.7792 | 0.0094117 | 0 | 0 | 0.018823
2017-12-05 18:00 | 272.2992 | 0.81161 |  | 285.9318 | 0 | 0 | 0 | 0 | 293.9668 | 0 | 0 | 0 | 0 | 300.5409 | 0.0088948 | 0 | 0 | 0.01779 | 300.7844 | 0.009423 | 0 | 0 | 0.018846 | 300.9467 | 0.009775 | 0 | 0 | 0.01955 | 301.1902 | 0.010303 | 0 | 0 | 0.020606 | 301.4337 | 0.010831 | 0 | 0 | 0.021663 | 301.6772 | 0.011359 | 0 | 0 | 0.022719 | 302.0018 | 0.012064 | 0 | 0 | 0.024127 | 302.2453 | 0.012592 | 0 | 0 | 0.025183 | 302.4076 | 0.012944 | 0 | 0 | 0.025888 | 302.6511 | 0.013472 | 0 | 0 | 0.026944 | 302.8134 | 0.013824 | 0 | 0 | 0.027648 | 303.0569 | 0.014352 | 0 | 0 | 0.028704 | 303.3004 | 0.01488 | 0 | 0 | 0.02976 | 303.4627 | 0.015232 | 0 | 0 | 0.030465 | 303.7062 | 0.01576 | 0 | 0 | 0.031521 | 303.9497 | 0.016288 | 0 | 0 | 0.032577 | 304.0308 | 0.016465 | 0 | 0 | 0.032929 | 304.2743 | 0.016993 | 0 | 0 | 0.033985 | 304.5178 | 0.017521 | 0 | 0 | 0.035042 | 304.6801 | 0.017873 | 0 | 0 | 0.035746 | 304.9236 | 0.018401 | 0 | 0 | 0.036802 | 305.0859 | 0.018753 | 0 | 0 | 0.037506 | 305.2483 | 0.019105 | 0 | 0 | 0.03821
2017-12-05 19:00 | 276.9898 | 0.8256 |  | 290.8572 | 0 | 0 | 0 | 0 | 299.0306 | 0.0056189 | 0 | 0 | 0.011238 | 305.7179 | 0.020124 | 0 | 0 | 0.040247 | 305.9656 | 0.020661 | 0 | 0 | 0.041322 | 306.1307 | 0.021019 | 0 | 0 | 0.042038 | 306.3784 | 0.021556 | 0 | 0 | 0.043113 | 306.626 | 0.022094 | 0 | 0 | 0.044187 | 306.8737 | 0.022631 | 0 | 0 | 0.045261 | 307.204 | 0.023347 | 0 | 0 | 0.046694 | 307.4516 | 0.023884 | 0 | 0 | 0.047768 | 307.6168 | 0.024242 | 0 | 0 | 0.048485 | 307.8644 | 0.02478 | 0 | 0 | 0.049559 | 308.0296 | 0.025138 | 0 | 0 | 0.050275 | 308.2772 | 0.025675 | 0 | 0 | 0.05135 | 308.5249 | 0.026212 | 0 | 0 | 0.052424 | 308.69 | 0.02657 | 0 | 0 | 0.053141 | 308.9377 | 0.027108 | 0 | 0 | 0.054215 | 309.1854 | 0.027645 | 0 | 0 | 0.05529 | 309.2679 | 0.027824 | 0 | 0 | 0.055648 | 309.5156 | 0.028361 | 0 | 0 | 0.056722 | 309.7633 | 0.028898 | 0 | 0 | 0.057797 | 309.9284 | 0.029256 | 0 | 0 | 0.058513 | 310.1761 | 0.029794 | 0 | 0 | 0.059587 | 310.3412 | 0.030152 | 0 | 0 | 0.060304 | 310.5063 | 0.03051 | 0 | 0 | 0.06102
2017-12-05 20:00 | 267.4976 | 0.7973 |  | 280.8898 | 0 | 0 | 0 | 0 | 288.7831 | 0 | 0 | 0 | 0 | 295.2412 | 0 | 0 | 0 | 0 | 295.4804 | 0 | 0 | 0 | 0 | 295.6399 | 0 | 0 | 0 | 0 | 295.8791 | 0 | 0 | 0 | 0 | 296.1182 | 0 | 0 | 0 | 0 | 296.3574 | 0 | 0 | 0 | 0 | 296.6764 | 0.00051265 | 0 | 0 | 0.0010253 | 296.9155 | 0.0010315 | 0 | 0 | 0.0020629 | 297.075 | 0.0013773 | 0 | 0 | 0.0027546 | 297.3142 | 0.0018961 | 0 | 0 | 0.0037923 | 297.4737 | 0.002242 | 0 | 0 | 0.004484 | 297.7128 | 0.0027608 | 0 | 0 | 0.0055216 | 297.952 | 0.0032796 | 0 | 0 | 0.0065592 | 298.1115 | 0.0036255 | 0 | 0 | 0.007251 | 298.3507 | 0.0041443 | 0 | 0 | 0.0082886 | 298.5899 | 0.0046631 | 0 | 0 | 0.0093262 | 298.6696 | 0.004836 | 0 | 0 | 0.009672 | 298.9088 | 0.0053548 | 0 | 0 | 0.01071 | 299.148 | 0.0058736 | 0 | 0 | 0.011747 | 299.3075 | 0.0062195 | 0 | 0 | 0.012439 | 299.5466 | 0.0067383 | 0 | 0 | 0.013477 | 299.7061 | 0.0070842 | 0 | 0 | 0.014168 | 299.8656 | 0.00743 | 0 | 0 | 0.01486
2017-12-05 21:00 | 284.8311 | 0.84897 |  | 299.0911 | 0.0057503 | 0 | 0 | 0.011501 | 307.4959 | 0.02398 | 0 | 0 | 0.04796 | 314.3725 | 0.038896 | 0 | 0 | 0.077791 | 314.6272 | 0.039448 | 0 | 0 | 0.078896 | 314.797 | 0.039816 | 0 | 0 | 0.079633 | 315.0517 | 0.040369 | 0 | 0 | 0.080738 | 315.3064 | 0.040921 | 0 | 0 | 0.081842 | 315.5611 | 0.041474 | 0 | 0 | 0.082947 | 315.9007 | 0.04221 | 0 | 0 | 0.08442 | 316.1554 | 0.042763 | 0 | 0 | 0.085525 | 316.3252 | 0.043131 | 0 | 0 | 0.086262 | 316.5798 | 0.043683 | 0 | 0 | 0.087367 | 316.7496 | 0.044052 | 0 | 0 | 0.088103 | 317.0043 | 0.044604 | 0 | 0 | 0.089208 | 317.259 | 0.045156 | 0 | 0 | 0.090313 | 317.4288 | 0.045525 | 0 | 0 | 0.091049 | 317.6835 | 0.046077 | 0 | 0 | 0.092154 | 317.9382 | 0.04663 | 0 | 0 | 0.093259 | 318.0231 | 0.046814 | 0 | 0 | 0.093627 | 318.2778 | 0.047366 | 0 | 0 | 0.094732 | 318.5325 | 0.047919 | 0 | 0 | 0.095837 | 318.7023 | 0.048287 | 0 | 0 | 0.096574 | 318.957 | 0.048839 | 0 | 0 | 0.097679 | 319.1267 | 0.049208 | 0 | 0 | 0.098415 | 319.2965 | 0.049576 | 0 | 0 | 0.099152
2017-12-05 22:00 | 280.2938 | 0.83544 |  | 294.3267 | 0 | 0 | 0 | 0 | 302.5975 | 0.013356 | 0 | 0 | 0.026711 | 309.3646 | 0.028034 | 0 | 0 | 0.056067 | 309.6153 | 0.028577 | 0 | 0 | 0.057154 | 309.7824 | 0.02894 | 0 | 0 | 0.057879 | 310.033 | 0.029483 | 0 | 0 | 0.058966 | 310.2836 | 0.030027 | 0 | 0 | 0.060054 | 310.5343 | 0.03057 | 0 | 0 | 0.061141 | 310.8684 | 0.031295 | 0 | 0 | 0.062591 | 311.1191 | 0.031839 | 0 | 0 | 0.063678 | 311.2862 | 0.032201 | 0 | 0 | 0.064403 | 311.5368 | 0.032745 | 0 | 0 | 0.06549 | 311.7039 | 0.033107 | 0 | 0 | 0.066215 | 311.9545 | 0.033651 | 0 | 0 | 0.067302 | 312.2051 | 0.034195 | 0 | 0 | 0.068389 | 312.3722 | 0.034557 | 0 | 0 | 0.069114 | 312.6229 | 0.035101 | 0 | 0 | 0.070201 | 312.8735 | 0.035644 | 0 | 0 | 0.071289 | 312.957 | 0.035825 | 0 | 0 | 0.071651 | 313.2077 | 0.036369 | 0 | 0 | 0.072738 | 313.4583 | 0.036913 | 0 | 0 | 0.073825 | 313.6254 | 0.037275 | 0 | 0 | 0.07455 | 313.876 | 0.037819 | 0 | 0 | 0.075637 | 314.0431 | 0.038181 | 0 | 0 | 0.076362 | 314.2102 | 0.038544 | 0 | 0 | 0.077087
2017-12-05 23:00 | 281.2726 | 0.83836 |  | 295.3544 | 0 | 0 | 0 | 0 | 303.6542 | 0.015648 | 0 | 0 | 0.031295 | 310.4449 | 0.030377 | 0 | 0 | 0.060753 | 310.6964 | 0.030922 | 0 | 0 | 0.061844 | 310.8641 | 0.031286 | 0 | 0 | 0.062572 | 311.1156 | 0.031831 | 0 | 0 | 0.063663 | 311.3671 | 0.032377 | 0 | 0 | 0.064754 | 311.6186 | 0.032922 | 0 | 0 | 0.065845 | 311.9539 | 0.03365 | 0 | 0 | 0.0673 | 312.2055 | 0.034195 | 0 | 0 | 0.068391 | 312.3731 | 0.034559 | 0 | 0 | 0.069118 | 312.6246 | 0.035104 | 0 | 0 | 0.070209 | 312.7923 | 0.035468 | 0 | 0 | 0.070936 | 313.0438 | 0.036014 | 0 | 0 | 0.072027 | 313.2953 | 0.036559 | 0 | 0 | 0.073118 | 313.463 | 0.036923 | 0 | 0 | 0.073846 | 313.7145 | 0.037468 | 0 | 0 | 0.074937 | 313.966 | 0.038014 | 0 | 0 | 0.076028 | 314.0498 | 0.038196 | 0 | 0 | 0.076392 | 314.3014 | 0.038741 | 0 | 0 | 0.077483 | 314.5529 | 0.039287 | 0 | 0 | 0.078574 | 314.7205 | 0.03965 | 0 | 0 | 0.079301 | 314.972 | 0.040196 | 0 | 0 | 0.080392 | 315.1397 | 0.04056 | 0 | 0 | 0.081119 | 315.3074 | 0.040923 | 0 | 0 | 0.081847
2017-12-06 | 276.4043 | 0.82385 |  | 290.2424 | 0 | 0 | 0 | 0 | 298.3985 | 0.004248 | 0 | 0 | 0.0084959 | 305.0717 | 0.018722 | 0 | 0 | 0.037444 | 305.3188 | 0.019258 | 0 | 0 | 0.038516 | 305.4836 | 0.019616 | 0 | 0 | 0.039231 | 305.7308 | 0.020152 | 0 | 0 | 0.040303 | 305.9779 | 0.020688 | 0 | 0 | 0.041375 | 306.2251 | 0.021224 | 0 | 0 | 0.042448 | 306.5546 | 0.021939 | 0 | 0 | 0.043877 | 306.8018 | 0.022475 | 0 | 0 | 0.044949 | 306.9665 | 0.022832 | 0 | 0 | 0.045664 | 307.2137 | 0.023368 | 0 | 0 | 0.046736 | 307.3785 | 0.023726 | 0 | 0 | 0.047451 | 307.6256 | 0.024262 | 0 | 0 | 0.048523 | 307.8728 | 0.024798 | 0 | 0 | 0.049595 | 308.0375 | 0.025155 | 0 | 0 | 0.05031 | 308.2847 | 0.025691 | 0 | 0 | 0.051382 | 308.5318 | 0.026227 | 0 | 0 | 0.052454 | 308.6142 | 0.026406 | 0 | 0 | 0.052812 | 308.8614 | 0.026942 | 0 | 0 | 0.053884 | 309.1085 | 0.027478 | 0 | 0 | 0.054956 | 309.2733 | 0.027835 | 0 | 0 | 0.055671 | 309.5205 | 0.028372 | 0 | 0 | 0.056743 | 309.6852 | 0.028729 | 0 | 0 | 0.057458 | 309.85 | 0.029086 | 0 | 0 | 0.058173
2017-12-06 01:00 | 280.0159 | 0.83461 |  | 294.0348 | 0 | 0 | 0 | 0 | 302.2975 | 0.012705 | 0 | 0 | 0.02541 | 309.0579 | 0.027368 | 0 | 0 | 0.054736 | 309.3082 | 0.027911 | 0 | 0 | 0.055822 | 309.4752 | 0.028273 | 0 | 0 | 0.056547 | 309.7255 | 0.028816 | 0 | 0 | 0.057633 | 309.9759 | 0.029359 | 0 | 0 | 0.058719 | 310.2263 | 0.029903 | 0 | 0 | 0.059805 | 310.5602 | 0.030627 | 0 | 0 | 0.061253 | 310.8105 | 0.03117 | 0 | 0 | 0.062339 | 310.9775 | 0.031532 | 0 | 0 | 0.063064 | 311.2279 | 0.032075 | 0 | 0 | 0.06415 | 311.3948 | 0.032437 | 0 | 0 | 0.064874 | 311.6452 | 0.03298 | 0 | 0 | 0.06596 | 311.8955 | 0.033523 | 0 | 0 | 0.067046 | 312.0625 | 0.033885 | 0 | 0 | 0.06777 | 312.3129 | 0.034428 | 0 | 0 | 0.068856 | 312.5632 | 0.034971 | 0 | 0 | 0.069943 | 312.6467 | 0.035152 | 0 | 0 | 0.070305 | 312.8971 | 0.035695 | 0 | 0 | 0.071391 | 313.1475 | 0.036238 | 0 | 0 | 0.072477 | 313.3144 | 0.036601 | 0 | 0 | 0.073201 | 313.5648 | 0.037144 | 0 | 0 | 0.074287 | 313.7317 | 0.037506 | 0 | 0 | 0.075011 | 313.8986 | 0.037868 | 0 | 0 | 0.075735
2017-12-06 02:00 | 277.7235 | 0.82778 |  | 291.6276 | 0 | 0 | 0 | 0 | 299.8227 | 0.007337 | 0 | 0 | 0.014674 | 306.5277 | 0.02188 | 0 | 0 | 0.04376 | 306.776 | 0.022419 | 0 | 0 | 0.044838 | 306.9416 | 0.022778 | 0 | 0 | 0.045556 | 307.1899 | 0.023317 | 0 | 0 | 0.046633 | 307.4383 | 0.023855 | 0 | 0 | 0.04771 | 307.6866 | 0.024394 | 0 | 0 | 0.048788 | 308.0177 | 0.025112 | 0 | 0 | 0.050224 | 308.266 | 0.025651 | 0 | 0 | 0.051301 | 308.4316 | 0.02601 | 0 | 0 | 0.05202 | 308.6799 | 0.026548 | 0 | 0 | 0.053097 | 308.8455 | 0.026907 | 0 | 0 | 0.053815 | 309.0938 | 0.027446 | 0 | 0 | 0.054892 | 309.3421 | 0.027985 | 0 | 0 | 0.05597 | 309.5077 | 0.028344 | 0 | 0 | 0.056688 | 309.756 | 0.028882 | 0 | 0 | 0.057765 | 310.0044 | 0.029421 | 0 | 0 | 0.058842 | 310.0872 | 0.029601 | 0 | 0 | 0.059201 | 310.3355 | 0.030139 | 0 | 0 | 0.060279 | 310.5838 | 0.030678 | 0 | 0 | 0.061356 | 310.7494 | 0.031037 | 0 | 0 | 0.062074 | 310.9977 | 0.031576 | 0 | 0 | 0.063151 | 311.1633 | 0.031935 | 0 | 0 | 0.06387 | 311.3288 | 0.032294 | 0 | 0 | 0.064588
2017-12-06 03:00 | 277.3575 | 0.82669 |  | 291.2434 | 0 | 0 | 0 | 0 | 299.4276 | 0.0064801 | 0 | 0 | 0.01296 | 306.1238 | 0.021004 | 0 | 0 | 0.042008 | 306.3718 | 0.021542 | 0 | 0 | 0.043084 | 306.5372 | 0.021901 | 0 | 0 | 0.043801 | 306.7852 | 0.022439 | 0 | 0 | 0.044877 | 307.0332 | 0.022977 | 0 | 0 | 0.045953 | 307.2812 | 0.023515 | 0 | 0 | 0.047029 | 307.6119 | 0.024232 | 0 | 0 | 0.048464 | 307.8599 | 0.02477 | 0 | 0 | 0.049539 | 308.0252 | 0.025128 | 0 | 0 | 0.050257 | 308.2732 | 0.025666 | 0 | 0 | 0.051332 | 308.4386 | 0.026025 | 0 | 0 | 0.05205 | 308.6866 | 0.026563 | 0 | 0 | 0.053126 | 308.9346 | 0.027101 | 0 | 0 | 0.054201 | 309.0999 | 0.027459 | 0 | 0 | 0.054919 | 309.3479 | 0.027997 | 0 | 0 | 0.055995 | 309.5959 | 0.028535 | 0 | 0 | 0.05707 | 309.6786 | 0.028715 | 0 | 0 | 0.057429 | 309.9266 | 0.029252 | 0 | 0 | 0.058505 | 310.1746 | 0.02979 | 0 | 0 | 0.059581 | 310.3399 | 0.030149 | 0 | 0 | 0.060298 | 310.588 | 0.030687 | 0 | 0 | 0.061374 | 310.7533 | 0.031046 | 0 | 0 | 0.062091 | 310.9186 | 0.031404 | 0 | 0 | 0.062808
2017-12-06 04:00 | 270.7733 | 0.80707 |  | 284.3295 | 0 | 0 | 0 | 0 | 292.3195 | 0 | 0 | 0 | 0 | 298.8567 | 0.0052419 | 0 | 0 | 0.010484 | 299.0988 | 0.005767 | 0 | 0 | 0.011534 | 299.2603 | 0.0061171 | 0 | 0 | 0.012234 | 299.5024 | 0.0066423 | 0 | 0 | 0.013285 | 299.7445 | 0.0071674 | 0 | 0 | 0.014335 | 299.9866 | 0.0076926 | 0 | 0 | 0.015385 | 300.3094 | 0.0083928 | 0 | 0 | 0.016786 | 300.5516 | 0.008918 | 0 | 0 | 0.017836 | 300.713 | 0.0092681 | 0 | 0 | 0.018536 | 300.9551 | 0.0097932 | 0 | 0 | 0.019586 | 301.1165 | 0.010143 | 0 | 0 | 0.020287 | 301.3586 | 0.010668 | 0 | 0 | 0.021337 | 301.6007 | 0.011194 | 0 | 0 | 0.022387 | 301.7622 | 0.011544 | 0 | 0 | 0.023088 | 302.0043 | 0.012069 | 0 | 0 | 0.024138 | 302.2464 | 0.012594 | 0 | 0 | 0.025188 | 302.3271 | 0.012769 | 0 | 0 | 0.025538 | 302.5692 | 0.013294 | 0 | 0 | 0.026589 | 302.8113 | 0.013819 | 0 | 0 | 0.027639 | 302.9728 | 0.01417 | 0 | 0 | 0.028339 | 303.2149 | 0.014695 | 0 | 0 | 0.029389 | 303.3763 | 0.015045 | 0 | 0 | 0.03009 | 303.5377 | 0.015395 | 0 | 0 | 0.03079
2017-12-06 05:00 | 273.6373 | 0.8156 |  | 287.3369 | 0 | 0 | 0 | 0 | 295.4113 | 0 | 0 | 0 | 0 | 302.0177 | 0.012098 | 0 | 0 | 0.024196 | 302.2624 | 0.012629 | 0 | 0 | 0.025257 | 302.4255 | 0.012983 | 0 | 0 | 0.025965 | 302.6702 | 0.013513 | 0 | 0 | 0.027027 | 302.9149 | 0.014044 | 0 | 0 | 0.028088 | 303.1595 | 0.014575 | 0 | 0 | 0.029149 | 303.4858 | 0.015282 | 0 | 0 | 0.030565 | 303.7305 | 0.015813 | 0 | 0 | 0.031626 | 303.8936 | 0.016167 | 0 | 0 | 0.032334 | 304.1383 | 0.016698 | 0 | 0 | 0.033395 | 304.3014 | 0.017051 | 0 | 0 | 0.034103 | 304.5461 | 0.017582 | 0 | 0 | 0.035164 | 304.7907 | 0.018113 | 0 | 0 | 0.036226 | 304.9539 | 0.018467 | 0 | 0 | 0.036933 | 305.1986 | 0.018997 | 0 | 0 | 0.037995 | 305.4432 | 0.019528 | 0 | 0 | 0.039056 | 305.5248 | 0.019705 | 0 | 0 | 0.03941 | 305.7695 | 0.020236 | 0 | 0 | 0.040471 | 306.0142 | 0.020766 | 0 | 0 | 0.041533 | 306.1773 | 0.02112 | 0 | 0 | 0.04224 | 306.422 | 0.021651 | 0 | 0 | 0.043302 | 306.5851 | 0.022005 | 0 | 0 | 0.044009 | 306.7482 | 0.022358 | 0 | 0 | 0.044717
2017-12-06 06:00 | 272.6484 | 0.81266 |  | 286.2984 | 0 | 0 | 0 | 0 | 294.3437 | 0 | 0 | 0 | 0 | 300.9262 | 0.0097307 | 0 | 0 | 0.019461 | 301.17 | 0.010259 | 0 | 0 | 0.020519 | 301.3326 | 0.010612 | 0 | 0 | 0.021224 | 301.5764 | 0.011141 | 0 | 0 | 0.022282 | 301.8202 | 0.01167 | 0 | 0 | 0.023339 | 302.064 | 0.012198 | 0 | 0 | 0.024397 | 302.389 | 0.012903 | 0 | 0 | 0.025807 | 302.6328 | 0.013432 | 0 | 0 | 0.026864 | 302.7953 | 0.013785 | 0 | 0 | 0.02757 | 303.0391 | 0.014314 | 0 | 0 | 0.028627 | 303.2017 | 0.014666 | 0 | 0 | 0.029332 | 303.4455 | 0.015195 | 0 | 0 | 0.03039 | 303.6893 | 0.015724 | 0 | 0 | 0.031447 | 303.8518 | 0.016076 | 0 | 0 | 0.032152 | 304.0956 | 0.016605 | 0 | 0 | 0.03321 | 304.3394 | 0.017134 | 0 | 0 | 0.034268 | 304.4207 | 0.01731 | 0 | 0 | 0.03462 | 304.6645 | 0.017839 | 0 | 0 | 0.035678 | 304.9083 | 0.018368 | 0 | 0 | 0.036735 | 305.0708 | 0.01872 | 0 | 0 | 0.03744 | 305.3146 | 0.019249 | 0 | 0 | 0.038498 | 305.4771 | 0.019601 | 0 | 0 | 0.039203 | 305.6396 | 0.019954 | 0 | 0 | 0.039908
2017-12-06 07:00 | 272.8718 | 0.81332 |  | 286.5331 | 0 | 0 | 0 | 0 | 294.585 | 0 | 0 | 0 | 0 | 301.1729 | 0.010266 | 0 | 0 | 0.020531 | 301.4169 | 0.010795 | 0 | 0 | 0.02159 | 301.5795 | 0.011148 | 0 | 0 | 0.022295 | 301.8235 | 0.011677 | 0 | 0 | 0.023354 | 302.0675 | 0.012206 | 0 | 0 | 0.024412 | 302.3115 | 0.012735 | 0 | 0 | 0.025471 | 302.6369 | 0.013441 | 0 | 0 | 0.026882 | 302.8809 | 0.01397 | 0 | 0 | 0.02794 | 303.0435 | 0.014323 | 0 | 0 | 0.028646 | 303.2875 | 0.014852 | 0 | 0 | 0.029705 | 303.4502 | 0.015205 | 0 | 0 | 0.03041 | 303.6942 | 0.015734 | 0 | 0 | 0.031469 | 303.9382 | 0.016264 | 0 | 0 | 0.032527 | 304.1008 | 0.016616 | 0 | 0 | 0.033233 | 304.3448 | 0.017146 | 0 | 0 | 0.034291 | 304.5888 | 0.017675 | 0 | 0 | 0.03535 | 304.6702 | 0.017851 | 0 | 0 | 0.035702 | 304.9142 | 0.01838 | 0 | 0 | 0.036761 | 305.1582 | 0.01891 | 0 | 0 | 0.037819 | 305.3208 | 0.019263 | 0 | 0 | 0.038525 | 305.5648 | 0.019792 | 0 | 0 | 0.039583 | 305.7275 | 0.020145 | 0 | 0 | 0.040289 | 305.8902 | 0.020497 | 0 | 0 | 0.040995
2017-12-06 08:00 | 271.5823 | 0.80948 |  | 285.179 | 0 | 0 | 0 | 0 | 293.1928 | 0 | 0 | 0 | 0 | 299.7496 | 0.0071785 | 0 | 0 | 0.014357 | 299.9924 | 0.0077052 | 0 | 0 | 0.01541 | 300.1543 | 0.0080564 | 0 | 0 | 0.016113 | 300.3972 | 0.0085831 | 0 | 0 | 0.017166 | 300.64 | 0.0091098 | 0 | 0 | 0.01822 | 300.8829 | 0.0096366 | 0 | 0 | 0.019273 | 301.2067 | 0.010339 | 0 | 0 | 0.020678 | 301.4495 | 0.010866 | 0 | 0 | 0.021731 | 301.6114 | 0.011217 | 0 | 0 | 0.022434 | 301.8542 | 0.011743 | 0 | 0 | 0.023487 | 302.0161 | 0.012095 | 0 | 0 | 0.024189 | 302.259 | 0.012621 | 0 | 0 | 0.025243 | 302.5018 | 0.013148 | 0 | 0 | 0.026296 | 302.6637 | 0.013499 | 0 | 0 | 0.026998 | 302.9066 | 0.014026 | 0 | 0 | 0.028052 | 303.1494 | 0.014553 | 0 | 0 | 0.029105 | 303.2303 | 0.014728 | 0 | 0 | 0.029457 | 303.4732 | 0.015255 | 0 | 0 | 0.03051 | 303.716 | 0.015782 | 0 | 0 | 0.031563 | 303.8779 | 0.016133 | 0 | 0 | 0.032266 | 304.1208 | 0.01666 | 0 | 0 | 0.033319 | 304.2827 | 0.017011 | 0 | 0 | 0.034021 | 304.4446 | 0.017362 | 0 | 0 | 0.034724
2017-12-06 09:00 | 272.9233 | 0.81347 |  | 286.5871 | 0 | 0 | 0 | 0 | 294.6405 | 0 | 0 | 0 | 0 | 301.2297 | 0.010389 | 0 | 0 | 0.020778 | 301.4737 | 0.010918 | 0 | 0 | 0.021836 | 301.6364 | 0.011271 | 0 | 0 | 0.022542 | 301.8805 | 0.0118 | 0 | 0 | 0.023601 | 302.1245 | 0.01233 | 0 | 0 | 0.024659 | 302.3685 | 0.012859 | 0 | 0 | 0.025718 | 302.6939 | 0.013565 | 0 | 0 | 0.02713 | 302.938 | 0.014094 | 0 | 0 | 0.028188 | 303.1007 | 0.014447 | 0 | 0 | 0.028894 | 303.3447 | 0.014976 | 0 | 0 | 0.029953 | 303.5074 | 0.015329 | 0 | 0 | 0.030658 | 303.7514 | 0.015859 | 0 | 0 | 0.031717 | 303.9955 | 0.016388 | 0 | 0 | 0.032776 | 304.1582 | 0.016741 | 0 | 0 | 0.033481 | 304.4022 | 0.01727 | 0 | 0 | 0.03454 | 304.6463 | 0.017799 | 0 | 0 | 0.035599 | 304.7276 | 0.017976 | 0 | 0 | 0.035952 | 304.9717 | 0.018505 | 0 | 0 | 0.03701 | 305.2157 | 0.019034 | 0 | 0 | 0.038069 | 305.3784 | 0.019387 | 0 | 0 | 0.038775 | 305.6224 | 0.019917 | 0 | 0 | 0.039833 | 305.7851 | 0.02027 | 0 | 0 | 0.040539 | 305.9478 | 0.020622 | 0 | 0 | 0.041245
2017-12-06 10:00 | 271.3471 | 0.80878 |  | 284.932 | 0 | 0 | 0 | 0 | 292.9389 | 0 | 0 | 0 | 0 | 299.49 | 0.0066154 | 0 | 0 | 0.013231 | 299.7326 | 0.0071417 | 0 | 0 | 0.014283 | 299.8944 | 0.0074925 | 0 | 0 | 0.014985 | 300.137 | 0.0080188 | 0 | 0 | 0.016038 | 300.3796 | 0.008545 | 0 | 0 | 0.01709 | 300.6223 | 0.0090713 | 0 | 0 | 0.018143 | 300.9458 | 0.009773 | 0 | 0 | 0.019546 | 301.1884 | 0.010299 | 0 | 0 | 0.020599 | 301.3502 | 0.01065 | 0 | 0 | 0.0213 | 301.5928 | 0.011176 | 0 | 0 | 0.022353 | 301.7545 | 0.011527 | 0 | 0 | 0.023055 | 301.9972 | 0.012054 | 0 | 0 | 0.024107 | 302.2398 | 0.01258 | 0 | 0 | 0.02516 | 302.4016 | 0.012931 | 0 | 0 | 0.025861 | 302.6442 | 0.013457 | 0 | 0 | 0.026914 | 302.8868 | 0.013983 | 0 | 0 | 0.027966 | 302.9677 | 0.014159 | 0 | 0 | 0.028317 | 303.2103 | 0.014685 | 0 | 0 | 0.02937 | 303.453 | 0.015211 | 0 | 0 | 0.030422 | 303.6147 | 0.015562 | 0 | 0 | 0.031124 | 303.8574 | 0.016088 | 0 | 0 | 0.032177 | 304.0191 | 0.016439 | 0 | 0 | 0.032878 | 304.1809 | 0.01679 | 0 | 0 | 0.03358
2017-12-06 11:00 | 259.0373 | 0.77209 |  | 272.0059 | 0 | 0 | 0 | 0 | 279.6495 | 0 | 0 | 0 | 0 | 285.9034 | 0 | 0 | 0 | 0 | 286.1351 | 0 | 0 | 0 | 0 | 286.2895 | 0 | 0 | 0 | 0 | 286.5211 | 0 | 0 | 0 | 0 | 286.7527 | 0 | 0 | 0 | 0 | 286.9844 | 0 | 0 | 0 | 0 | 287.2932 | 0 | 0 | 0 | 0 | 287.5248 | 0 | 0 | 0 | 0 | 287.6792 | 0 | 0 | 0 | 0 | 287.9109 | 0 | 0 | 0 | 0 | 288.0653 | 0 | 0 | 0 | 0 | 288.2969 | 0 | 0 | 0 | 0 | 288.5285 | 0 | 0 | 0 | 0 | 288.6829 | 0 | 0 | 0 | 0 | 288.9146 | 0 | 0 | 0 | 0 | 289.1462 | 0 | 0 | 0 | 0 | 289.2234 | 0 | 0 | 0 | 0 | 289.455 | 0 | 0 | 0 | 0 | 289.6867 | 0 | 0 | 0 | 0 | 289.8411 | 0 | 0 | 0 | 0 | 290.0727 | 0 | 0 | 0 | 0 | 290.2271 | 0 | 0 | 0 | 0 | 290.3815 | 0 | 0 | 0 | 0
2017-12-06 12:00 | 265.1204 | 0.79022 |  | 278.3936 | 0 | 0 | 0 | 0 | 286.2167 | 0 | 0 | 0 | 0 | 292.6175 | 0 | 0 | 0 | 0 | 292.8546 | 0 | 0 | 0 | 0 | 293.0126 | 0 | 0 | 0 | 0 | 293.2497 | 0 | 0 | 0 | 0 | 293.4867 | 0 | 0 | 0 | 0 | 293.7238 | 0 | 0 | 0 | 0 | 294.0399 | 0 | 0 | 0 | 0 | 294.277 | 0 | 0 | 0 | 0 | 294.435 | 0 | 0 | 0 | 0 | 294.6721 | 0 | 0 | 0 | 0 | 294.8301 | 0 | 0 | 0 | 0 | 295.0672 | 0 | 0 | 0 | 0 | 295.3042 | 0 | 0 | 0 | 0 | 295.4623 | 0 | 0 | 0 | 0 | 295.6993 | 0 | 0 | 0 | 0 | 295.9364 | 0 | 0 | 0 | 0 | 296.0154 | 0 | 0 | 0 | 0 | 296.2525 | 0 | 0 | 0 | 0 | 296.4896 | 0.00010751 | 0 | 0 | 0.00021502 | 296.6476 | 0.0004503 | 0 | 0 | 0.00090061 | 296.8847 | 0.0009645 | 0 | 0 | 0.001929 | 297.0427 | 0.0013073 | 0 | 0 | 0.0026146 | 297.2008 | 0.0016501 | 0 | 0 | 0.0033002
2017-12-06 13:00 | 276.8318 | 0.82512 |  | 290.6913 | 0 | 0 | 0 | 0 | 298.86 | 0.005249 | 0 | 0 | 0.010498 | 305.5435 | 0.019746 | 0 | 0 | 0.039491 | 305.791 | 0.020282 | 0 | 0 | 0.040565 | 305.9561 | 0.02064 | 0 | 0 | 0.041281 | 306.2036 | 0.021177 | 0 | 0 | 0.042355 | 306.4511 | 0.021714 | 0 | 0 | 0.043428 | 306.6987 | 0.022251 | 0 | 0 | 0.044502 | 307.0287 | 0.022967 | 0 | 0 | 0.045934 | 307.2763 | 0.023504 | 0 | 0 | 0.047008 | 307.4413 | 0.023862 | 0 | 0 | 0.047724 | 307.6888 | 0.024399 | 0 | 0 | 0.048797 | 307.8539 | 0.024757 | 0 | 0 | 0.049513 | 308.1014 | 0.025294 | 0 | 0 | 0.050587 | 308.3489 | 0.02583 | 0 | 0 | 0.051661 | 308.514 | 0.026188 | 0 | 0 | 0.052377 | 308.7615 | 0.026725 | 0 | 0 | 0.053451 | 309.009 | 0.027262 | 0 | 0 | 0.054524 | 309.0915 | 0.027441 | 0 | 0 | 0.054882 | 309.3391 | 0.027978 | 0 | 0 | 0.055956 | 309.5866 | 0.028515 | 0 | 0 | 0.05703 | 309.7516 | 0.028873 | 0 | 0 | 0.057746 | 309.9992 | 0.02941 | 0 | 0 | 0.05882 | 310.1642 | 0.029768 | 0 | 0 | 0.059536 | 310.3292 | 0.030126 | 0 | 0 | 0.060251
2017-12-06 14:00 | 276.175 | 0.82317 |  | 290.0016 | 0 | 0 | 0 | 0 | 298.1509 | 0.003711 | 0 | 0 | 0.0074221 | 304.8186 | 0.018173 | 0 | 0 | 0.036346 | 305.0655 | 0.018709 | 0 | 0 | 0.037418 | 305.2302 | 0.019066 | 0 | 0 | 0.038132 | 305.4771 | 0.019602 | 0 | 0 | 0.039203 | 305.7241 | 0.020137 | 0 | 0 | 0.040274 | 305.971 | 0.020673 | 0 | 0 | 0.041346 | 306.3003 | 0.021387 | 0 | 0 | 0.042774 | 306.5472 | 0.021923 | 0 | 0 | 0.043845 | 306.7119 | 0.02228 | 0 | 0 | 0.044559 | 306.9588 | 0.022815 | 0 | 0 | 0.045631 | 307.1235 | 0.023172 | 0 | 0 | 0.046345 | 307.3704 | 0.023708 | 0 | 0 | 0.047416 | 307.6174 | 0.024244 | 0 | 0 | 0.048487 | 307.782 | 0.024601 | 0 | 0 | 0.049202 | 308.0289 | 0.025136 | 0 | 0 | 0.050273 | 308.2759 | 0.025672 | 0 | 0 | 0.051344 | 308.3582 | 0.025851 | 0 | 0 | 0.051701 | 308.6052 | 0.026386 | 0 | 0 | 0.052772 | 308.8521 | 0.026922 | 0 | 0 | 0.053844 | 309.0167 | 0.027279 | 0 | 0 | 0.054558 | 309.2637 | 0.027815 | 0 | 0 | 0.055629 | 309.4283 | 0.028172 | 0 | 0 | 0.056343 | 309.593 | 0.028529 | 0 | 0 | 0.057058
2017-12-06 15:00 | 280.754 | 0.83681 |  | 294.8099 | 0 | 0 | 0 | 0 | 303.0943 | 0.014433 | 0 | 0 | 0.028867 | 309.8725 | 0.029135 | 0 | 0 | 0.05827 | 310.1236 | 0.02968 | 0 | 0 | 0.059359 | 310.291 | 0.030043 | 0 | 0 | 0.060085 | 310.542 | 0.030587 | 0 | 0 | 0.061174 | 310.793 | 0.031132 | 0 | 0 | 0.062263 | 311.0441 | 0.031676 | 0 | 0 | 0.063353 | 311.3788 | 0.032402 | 0 | 0 | 0.064805 | 311.6299 | 0.032947 | 0 | 0 | 0.065894 | 311.7972 | 0.03331 | 0 | 0 | 0.06662 | 312.0483 | 0.033854 | 0 | 0 | 0.067709 | 312.2156 | 0.034217 | 0 | 0 | 0.068435 | 312.4667 | 0.034762 | 0 | 0 | 0.069524 | 312.7177 | 0.035306 | 0 | 0 | 0.070613 | 312.8851 | 0.035669 | 0 | 0 | 0.071339 | 313.1361 | 0.036214 | 0 | 0 | 0.072428 | 313.3872 | 0.036758 | 0 | 0 | 0.073517 | 313.4708 | 0.03694 | 0 | 0 | 0.07388 | 313.7219 | 0.037484 | 0 | 0 | 0.074969 | 313.9729 | 0.038029 | 0 | 0 | 0.076058 | 314.1403 | 0.038392 | 0 | 0 | 0.076784 | 314.3913 | 0.038936 | 0 | 0 | 0.077873 | 314.5587 | 0.039299 | 0 | 0 | 0.078599 | 314.7261 | 0.039662 | 0 | 0 | 0.079325
2017-12-06 16:00 | 282.0569 | 0.8407 |  | 296.178 | 0 | 0 | 0 | 0 | 304.5009 | 0.017484 | 0 | 0 | 0.034968 | 311.3105 | 0.032254 | 0 | 0 | 0.064508 | 311.5628 | 0.032801 | 0 | 0 | 0.065603 | 311.7309 | 0.033166 | 0 | 0 | 0.066332 | 311.9831 | 0.033713 | 0 | 0 | 0.067426 | 312.2353 | 0.03426 | 0 | 0 | 0.06852 | 312.4875 | 0.034807 | 0 | 0 | 0.069614 | 312.8238 | 0.035536 | 0 | 0 | 0.071073 | 313.076 | 0.036084 | 0 | 0 | 0.072167 | 313.2442 | 0.036448 | 0 | 0 | 0.072896 | 313.4964 | 0.036995 | 0 | 0 | 0.07399 | 313.6645 | 0.03736 | 0 | 0 | 0.07472 | 313.9167 | 0.037907 | 0 | 0 | 0.075814 | 314.1689 | 0.038454 | 0 | 0 | 0.076908 | 314.3371 | 0.038819 | 0 | 0 | 0.077637 | 314.5893 | 0.039366 | 0 | 0 | 0.078732 | 314.8415 | 0.039913 | 0 | 0 | 0.079826 | 314.9255 | 0.040095 | 0 | 0 | 0.08019 | 315.1778 | 0.040642 | 0 | 0 | 0.081284 | 315.43 | 0.041189 | 0 | 0 | 0.082378 | 315.5981 | 0.041554 | 0 | 0 | 0.083108 | 315.8503 | 0.042101 | 0 | 0 | 0.084202 | 316.0185 | 0.042466 | 0 | 0 | 0.084931 | 316.1866 | 0.04283 | 0 | 0 | 0.085661
2017-12-06 17:00 | 284.1764 | 0.84702 |  | 298.4036 | 0.004259 | 0 | 0 | 0.008518 | 306.789 | 0.022447 | 0 | 0 | 0.044894 | 313.6499 | 0.037328 | 0 | 0 | 0.074656 | 313.904 | 0.037879 | 0 | 0 | 0.075759 | 314.0734 | 0.038247 | 0 | 0 | 0.076494 | 314.3275 | 0.038798 | 0 | 0 | 0.077596 | 314.5816 | 0.039349 | 0 | 0 | 0.078698 | 314.8357 | 0.0399 | 0 | 0 | 0.0798 | 315.1745 | 0.040635 | 0 | 0 | 0.08127 | 315.4286 | 0.041186 | 0 | 0 | 0.082372 | 315.598 | 0.041554 | 0 | 0 | 0.083107 | 315.8521 | 0.042105 | 0 | 0 | 0.08421 | 316.0215 | 0.042472 | 0 | 0 | 0.084945 | 316.2756 | 0.043023 | 0 | 0 | 0.086047 | 316.5297 | 0.043575 | 0 | 0 | 0.087149 | 316.6991 | 0.043942 | 0 | 0 | 0.087884 | 316.9532 | 0.044493 | 0 | 0 | 0.088986 | 317.2073 | 0.045044 | 0 | 0 | 0.090089 | 317.292 | 0.045228 | 0 | 0 | 0.090456 | 317.5461 | 0.045779 | 0 | 0 | 0.091558 | 317.8002 | 0.04633 | 0 | 0 | 0.092661 | 317.9696 | 0.046698 | 0 | 0 | 0.093396 | 318.2237 | 0.047249 | 0 | 0 | 0.094498 | 318.3931 | 0.047616 | 0 | 0 | 0.095233 | 318.5625 | 0.047984 | 0 | 0 | 0.095968
2017-12-06 18:00 | 287.2691 | 0.85623 |  | 301.6511 | 0.011303 | 0 | 0 | 0.022606 | 310.1279 | 0.029689 | 0 | 0 | 0.059378 | 317.0633 | 0.044732 | 0 | 0 | 0.089464 | 317.3202 | 0.045289 | 0 | 0 | 0.090578 | 317.4915 | 0.045661 | 0 | 0 | 0.091321 | 317.7483 | 0.046218 | 0 | 0 | 0.092436 | 318.0052 | 0.046775 | 0 | 0 | 0.09355 | 318.2621 | 0.047332 | 0 | 0 | 0.094664 | 318.6046 | 0.048075 | 0 | 0 | 0.09615 | 318.8614 | 0.048632 | 0 | 0 | 0.097264 | 319.0327 | 0.049004 | 0 | 0 | 0.098007 | 319.2896 | 0.049561 | 0 | 0 | 0.099121 | 319.4608 | 0.049932 | 0 | 0 | 0.099864 | 319.7177 | 0.050489 | 0 | 0 | 0.10098 | 319.9745 | 0.051046 | 0 | 0 | 0.10209 | 320.1458 | 0.051418 | 0 | 0 | 0.10284 | 320.4027 | 0.051975 | 0 | 0 | 0.10395 | 320.6595 | 0.052532 | 0 | 0 | 0.10506 | 320.7451 | 0.052718 | 0 | 0 | 0.10544 | 321.002 | 0.053275 | 0 | 0 | 0.10655 | 321.2589 | 0.053832 | 0 | 0 | 0.10766 | 321.4301 | 0.054204 | 0 | 0 | 0.10841 | 321.687 | 0.054761 | 0 | 0 | 0.10952 | 321.8583 | 0.055132 | 0 | 0 | 0.11026 | 322.0295 | 0.055504 | 0 | 0 | 0.11101
2017-12-06 19:00 | 278.0165 | 0.82866 |  | 291.9354 | 0 | 0 | 0 | 0 | 300.1391 | 0.0080232 | 0 | 0 | 0.016046 | 306.8512 | 0.022582 | 0 | 0 | 0.045164 | 307.0998 | 0.023121 | 0 | 0 | 0.046242 | 307.2655 | 0.02348 | 0 | 0 | 0.046961 | 307.5141 | 0.02402 | 0 | 0 | 0.048039 | 307.7627 | 0.024559 | 0 | 0 | 0.049118 | 308.0113 | 0.025098 | 0 | 0 | 0.050196 | 308.3427 | 0.025817 | 0 | 0 | 0.051634 | 308.5913 | 0.026356 | 0 | 0 | 0.052713 | 308.7571 | 0.026716 | 0 | 0 | 0.053431 | 309.0057 | 0.027255 | 0 | 0 | 0.05451 | 309.1714 | 0.027614 | 0 | 0 | 0.055229 | 309.42 | 0.028154 | 0 | 0 | 0.056307 | 309.6686 | 0.028693 | 0 | 0 | 0.057386 | 309.8343 | 0.029052 | 0 | 0 | 0.058105 | 310.0829 | 0.029591 | 0 | 0 | 0.059183 | 310.3315 | 0.030131 | 0 | 0 | 0.060261 | 310.4144 | 0.03031 | 0 | 0 | 0.060621 | 310.663 | 0.03085 | 0 | 0 | 0.061699 | 310.9116 | 0.031389 | 0 | 0 | 0.062778 | 311.0773 | 0.031748 | 0 | 0 | 0.063497 | 311.3259 | 0.032288 | 0 | 0 | 0.064575 | 311.4916 | 0.032647 | 0 | 0 | 0.065294 | 311.6574 | 0.033006 | 0 | 0 | 0.066013
2017-12-06 20:00 | 284.8756 | 0.8491 |  | 299.1378 | 0.0058515 | 0 | 0 | 0.011703 | 307.5439 | 0.024084 | 0 | 0 | 0.048169 | 314.4216 | 0.039002 | 0 | 0 | 0.078004 | 314.6763 | 0.039555 | 0 | 0 | 0.079109 | 314.8461 | 0.039923 | 0 | 0 | 0.079846 | 315.1009 | 0.040475 | 0 | 0 | 0.080951 | 315.3556 | 0.041028 | 0 | 0 | 0.082056 | 315.6103 | 0.04158 | 0 | 0 | 0.083161 | 315.95 | 0.042317 | 0 | 0 | 0.084634 | 316.2047 | 0.04287 | 0 | 0 | 0.085739 | 316.3745 | 0.043238 | 0 | 0 | 0.086476 | 316.6292 | 0.04379 | 0 | 0 | 0.087581 | 316.7991 | 0.044159 | 0 | 0 | 0.088318 | 317.0538 | 0.044711 | 0 | 0 | 0.089423 | 317.3085 | 0.045264 | 0 | 0 | 0.090528 | 317.4783 | 0.045632 | 0 | 0 | 0.091264 | 317.7331 | 0.046185 | 0 | 0 | 0.092369 | 317.9878 | 0.046737 | 0 | 0 | 0.093474 | 318.0727 | 0.046921 | 0 | 0 | 0.093843 | 318.3274 | 0.047474 | 0 | 0 | 0.094948 | 318.5822 | 0.048026 | 0 | 0 | 0.096053 | 318.752 | 0.048395 | 0 | 0 | 0.096789 | 319.0067 | 0.048947 | 0 | 0 | 0.097894 | 319.1765 | 0.049316 | 0 | 0 | 0.098631 | 319.3464 | 0.049684 | 0 | 0 | 0.099368
2017-12-06 21:00 | 290.1912 | 0.86494 |  | 304.7196 | 0.017958 | 0 | 0 | 0.035917 | 313.2825 | 0.036531 | 0 | 0 | 0.073063 | 320.2885 | 0.051727 | 0 | 0 | 0.10345 | 320.548 | 0.05229 | 0 | 0 | 0.10458 | 320.721 | 0.052666 | 0 | 0 | 0.10533 | 320.9805 | 0.053228 | 0 | 0 | 0.10646 | 321.24 | 0.053791 | 0 | 0 | 0.10758 | 321.4995 | 0.054354 | 0 | 0 | 0.10871 | 321.8454 | 0.055104 | 0 | 0 | 0.11021 | 322.1049 | 0.055667 | 0 | 0 | 0.11133 | 322.2779 | 0.056042 | 0 | 0 | 0.11208 | 322.5374 | 0.056605 | 0 | 0 | 0.11321 | 322.7104 | 0.05698 | 0 | 0 | 0.11396 | 322.9699 | 0.057543 | 0 | 0 | 0.11509 | 323.2293 | 0.058106 | 0 | 0 | 0.11621 | 323.4023 | 0.058481 | 0 | 0 | 0.11696 | 323.6618 | 0.059044 | 0 | 0 | 0.11809 | 323.9213 | 0.059607 | 0 | 0 | 0.11921 | 324.0078 | 0.059795 | 0 | 0 | 0.11959 | 324.2673 | 0.060357 | 0 | 0 | 0.12071 | 324.5268 | 0.06092 | 0 | 0 | 0.12184 | 324.6998 | 0.061295 | 0 | 0 | 0.12259 | 324.9592 | 0.061858 | 0 | 0 | 0.12372 | 325.1322 | 0.062233 | 0 | 0 | 0.12447 | 325.3052 | 0.062609 | 0 | 0 | 0.12522
2017-12-06 22:00 | 289.1548 | 0.86185 |  | 303.6312 | 0.015598 | 0 | 0 | 0.031196 | 312.1636 | 0.034104 | 0 | 0 | 0.068209 | 319.1446 | 0.049246 | 0 | 0 | 0.098493 | 319.4032 | 0.049807 | 0 | 0 | 0.099614 | 319.5755 | 0.050181 | 0 | 0 | 0.10036 | 319.8341 | 0.050742 | 0 | 0 | 0.10148 | 320.0927 | 0.051303 | 0 | 0 | 0.10261 | 320.3512 | 0.051863 | 0 | 0 | 0.10373 | 320.696 | 0.052611 | 0 | 0 | 0.10522 | 320.9545 | 0.053172 | 0 | 0 | 0.10634 | 321.1269 | 0.053546 | 0 | 0 | 0.10709 | 321.3854 | 0.054107 | 0 | 0 | 0.10821 | 321.5578 | 0.054481 | 0 | 0 | 0.10896 | 321.8164 | 0.055041 | 0 | 0 | 0.11008 | 322.0749 | 0.055602 | 0 | 0 | 0.1112 | 322.2473 | 0.055976 | 0 | 0 | 0.11195 | 322.5058 | 0.056537 | 0 | 0 | 0.11307 | 322.7644 | 0.057098 | 0 | 0 | 0.1142 | 322.8506 | 0.057285 | 0 | 0 | 0.11457 | 323.1091 | 0.057845 | 0 | 0 | 0.11569 | 323.3677 | 0.058406 | 0 | 0 | 0.11681 | 323.5401 | 0.05878 | 0 | 0 | 0.11756 | 323.7986 | 0.059341 | 0 | 0 | 0.11868 | 323.971 | 0.059715 | 0 | 0 | 0.11943 | 324.1434 | 0.060089 | 0 | 0 | 0.12018
2017-12-06 23:00 | 282.1932 | 0.8411 |  | 296.3212 | 0 | 0 | 0 | 0 | 304.6481 | 0.017803 | 0 | 0 | 0.035607 | 311.461 | 0.032581 | 0 | 0 | 0.065161 | 311.7134 | 0.033128 | 0 | 0 | 0.066256 | 311.8816 | 0.033493 | 0 | 0 | 0.066986 | 312.1339 | 0.03404 | 0 | 0 | 0.06808 | 312.3863 | 0.034587 | 0 | 0 | 0.069175 | 312.6386 | 0.035135 | 0 | 0 | 0.07027 | 312.975 | 0.035864 | 0 | 0 | 0.071729 | 313.2274 | 0.036412 | 0 | 0 | 0.072824 | 313.3956 | 0.036777 | 0 | 0 | 0.073553 | 313.6479 | 0.037324 | 0 | 0 | 0.074648 | 313.8161 | 0.037689 | 0 | 0 | 0.075378 | 314.0685 | 0.038236 | 0 | 0 | 0.076472 | 314.3208 | 0.038783 | 0 | 0 | 0.077567 | 314.489 | 0.039148 | 0 | 0 | 0.078297 | 314.7414 | 0.039696 | 0 | 0 | 0.079391 | 314.9937 | 0.040243 | 0 | 0 | 0.080486 | 315.0778 | 0.040425 | 0 | 0 | 0.080851 | 315.3301 | 0.040973 | 0 | 0 | 0.081945 | 315.5825 | 0.04152 | 0 | 0 | 0.08304 | 315.7507 | 0.041885 | 0 | 0 | 0.08377 | 316.003 | 0.042432 | 0 | 0 | 0.084864 | 316.1712 | 0.042797 | 0 | 0 | 0.085594 | 316.3395 | 0.043162 | 0 | 0 | 0.086324
2017-12-07 | 276.9907 | 0.8256 |  | 290.8581 | 0 | 0 | 0 | 0 | 299.0315 | 0.0056211 | 0 | 0 | 0.011242 | 305.7189 | 0.020126 | 0 | 0 | 0.040252 | 305.9666 | 0.020663 | 0 | 0 | 0.041326 | 306.1317 | 0.021021 | 0 | 0 | 0.042043 | 306.3794 | 0.021558 | 0 | 0 | 0.043117 | 306.627 | 0.022096 | 0 | 0 | 0.044191 | 306.8747 | 0.022633 | 0 | 0 | 0.045266 | 307.205 | 0.023349 | 0 | 0 | 0.046698 | 307.4526 | 0.023886 | 0 | 0 | 0.047773 | 307.6178 | 0.024245 | 0 | 0 | 0.048489 | 307.8654 | 0.024782 | 0 | 0 | 0.049564 | 308.0306 | 0.02514 | 0 | 0 | 0.05028 | 308.2782 | 0.025677 | 0 | 0 | 0.051354 | 308.5259 | 0.026214 | 0 | 0 | 0.052429 | 308.691 | 0.026572 | 0 | 0 | 0.053145 | 308.9387 | 0.02711 | 0 | 0 | 0.054219 | 309.1864 | 0.027647 | 0 | 0 | 0.055294 | 309.269 | 0.027826 | 0 | 0 | 0.055652 | 309.5166 | 0.028363 | 0 | 0 | 0.056726 | 309.7643 | 0.0289 | 0 | 0 | 0.057801 | 309.9294 | 0.029259 | 0 | 0 | 0.058517 | 310.1771 | 0.029796 | 0 | 0 | 0.059592 | 310.3422 | 0.030154 | 0 | 0 | 0.060308 | 310.5074 | 0.030512 | 0 | 0 | 0.061024
2017-12-07 01:00 | 271.9022 | 0.81043 |  | 285.5149 | 0 | 0 | 0 | 0 | 293.5382 | 0 | 0 | 0 | 0 | 300.1026 | 0.0079443 | 0 | 0 | 0.015889 | 300.3458 | 0.0084716 | 0 | 0 | 0.016943 | 300.5079 | 0.0088232 | 0 | 0 | 0.017646 | 300.751 | 0.0093505 | 0 | 0 | 0.018701 | 300.9941 | 0.0098779 | 0 | 0 | 0.019756 | 301.2372 | 0.010405 | 0 | 0 | 0.02081 | 301.5614 | 0.011108 | 0 | 0 | 0.022217 | 301.8045 | 0.011636 | 0 | 0 | 0.023271 | 301.9666 | 0.011987 | 0 | 0 | 0.023975 | 302.2098 | 0.012515 | 0 | 0 | 0.025029 | 302.3719 | 0.012866 | 0 | 0 | 0.025732 | 302.615 | 0.013394 | 0 | 0 | 0.026787 | 302.8581 | 0.013921 | 0 | 0 | 0.027842 | 303.0202 | 0.014272 | 0 | 0 | 0.028545 | 303.2633 | 0.0148 | 0 | 0 | 0.0296 | 303.5065 | 0.015327 | 0 | 0 | 0.030654 | 303.5875 | 0.015503 | 0 | 0 | 0.031006 | 303.8306 | 0.01603 | 0 | 0 | 0.032061 | 304.0738 | 0.016558 | 0 | 0 | 0.033115 | 304.2358 | 0.016909 | 0 | 0 | 0.033818 | 304.479 | 0.017437 | 0 | 0 | 0.034873 | 304.6411 | 0.017788 | 0 | 0 | 0.035576 | 304.8031 | 0.01814 | 0 | 0 | 0.036279
2017-12-07 02:00 | 274.1106 | 0.81701 |  | 287.8339 | 0 | 0 | 0 | 0 | 295.9224 | 0 | 0 | 0 | 0 | 302.5402 | 0.013231 | 0 | 0 | 0.026463 | 302.7853 | 0.013763 | 0 | 0 | 0.027526 | 302.9487 | 0.014117 | 0 | 0 | 0.028235 | 303.1938 | 0.014649 | 0 | 0 | 0.029298 | 303.4389 | 0.015181 | 0 | 0 | 0.030361 | 303.684 | 0.015712 | 0 | 0 | 0.031424 | 304.0108 | 0.016421 | 0 | 0 | 0.032842 | 304.2559 | 0.016953 | 0 | 0 | 0.033905 | 304.4193 | 0.017307 | 0 | 0 | 0.034614 | 304.6644 | 0.017839 | 0 | 0 | 0.035677 | 304.8278 | 0.018193 | 0 | 0 | 0.036386 | 305.0729 | 0.018725 | 0 | 0 | 0.03745 | 305.318 | 0.019256 | 0 | 0 | 0.038513 | 305.4814 | 0.019611 | 0 | 0 | 0.039222 | 305.7265 | 0.020142 | 0 | 0 | 0.040285 | 305.9716 | 0.020674 | 0 | 0 | 0.041348 | 306.0533 | 0.020851 | 0 | 0 | 0.041703 | 306.2984 | 0.021383 | 0 | 0 | 0.042766 | 306.5435 | 0.021915 | 0 | 0 | 0.043829 | 306.7069 | 0.022269 | 0 | 0 | 0.044538 | 306.952 | 0.022801 | 0 | 0 | 0.045601 | 307.1154 | 0.023155 | 0 | 0 | 0.04631 | 307.2788 | 0.023509 | 0 | 0 | 0.047019
2017-12-07 03:00 | 269.9558 | 0.80463 |  | 283.4711 | 0 | 0 | 0 | 0 | 291.4369 | 0 | 0 | 0 | 0 | 297.9544 | 0.0032848 | 0 | 0 | 0.0065697 | 298.1958 | 0.0038084 | 0 | 0 | 0.0076168 | 298.3568 | 0.0041574 | 0 | 0 | 0.0083149 | 298.5981 | 0.004681 | 0 | 0 | 0.009362 | 298.8395 | 0.0052046 | 0 | 0 | 0.010409 | 299.0809 | 0.0057282 | 0 | 0 | 0.011456 | 299.4028 | 0.0064263 | 0 | 0 | 0.012853 | 299.6442 | 0.0069498 | 0 | 0 | 0.0139 | 299.8051 | 0.0072989 | 0 | 0 | 0.014598 | 300.0465 | 0.0078225 | 0 | 0 | 0.015645 | 300.2074 | 0.0081715 | 0 | 0 | 0.016343 | 300.4488 | 0.0086951 | 0 | 0 | 0.01739 | 300.6902 | 0.0092187 | 0 | 0 | 0.018437 | 300.8511 | 0.0095677 | 0 | 0 | 0.019135 | 301.0925 | 0.010091 | 0 | 0 | 0.020183 | 301.3339 | 0.010615 | 0 | 0 | 0.02123 | 301.4144 | 0.010789 | 0 | 0 | 0.021579 | 301.6557 | 0.011313 | 0 | 0 | 0.022626 | 301.8971 | 0.011837 | 0 | 0 | 0.023673 | 302.0581 | 0.012186 | 0 | 0 | 0.024371 | 302.2994 | 0.012709 | 0 | 0 | 0.025418 | 302.4604 | 0.013058 | 0 | 0 | 0.026116 | 302.6213 | 0.013407 | 0 | 0 | 0.026814
2017-12-07 04:00 | 279.3835 | 0.83273 |  | 293.3707 | 0 | 0 | 0 | 0 | 301.6148 | 0.011224 | 0 | 0 | 0.022448 | 308.3599 | 0.025854 | 0 | 0 | 0.051708 | 308.6097 | 0.026396 | 0 | 0 | 0.052792 | 308.7762 | 0.026757 | 0 | 0 | 0.053515 | 309.0261 | 0.027299 | 0 | 0 | 0.054598 | 309.2759 | 0.027841 | 0 | 0 | 0.055682 | 309.5257 | 0.028383 | 0 | 0 | 0.056766 | 309.8588 | 0.029105 | 0 | 0 | 0.058211 | 310.1086 | 0.029647 | 0 | 0 | 0.059294 | 310.2751 | 0.030008 | 0 | 0 | 0.060017 | 310.525 | 0.03055 | 0 | 0 | 0.061101 | 310.6915 | 0.030912 | 0 | 0 | 0.061823 | 310.9413 | 0.031453 | 0 | 0 | 0.062907 | 311.1912 | 0.031995 | 0 | 0 | 0.06399 | 311.3577 | 0.032356 | 0 | 0 | 0.064713 | 311.6075 | 0.032898 | 0 | 0 | 0.065797 | 311.8573 | 0.03344 | 0 | 0 | 0.06688 | 311.9406 | 0.033621 | 0 | 0 | 0.067242 | 312.1904 | 0.034163 | 0 | 0 | 0.068325 | 312.4402 | 0.034705 | 0 | 0 | 0.069409 | 312.6068 | 0.035066 | 0 | 0 | 0.070132 | 312.8566 | 0.035608 | 0 | 0 | 0.071215 | 313.0232 | 0.035969 | 0 | 0 | 0.071938 | 313.1897 | 0.03633 | 0 | 0 | 0.07266
2017-12-07 05:00 | 285.1447 | 0.8499 |  | 299.4203 | 0.0064644 | 0 | 0 | 0.012929 | 307.8344 | 0.024714 | 0 | 0 | 0.049429 | 314.7186 | 0.039646 | 0 | 0 | 0.079292 | 314.9735 | 0.040199 | 0 | 0 | 0.080399 | 315.1435 | 0.040568 | 0 | 0 | 0.081136 | 315.3985 | 0.041121 | 0 | 0 | 0.082242 | 315.6535 | 0.041674 | 0 | 0 | 0.083348 | 315.9084 | 0.042227 | 0 | 0 | 0.084454 | 316.2484 | 0.042964 | 0 | 0 | 0.085929 | 316.5034 | 0.043517 | 0 | 0 | 0.087035 | 316.6733 | 0.043886 | 0 | 0 | 0.087772 | 316.9283 | 0.044439 | 0 | 0 | 0.088878 | 317.0983 | 0.044808 | 0 | 0 | 0.089616 | 317.3533 | 0.045361 | 0 | 0 | 0.090722 | 317.6082 | 0.045914 | 0 | 0 | 0.091828 | 317.7782 | 0.046283 | 0 | 0 | 0.092565 | 318.0332 | 0.046836 | 0 | 0 | 0.093671 | 318.2882 | 0.047389 | 0 | 0 | 0.094777 | 318.3731 | 0.047573 | 0 | 0 | 0.095146 | 318.6281 | 0.048126 | 0 | 0 | 0.096252 | 318.8831 | 0.048679 | 0 | 0 | 0.097358 | 319.0531 | 0.049048 | 0 | 0 | 0.098095 | 319.308 | 0.049601 | 0 | 0 | 0.099202 | 319.478 | 0.049969 | 0 | 0 | 0.099939 | 319.648 | 0.050338 | 0 | 0 | 0.10068
2017-12-07 06:00 | 282.1662 | 0.84102 |  | 296.2927 | 0 | 0 | 0 | 0 | 304.6189 | 0.01774 | 0 | 0 | 0.03548 | 311.4312 | 0.032516 | 0 | 0 | 0.065032 | 311.6835 | 0.033063 | 0 | 0 | 0.066126 | 311.8517 | 0.033428 | 0 | 0 | 0.066856 | 312.104 | 0.033975 | 0 | 0 | 0.06795 | 312.3563 | 0.034522 | 0 | 0 | 0.069045 | 312.6086 | 0.03507 | 0 | 0 | 0.070139 | 312.945 | 0.035799 | 0 | 0 | 0.071599 | 313.1973 | 0.036347 | 0 | 0 | 0.072693 | 313.3655 | 0.036711 | 0 | 0 | 0.073423 | 313.6178 | 0.037259 | 0 | 0 | 0.074517 | 313.786 | 0.037624 | 0 | 0 | 0.075247 | 314.0383 | 0.038171 | 0 | 0 | 0.076342 | 314.2907 | 0.038718 | 0 | 0 | 0.077436 | 314.4589 | 0.039083 | 0 | 0 | 0.078166 | 314.7112 | 0.03963 | 0 | 0 | 0.07926 | 314.9635 | 0.040177 | 0 | 0 | 0.080355 | 315.0476 | 0.04036 | 0 | 0 | 0.08072 | 315.2999 | 0.040907 | 0 | 0 | 0.081814 | 315.5522 | 0.041454 | 0 | 0 | 0.082909 | 315.7204 | 0.041819 | 0 | 0 | 0.083638 | 315.9727 | 0.042366 | 0 | 0 | 0.084733 | 316.1409 | 0.042731 | 0 | 0 | 0.085463 | 316.3091 | 0.043096 | 0 | 0 | 0.086192
2017-12-07 07:00 | 275.355 | 0.82072 |  | 289.1406 | 0 | 0 | 0 | 0 | 297.2657 | 0.001791 | 0 | 0 | 0.003582 | 303.9136 | 0.01621 | 0 | 0 | 0.03242 | 304.1598 | 0.016744 | 0 | 0 | 0.033488 | 304.3239 | 0.0171 | 0 | 0 | 0.034201 | 304.5702 | 0.017634 | 0 | 0 | 0.035269 | 304.8164 | 0.018168 | 0 | 0 | 0.036337 | 305.0626 | 0.018702 | 0 | 0 | 0.037405 | 305.3909 | 0.019414 | 0 | 0 | 0.038829 | 305.6371 | 0.019948 | 0 | 0 | 0.039897 | 305.8012 | 0.020305 | 0 | 0 | 0.040609 | 306.0475 | 0.020839 | 0 | 0 | 0.041677 | 306.2116 | 0.021195 | 0 | 0 | 0.042389 | 306.4578 | 0.021729 | 0 | 0 | 0.043457 | 306.704 | 0.022263 | 0 | 0 | 0.044525 | 306.8682 | 0.022619 | 0 | 0 | 0.045237 | 307.1144 | 0.023153 | 0 | 0 | 0.046306 | 307.3606 | 0.023687 | 0 | 0 | 0.047374 | 307.4427 | 0.023865 | 0 | 0 | 0.04773 | 307.6889 | 0.024399 | 0 | 0 | 0.048798 | 307.9351 | 0.024933 | 0 | 0 | 0.049866 | 308.0993 | 0.025289 | 0 | 0 | 0.050578 | 308.3455 | 0.025823 | 0 | 0 | 0.051646 | 308.5096 | 0.026179 | 0 | 0 | 0.052358 | 308.6738 | 0.026535 | 0 | 0 | 0.05307
2017-12-07 08:00 | 269.9564 | 0.80463 |  | 283.4717 | 0 | 0 | 0 | 0 | 291.4376 | 0 | 0 | 0 | 0 | 297.9551 | 0.0032862 | 0 | 0 | 0.0065724 | 298.1965 | 0.0038098 | 0 | 0 | 0.0076195 | 298.3574 | 0.0041588 | 0 | 0 | 0.0083176 | 298.5988 | 0.0046824 | 0 | 0 | 0.0093648 | 298.8402 | 0.005206 | 0 | 0 | 0.010412 | 299.0816 | 0.0057295 | 0 | 0 | 0.011459 | 299.4034 | 0.0064276 | 0 | 0 | 0.012855 | 299.6448 | 0.0069512 | 0 | 0 | 0.013902 | 299.8057 | 0.0073002 | 0 | 0 | 0.0146 | 300.0471 | 0.0078238 | 0 | 0 | 0.015648 | 300.208 | 0.0081729 | 0 | 0 | 0.016346 | 300.4494 | 0.0086964 | 0 | 0 | 0.017393 | 300.6908 | 0.00922 | 0 | 0 | 0.01844 | 300.8517 | 0.0095691 | 0 | 0 | 0.019138 | 301.0931 | 0.010093 | 0 | 0 | 0.020185 | 301.3345 | 0.010616 | 0 | 0 | 0.021232 | 301.415 | 0.010791 | 0 | 0 | 0.021581 | 301.6564 | 0.011314 | 0 | 0 | 0.022629 | 301.8978 | 0.011838 | 0 | 0 | 0.023676 | 302.0587 | 0.012187 | 0 | 0 | 0.024374 | 302.3001 | 0.012711 | 0 | 0 | 0.025421 | 302.461 | 0.01306 | 0 | 0 | 0.026119 | 302.6219 | 0.013409 | 0 | 0 | 0.026817
2017-12-07 09:00 | 266.476 | 0.79426 |  | 279.817 | 0 | 0 | 0 | 0 | 287.6802 | 0 | 0 | 0 | 0 | 294.1136 | 0 | 0 | 0 | 0 | 294.3519 | 0 | 0 | 0 | 0 | 294.5108 | 0 | 0 | 0 | 0 | 294.7491 | 0 | 0 | 0 | 0 | 294.9873 | 0 | 0 | 0 | 0 | 295.2256 | 0 | 0 | 0 | 0 | 295.5433 | 0 | 0 | 0 | 0 | 295.7816 | 0 | 0 | 0 | 0 | 295.9404 | 0 | 0 | 0 | 0 | 296.1787 | 0 | 0 | 0 | 0 | 296.3376 | 0 | 0 | 0 | 0 | 296.5758 | 0.00029465 | 0 | 0 | 0.00058931 | 296.8141 | 0.00081148 | 0 | 0 | 0.001623 | 296.973 | 0.001156 | 0 | 0 | 0.0023121 | 297.2113 | 0.0016729 | 0 | 0 | 0.0033457 | 297.4495 | 0.0021897 | 0 | 0 | 0.0043793 | 297.529 | 0.0023619 | 0 | 0 | 0.0047239 | 297.7672 | 0.0028788 | 0 | 0 | 0.0057575 | 298.0055 | 0.0033956 | 0 | 0 | 0.0067912 | 298.1644 | 0.0037401 | 0 | 0 | 0.0074803 | 298.4026 | 0.004257 | 0 | 0 | 0.0085139 | 298.5615 | 0.0046015 | 0 | 0 | 0.009203 | 298.7203 | 0.0049461 | 0 | 0 | 0.0098921
2017-12-07 10:00 | 273.4736 | 0.81511 |  | 287.165 | 0 | 0 | 0 | 0 | 295.2346 | 0 | 0 | 0 | 0 | 301.837 | 0.011706 | 0 | 0 | 0.023412 | 302.0816 | 0.012237 | 0 | 0 | 0.024473 | 302.2446 | 0.01259 | 0 | 0 | 0.02518 | 302.4891 | 0.013121 | 0 | 0 | 0.026241 | 302.7337 | 0.013651 | 0 | 0 | 0.027302 | 302.9782 | 0.014181 | 0 | 0 | 0.028363 | 303.3042 | 0.014889 | 0 | 0 | 0.029777 | 303.5488 | 0.015419 | 0 | 0 | 0.030838 | 303.7118 | 0.015773 | 0 | 0 | 0.031545 | 303.9563 | 0.016303 | 0 | 0 | 0.032606 | 304.1194 | 0.016657 | 0 | 0 | 0.033313 | 304.3639 | 0.017187 | 0 | 0 | 0.034374 | 304.6084 | 0.017717 | 0 | 0 | 0.035435 | 304.7714 | 0.018071 | 0 | 0 | 0.036142 | 305.016 | 0.018601 | 0 | 0 | 0.037203 | 305.2605 | 0.019132 | 0 | 0 | 0.038263 | 305.342 | 0.019308 | 0 | 0 | 0.038617 | 305.5866 | 0.019839 | 0 | 0 | 0.039678 | 305.8311 | 0.020369 | 0 | 0 | 0.040739 | 305.9941 | 0.020723 | 0 | 0 | 0.041446 | 306.2387 | 0.021253 | 0 | 0 | 0.042507 | 306.4017 | 0.021607 | 0 | 0 | 0.043214 | 306.5647 | 0.02196 | 0 | 0 | 0.043921
2017-12-07 11:00 | 271.8306 | 0.81022 |  | 285.4397 | 0 | 0 | 0 | 0 | 293.4609 | 0 | 0 | 0 | 0 | 300.0237 | 0.007773 | 0 | 0 | 0.015546 | 300.2667 | 0.0083002 | 0 | 0 | 0.0166 | 300.4288 | 0.0086516 | 0 | 0 | 0.017303 | 300.6718 | 0.0091789 | 0 | 0 | 0.018358 | 300.9149 | 0.0097061 | 0 | 0 | 0.019412 | 301.158 | 0.010233 | 0 | 0 | 0.020467 | 301.4821 | 0.010936 | 0 | 0 | 0.021872 | 301.7251 | 0.011463 | 0 | 0 | 0.022927 | 301.8872 | 0.011815 | 0 | 0 | 0.02363 | 302.1302 | 0.012342 | 0 | 0 | 0.024684 | 302.2923 | 0.012694 | 0 | 0 | 0.025387 | 302.5353 | 0.013221 | 0 | 0 | 0.026442 | 302.7784 | 0.013748 | 0 | 0 | 0.027496 | 302.9404 | 0.014099 | 0 | 0 | 0.028199 | 303.1835 | 0.014627 | 0 | 0 | 0.029253 | 303.4266 | 0.015154 | 0 | 0 | 0.030308 | 303.5076 | 0.01533 | 0 | 0 | 0.030659 | 303.7507 | 0.015857 | 0 | 0 | 0.031714 | 303.9937 | 0.016384 | 0 | 0 | 0.032768 | 304.1558 | 0.016736 | 0 | 0 | 0.033471 | 304.3988 | 0.017263 | 0 | 0 | 0.034525 | 304.5609 | 0.017614 | 0 | 0 | 0.035228 | 304.7229 | 0.017966 | 0 | 0 | 0.035931
2017-12-07 12:00 | 280.3491 | 0.83561 |  | 294.3847 | 0 | 0 | 0 | 0 | 302.6572 | 0.013485 | 0 | 0 | 0.02697 | 309.4256 | 0.028166 | 0 | 0 | 0.056331 | 309.6763 | 0.028709 | 0 | 0 | 0.057419 | 309.8434 | 0.029072 | 0 | 0 | 0.058144 | 310.0941 | 0.029616 | 0 | 0 | 0.059231 | 310.3448 | 0.030159 | 0 | 0 | 0.060319 | 310.5954 | 0.030703 | 0 | 0 | 0.061406 | 310.9297 | 0.031428 | 0 | 0 | 0.062856 | 311.1804 | 0.031972 | 0 | 0 | 0.063944 | 311.3475 | 0.032334 | 0 | 0 | 0.064669 | 311.5982 | 0.032878 | 0 | 0 | 0.065756 | 311.7653 | 0.033241 | 0 | 0 | 0.066481 | 312.016 | 0.033784 | 0 | 0 | 0.067569 | 312.2667 | 0.034328 | 0 | 0 | 0.068656 | 312.4338 | 0.034691 | 0 | 0 | 0.069381 | 312.6845 | 0.035234 | 0 | 0 | 0.070468 | 312.9351 | 0.035778 | 0 | 0 | 0.071556 | 313.0187 | 0.035959 | 0 | 0 | 0.071918 | 313.2694 | 0.036503 | 0 | 0 | 0.073006 | 313.5201 | 0.037047 | 0 | 0 | 0.074093 | 313.6872 | 0.037409 | 0 | 0 | 0.074818 | 313.9379 | 0.037953 | 0 | 0 | 0.075906 | 314.105 | 0.038315 | 0 | 0 | 0.076631 | 314.2721 | 0.038678 | 0 | 0 | 0.077356
2017-12-07 13:00 | 273.8412 | 0.81621 |  | 287.551 | 0 | 0 | 0 | 0 | 295.6315 | 0 | 0 | 0 | 0 | 302.2428 | 0.012586 | 0 | 0 | 0.025172 | 302.4876 | 0.013117 | 0 | 0 | 0.026235 | 302.6509 | 0.013471 | 0 | 0 | 0.026943 | 302.8957 | 0.014003 | 0 | 0 | 0.028005 | 303.1406 | 0.014534 | 0 | 0 | 0.029067 | 303.3855 | 0.015065 | 0 | 0 | 0.030129 | 303.712 | 0.015773 | 0 | 0 | 0.031546 | 303.9568 | 0.016304 | 0 | 0 | 0.032608 | 304.1201 | 0.016658 | 0 | 0 | 0.033316 | 304.3649 | 0.017189 | 0 | 0 | 0.034378 | 304.5282 | 0.017543 | 0 | 0 | 0.035086 | 304.773 | 0.018074 | 0 | 0 | 0.036149 | 305.0179 | 0.018605 | 0 | 0 | 0.037211 | 305.1811 | 0.01896 | 0 | 0 | 0.037919 | 305.426 | 0.019491 | 0 | 0 | 0.038981 | 305.6709 | 0.020022 | 0 | 0 | 0.040043 | 305.7525 | 0.020199 | 0 | 0 | 0.040398 | 305.9973 | 0.02073 | 0 | 0 | 0.04146 | 306.2422 | 0.021261 | 0 | 0 | 0.042522 | 306.4054 | 0.021615 | 0 | 0 | 0.04323 | 306.6503 | 0.022146 | 0 | 0 | 0.044292 | 306.8136 | 0.0225 | 0 | 0 | 0.045 | 306.9768 | 0.022854 | 0 | 0 | 0.045709
2017-12-07 14:00 | 270.1567 | 0.80523 |  | 283.6821 | 0 | 0 | 0 | 0 | 291.6538 | 0 | 0 | 0 | 0 | 298.1762 | 0.0037658 | 0 | 0 | 0.0075315 | 298.4177 | 0.0042897 | 0 | 0 | 0.0085794 | 298.5788 | 0.004639 | 0 | 0 | 0.0092781 | 298.8204 | 0.005163 | 0 | 0 | 0.010326 | 299.0619 | 0.005687 | 0 | 0 | 0.011374 | 299.3035 | 0.0062109 | 0 | 0 | 0.012422 | 299.6256 | 0.0069095 | 0 | 0 | 0.013819 | 299.8672 | 0.0074335 | 0 | 0 | 0.014867 | 300.0282 | 0.0077828 | 0 | 0 | 0.015566 | 300.2698 | 0.0083068 | 0 | 0 | 0.016614 | 300.4308 | 0.0086561 | 0 | 0 | 0.017312 | 300.6724 | 0.00918 | 0 | 0 | 0.01836 | 300.914 | 0.009704 | 0 | 0 | 0.019408 | 301.075 | 0.010053 | 0 | 0 | 0.020107 | 301.3166 | 0.010577 | 0 | 0 | 0.021155 | 301.5581 | 0.011101 | 0 | 0 | 0.022202 | 301.6387 | 0.011276 | 0 | 0 | 0.022552 | 301.8802 | 0.0118 | 0 | 0 | 0.0236 | 302.1218 | 0.012324 | 0 | 0 | 0.024648 | 302.2828 | 0.012673 | 0 | 0 | 0.025346 | 302.5244 | 0.013197 | 0 | 0 | 0.026394 | 302.6855 | 0.013546 | 0 | 0 | 0.027093 | 302.8465 | 0.013896 | 0 | 0 | 0.027791
2017-12-07 15:00 | 273.2531 | 0.81446 |  | 286.9334 | 0 | 0 | 0 | 0 | 294.9966 | 0 | 0 | 0 | 0 | 301.5937 | 0.011178 | 0 | 0 | 0.022357 | 301.838 | 0.011708 | 0 | 0 | 0.023417 | 302.0009 | 0.012062 | 0 | 0 | 0.024123 | 302.2452 | 0.012592 | 0 | 0 | 0.025183 | 302.4896 | 0.013122 | 0 | 0 | 0.026243 | 302.7339 | 0.013652 | 0 | 0 | 0.027303 | 303.0597 | 0.014358 | 0 | 0 | 0.028716 | 303.304 | 0.014888 | 0 | 0 | 0.029776 | 303.4669 | 0.015241 | 0 | 0 | 0.030483 | 303.7113 | 0.015771 | 0 | 0 | 0.031543 | 303.8742 | 0.016125 | 0 | 0 | 0.032249 | 304.1185 | 0.016655 | 0 | 0 | 0.033309 | 304.3628 | 0.017185 | 0 | 0 | 0.034369 | 304.5257 | 0.017538 | 0 | 0 | 0.035076 | 304.7701 | 0.018068 | 0 | 0 | 0.036136 | 305.0144 | 0.018598 | 0 | 0 | 0.037196 | 305.0958 | 0.018775 | 0 | 0 | 0.037549 | 305.3402 | 0.019305 | 0 | 0 | 0.038609 | 305.5845 | 0.019834 | 0 | 0 | 0.039669 | 305.7474 | 0.020188 | 0 | 0 | 0.040376 | 305.9918 | 0.020718 | 0 | 0 | 0.041436 | 306.1546 | 0.021071 | 0 | 0 | 0.042142 | 306.3175 | 0.021424 | 0 | 0 | 0.042849
2017-12-07 16:00 | 275.3421 | 0.82068 |  | 289.127 | 0 | 0 | 0 | 0 | 297.2518 | 0.0017607 | 0 | 0 | 0.0035215 | 303.8993 | 0.016179 | 0 | 0 | 0.032358 | 304.1455 | 0.016713 | 0 | 0 | 0.033427 | 304.3097 | 0.017069 | 0 | 0 | 0.034139 | 304.5559 | 0.017603 | 0 | 0 | 0.035207 | 304.8021 | 0.018137 | 0 | 0 | 0.036275 | 305.0483 | 0.018671 | 0 | 0 | 0.037343 | 305.3765 | 0.019383 | 0 | 0 | 0.038767 | 305.6227 | 0.019917 | 0 | 0 | 0.039835 | 305.7869 | 0.020273 | 0 | 0 | 0.040547 | 306.0331 | 0.020807 | 0 | 0 | 0.041615 | 306.1972 | 0.021163 | 0 | 0 | 0.042327 | 306.4434 | 0.021697 | 0 | 0 | 0.043395 | 306.6896 | 0.022231 | 0 | 0 | 0.044463 | 306.8538 | 0.022587 | 0 | 0 | 0.045175 | 307.1 | 0.023121 | 0 | 0 | 0.046243 | 307.3462 | 0.023656 | 0 | 0 | 0.047311 | 307.4283 | 0.023834 | 0 | 0 | 0.047667 | 307.6745 | 0.024368 | 0 | 0 | 0.048735 | 307.9207 | 0.024902 | 0 | 0 | 0.049803 | 308.0848 | 0.025258 | 0 | 0 | 0.050515 | 308.331 | 0.025792 | 0 | 0 | 0.051583 | 308.4951 | 0.026148 | 0 | 0 | 0.052295 | 308.6593 | 0.026504 | 0 | 0 | 0.053007
2017-12-07 17:00 | 270.9676 | 0.80765 |  | 284.5335 | 0 | 0 | 0 | 0 | 292.5292 | 0 | 0 | 0 | 0 | 299.0711 | 0.0057069 | 0 | 0 | 0.011414 | 299.3134 | 0.0062324 | 0 | 0 | 0.012465 | 299.4749 | 0.0065828 | 0 | 0 | 0.013166 | 299.7172 | 0.0071083 | 0 | 0 | 0.014217 | 299.9595 | 0.0076339 | 0 | 0 | 0.015268 | 300.2018 | 0.0081594 | 0 | 0 | 0.016319 | 300.5249 | 0.0088601 | 0 | 0 | 0.01772 | 300.7672 | 0.0093857 | 0 | 0 | 0.018771 | 300.9287 | 0.009736 | 0 | 0 | 0.019472 | 301.171 | 0.010262 | 0 | 0 | 0.020523 | 301.3325 | 0.010612 | 0 | 0 | 0.021224 | 301.5748 | 0.011137 | 0 | 0 | 0.022275 | 301.8171 | 0.011663 | 0 | 0 | 0.023326 | 301.9787 | 0.012013 | 0 | 0 | 0.024027 | 302.2209 | 0.012539 | 0 | 0 | 0.025078 | 302.4632 | 0.013064 | 0 | 0 | 0.026129 | 302.544 | 0.01324 | 0 | 0 | 0.026479 | 302.7863 | 0.013765 | 0 | 0 | 0.02753 | 303.0286 | 0.014291 | 0 | 0 | 0.028581 | 303.1901 | 0.014641 | 0 | 0 | 0.029282 | 303.4324 | 0.015167 | 0 | 0 | 0.030333 | 303.5939 | 0.015517 | 0 | 0 | 0.031034 | 303.7555 | 0.015867 | 0 | 0 | 0.031735
2017-12-07 18:00 | 277.6867 | 0.82767 |  | 291.589 | 0 | 0 | 0 | 0 | 299.783 | 0.0072509 | 0 | 0 | 0.014502 | 306.4871 | 0.021792 | 0 | 0 | 0.043584 | 306.7354 | 0.022331 | 0 | 0 | 0.044662 | 306.901 | 0.02269 | 0 | 0 | 0.04538 | 307.1493 | 0.023228 | 0 | 0 | 0.046457 | 307.3976 | 0.023767 | 0 | 0 | 0.047534 | 307.6459 | 0.024306 | 0 | 0 | 0.048611 | 307.9769 | 0.025024 | 0 | 0 | 0.050047 | 308.2252 | 0.025562 | 0 | 0 | 0.051124 | 308.3908 | 0.025921 | 0 | 0 | 0.051842 | 308.6391 | 0.02646 | 0 | 0 | 0.05292 | 308.8046 | 0.026819 | 0 | 0 | 0.053638 | 309.0529 | 0.027357 | 0 | 0 | 0.054715 | 309.3012 | 0.027896 | 0 | 0 | 0.055792 | 309.4667 | 0.028255 | 0 | 0 | 0.05651 | 309.7151 | 0.028794 | 0 | 0 | 0.057587 | 309.9634 | 0.029332 | 0 | 0 | 0.058664 | 310.0461 | 0.029512 | 0 | 0 | 0.059023 | 310.2944 | 0.03005 | 0 | 0 | 0.0601 | 310.5427 | 0.030589 | 0 | 0 | 0.061178 | 310.7083 | 0.030948 | 0 | 0 | 0.061896 | 310.9566 | 0.031486 | 0 | 0 | 0.062973 | 311.1221 | 0.031845 | 0 | 0 | 0.063691 | 311.2876 | 0.032205 | 0 | 0 | 0.064409
2017-12-07 19:00 | 284.2114 | 0.84712 |  | 298.4404 | 0.0043389 | 0 | 0 | 0.0086778 | 306.8269 | 0.022529 | 0 | 0 | 0.045058 | 313.6886 | 0.037412 | 0 | 0 | 0.074824 | 313.9427 | 0.037963 | 0 | 0 | 0.075927 | 314.1121 | 0.038331 | 0 | 0 | 0.076662 | 314.3663 | 0.038882 | 0 | 0 | 0.077764 | 314.6204 | 0.039433 | 0 | 0 | 0.078867 | 314.8745 | 0.039985 | 0 | 0 | 0.079969 | 315.2134 | 0.040719 | 0 | 0 | 0.081439 | 315.4675 | 0.041271 | 0 | 0 | 0.082541 | 315.6369 | 0.041638 | 0 | 0 | 0.083276 | 315.8911 | 0.042189 | 0 | 0 | 0.084379 | 316.0605 | 0.042557 | 0 | 0 | 0.085114 | 316.3146 | 0.043108 | 0 | 0 | 0.086216 | 316.5688 | 0.043659 | 0 | 0 | 0.087319 | 316.7382 | 0.044027 | 0 | 0 | 0.088054 | 316.9923 | 0.044578 | 0 | 0 | 0.089156 | 317.2465 | 0.045129 | 0 | 0 | 0.090258 | 317.3312 | 0.045313 | 0 | 0 | 0.090626 | 317.5853 | 0.045864 | 0 | 0 | 0.091728 | 317.8395 | 0.046415 | 0 | 0 | 0.092831 | 318.0089 | 0.046783 | 0 | 0 | 0.093566 | 318.263 | 0.047334 | 0 | 0 | 0.094668 | 318.4324 | 0.047702 | 0 | 0 | 0.095403 | 318.6019 | 0.048069 | 0 | 0 | 0.096138
2017-12-07 20:00 | 274.0556 | 0.81685 |  | 287.7761 | 0 | 0 | 0 | 0 | 295.8629 | 0 | 0 | 0 | 0 | 302.4794 | 0.0131 | 0 | 0 | 0.026199 | 302.7245 | 0.013631 | 0 | 0 | 0.027262 | 302.8879 | 0.013985 | 0 | 0 | 0.027971 | 303.1329 | 0.014517 | 0 | 0 | 0.029034 | 303.378 | 0.015048 | 0 | 0 | 0.030097 | 303.623 | 0.01558 | 0 | 0 | 0.03116 | 303.9498 | 0.016289 | 0 | 0 | 0.032577 | 304.1948 | 0.01682 | 0 | 0 | 0.03364 | 304.3582 | 0.017175 | 0 | 0 | 0.034349 | 304.6032 | 0.017706 | 0 | 0 | 0.035412 | 304.7666 | 0.01806 | 0 | 0 | 0.036121 | 305.0117 | 0.018592 | 0 | 0 | 0.037184 | 305.2567 | 0.019123 | 0 | 0 | 0.038247 | 305.4201 | 0.019478 | 0 | 0 | 0.038956 | 305.6651 | 0.020009 | 0 | 0 | 0.040019 | 305.9102 | 0.020541 | 0 | 0 | 0.041082 | 305.9919 | 0.020718 | 0 | 0 | 0.041436 | 306.2369 | 0.02125 | 0 | 0 | 0.042499 | 306.482 | 0.021781 | 0 | 0 | 0.043562 | 306.6454 | 0.022135 | 0 | 0 | 0.044271 | 306.8904 | 0.022667 | 0 | 0 | 0.045334 | 307.0538 | 0.023021 | 0 | 0 | 0.046043 | 307.2172 | 0.023376 | 0 | 0 | 0.046751
2017-12-07 21:00 | 276.4243 | 0.82391 |  | 290.2634 | 0 | 0 | 0 | 0 | 298.4201 | 0.0042948 | 0 | 0 | 0.0085897 | 305.0938 | 0.01877 | 0 | 0 | 0.03754 | 305.3409 | 0.019306 | 0 | 0 | 0.038612 | 305.5057 | 0.019664 | 0 | 0 | 0.039327 | 305.7529 | 0.0202 | 0 | 0 | 0.040399 | 306.0001 | 0.020736 | 0 | 0 | 0.041472 | 306.2472 | 0.021272 | 0 | 0 | 0.042544 | 306.5768 | 0.021987 | 0 | 0 | 0.043973 | 306.824 | 0.022523 | 0 | 0 | 0.045046 | 306.9888 | 0.02288 | 0 | 0 | 0.045761 | 307.2359 | 0.023416 | 0 | 0 | 0.046833 | 307.4007 | 0.023774 | 0 | 0 | 0.047548 | 307.6479 | 0.02431 | 0 | 0 | 0.04862 | 307.8951 | 0.024846 | 0 | 0 | 0.049692 | 308.0598 | 0.025203 | 0 | 0 | 0.050407 | 308.307 | 0.02574 | 0 | 0 | 0.051479 | 308.5542 | 0.026276 | 0 | 0 | 0.052551 | 308.6366 | 0.026454 | 0 | 0 | 0.052909 | 308.8838 | 0.026991 | 0 | 0 | 0.053981 | 309.1309 | 0.027527 | 0 | 0 | 0.055053 | 309.2957 | 0.027884 | 0 | 0 | 0.055768 | 309.5429 | 0.02842 | 0 | 0 | 0.05684 | 309.7077 | 0.028778 | 0 | 0 | 0.057555 | 309.8724 | 0.029135 | 0 | 0 | 0.05827
2017-12-07 22:00 | 280.9185 | 0.83731 |  | 294.9826 | 0 | 0 | 0 | 0 | 303.272 | 0.014819 | 0 | 0 | 0.029637 | 310.0541 | 0.029529 | 0 | 0 | 0.059058 | 310.3053 | 0.030074 | 0 | 0 | 0.060148 | 310.4728 | 0.030437 | 0 | 0 | 0.060874 | 310.724 | 0.030982 | 0 | 0 | 0.061964 | 310.9752 | 0.031527 | 0 | 0 | 0.063054 | 311.2264 | 0.032072 | 0 | 0 | 0.064143 | 311.5613 | 0.032798 | 0 | 0 | 0.065596 | 311.8125 | 0.033343 | 0 | 0 | 0.066686 | 311.9799 | 0.033706 | 0 | 0 | 0.067412 | 312.2311 | 0.034251 | 0 | 0 | 0.068502 | 312.3986 | 0.034614 | 0 | 0 | 0.069228 | 312.6498 | 0.035159 | 0 | 0 | 0.070318 | 312.901 | 0.035704 | 0 | 0 | 0.071408 | 313.0684 | 0.036067 | 0 | 0 | 0.072134 | 313.3196 | 0.036612 | 0 | 0 | 0.073224 | 313.5708 | 0.037157 | 0 | 0 | 0.074313 | 313.6545 | 0.037338 | 0 | 0 | 0.074677 | 313.9057 | 0.037883 | 0 | 0 | 0.075766 | 314.1569 | 0.038428 | 0 | 0 | 0.076856 | 314.3244 | 0.038791 | 0 | 0 | 0.077583 | 314.5756 | 0.039336 | 0 | 0 | 0.078672 | 314.743 | 0.039699 | 0 | 0 | 0.079399 | 314.9105 | 0.040063 | 0 | 0 | 0.080125
2017-12-07 23:00 | 281.4798 | 0.83898 |  | 295.572 | 0 | 0 | 0 | 0 | 303.8779 | 0.016133 | 0 | 0 | 0.032266 | 310.6736 | 0.030873 | 0 | 0 | 0.061745 | 310.9253 | 0.031419 | 0 | 0 | 0.062837 | 311.0931 | 0.031783 | 0 | 0 | 0.063565 | 311.3448 | 0.032329 | 0 | 0 | 0.064657 | 311.5965 | 0.032874 | 0 | 0 | 0.065749 | 311.8482 | 0.03342 | 0 | 0 | 0.066841 | 312.1838 | 0.034148 | 0 | 0 | 0.068297 | 312.4355 | 0.034694 | 0 | 0 | 0.069388 | 312.6033 | 0.035058 | 0 | 0 | 0.070116 | 312.855 | 0.035604 | 0 | 0 | 0.071208 | 313.0228 | 0.035968 | 0 | 0 | 0.071936 | 313.2745 | 0.036514 | 0 | 0 | 0.073028 | 313.5261 | 0.03706 | 0 | 0 | 0.07412 | 313.6939 | 0.037424 | 0 | 0 | 0.074848 | 313.9456 | 0.03797 | 0 | 0 | 0.075939 | 314.1973 | 0.038516 | 0 | 0 | 0.077031 | 314.2812 | 0.038698 | 0 | 0 | 0.077395 | 314.5329 | 0.039244 | 0 | 0 | 0.078487 | 314.7846 | 0.039789 | 0 | 0 | 0.079579 | 314.9524 | 0.040153 | 0 | 0 | 0.080307 | 315.2041 | 0.040699 | 0 | 0 | 0.081399 | 315.3719 | 0.041063 | 0 | 0 | 0.082127 | 315.5397 | 0.041427 | 0 | 0 | 0.082854
2017-12-08 | 284.5381 | 0.84809 |  | 298.7834 | 0.0050829 | 0 | 0 | 0.010166 | 307.1796 | 0.023294 | 0 | 0 | 0.046588 | 314.0491 | 0.038194 | 0 | 0 | 0.076388 | 314.3036 | 0.038746 | 0 | 0 | 0.077492 | 314.4732 | 0.039114 | 0 | 0 | 0.078228 | 314.7276 | 0.039666 | 0 | 0 | 0.079332 | 314.982 | 0.040218 | 0 | 0 | 0.080435 | 315.2365 | 0.04077 | 0 | 0 | 0.081539 | 315.5757 | 0.041505 | 0 | 0 | 0.083011 | 315.8301 | 0.042057 | 0 | 0 | 0.084114 | 315.9997 | 0.042425 | 0 | 0 | 0.08485 | 316.2542 | 0.042977 | 0 | 0 | 0.085954 | 316.4238 | 0.043345 | 0 | 0 | 0.08669 | 316.6782 | 0.043897 | 0 | 0 | 0.087793 | 316.9326 | 0.044449 | 0 | 0 | 0.088897 | 317.1023 | 0.044816 | 0 | 0 | 0.089633 | 317.3567 | 0.045368 | 0 | 0 | 0.090737 | 317.6111 | 0.04592 | 0 | 0 | 0.09184 | 317.6959 | 0.046104 | 0 | 0 | 0.092208 | 317.9504 | 0.046656 | 0 | 0 | 0.093312 | 318.2048 | 0.047208 | 0 | 0 | 0.094416 | 318.3744 | 0.047576 | 0 | 0 | 0.095151 | 318.6288 | 0.048128 | 0 | 0 | 0.096255 | 318.7985 | 0.048495 | 0 | 0 | 0.096991 | 318.9681 | 0.048863 | 0 | 0 | 0.097727
2017-12-08 01:00 | 286.174 | 0.85297 |  | 300.5013 | 0.0088089 | 0 | 0 | 0.017618 | 308.9457 | 0.027125 | 0 | 0 | 0.05425 | 315.8547 | 0.042111 | 0 | 0 | 0.084221 | 316.1106 | 0.042666 | 0 | 0 | 0.085331 | 316.2812 | 0.043036 | 0 | 0 | 0.086071 | 316.5371 | 0.043591 | 0 | 0 | 0.087181 | 316.793 | 0.044146 | 0 | 0 | 0.088291 | 317.0489 | 0.044701 | 0 | 0 | 0.089401 | 317.3901 | 0.045441 | 0 | 0 | 0.090881 | 317.646 | 0.045996 | 0 | 0 | 0.091991 | 317.8165 | 0.046366 | 0 | 0 | 0.092731 | 318.0724 | 0.046921 | 0 | 0 | 0.093842 | 318.243 | 0.047291 | 0 | 0 | 0.094582 | 318.4989 | 0.047846 | 0 | 0 | 0.095692 | 318.7548 | 0.048401 | 0 | 0 | 0.096802 | 318.9254 | 0.048771 | 0 | 0 | 0.097542 | 319.1813 | 0.049326 | 0 | 0 | 0.098652 | 319.4372 | 0.049881 | 0 | 0 | 0.099762 | 319.5225 | 0.050066 | 0 | 0 | 0.10013 | 319.7784 | 0.050621 | 0 | 0 | 0.10124 | 320.0343 | 0.051176 | 0 | 0 | 0.10235 | 320.2049 | 0.051546 | 0 | 0 | 0.10309 | 320.4608 | 0.052101 | 0 | 0 | 0.1042 | 320.6313 | 0.052471 | 0 | 0 | 0.10494 | 320.8019 | 0.052841 | 0 | 0 | 0.10568
2017-12-08 02:00 | 283.4384 | 0.84482 |  | 297.6286 | 0.0025782 | 0 | 0 | 0.0051564 | 305.9923 | 0.020719 | 0 | 0 | 0.041438 | 312.8353 | 0.035561 | 0 | 0 | 0.071123 | 313.0888 | 0.036111 | 0 | 0 | 0.072222 | 313.2577 | 0.036478 | 0 | 0 | 0.072955 | 313.5112 | 0.037027 | 0 | 0 | 0.074055 | 313.7646 | 0.037577 | 0 | 0 | 0.075154 | 314.0181 | 0.038127 | 0 | 0 | 0.076254 | 314.356 | 0.03886 | 0 | 0 | 0.07772 | 314.6094 | 0.03941 | 0 | 0 | 0.078819 | 314.7784 | 0.039776 | 0 | 0 | 0.079552 | 315.0319 | 0.040326 | 0 | 0 | 0.080651 | 315.2008 | 0.040692 | 0 | 0 | 0.081384 | 315.4543 | 0.041242 | 0 | 0 | 0.082484 | 315.7077 | 0.041792 | 0 | 0 | 0.083583 | 315.8767 | 0.042158 | 0 | 0 | 0.084316 | 316.1301 | 0.042708 | 0 | 0 | 0.085416 | 316.3836 | 0.043258 | 0 | 0 | 0.086515 | 316.468 | 0.043441 | 0 | 0 | 0.086882 | 316.7215 | 0.043991 | 0 | 0 | 0.087981 | 316.9749 | 0.04454 | 0 | 0 | 0.089081 | 317.1439 | 0.044907 | 0 | 0 | 0.089814 | 317.3973 | 0.045456 | 0 | 0 | 0.090913 | 317.5663 | 0.045823 | 0 | 0 | 0.091646 | 317.7353 | 0.046189 | 0 | 0 | 0.092379
2017-12-08 03:00 | 281.52 | 0.8391 |  | 295.6142 | 0 | 0 | 0 | 0 | 303.9212 | 0.016227 | 0 | 0 | 0.032454 | 310.7179 | 0.030969 | 0 | 0 | 0.061938 | 310.9697 | 0.031515 | 0 | 0 | 0.06303 | 311.1375 | 0.031879 | 0 | 0 | 0.063758 | 311.3892 | 0.032425 | 0 | 0 | 0.06485 | 311.6409 | 0.032971 | 0 | 0 | 0.065942 | 311.8927 | 0.033517 | 0 | 0 | 0.067034 | 312.2283 | 0.034245 | 0 | 0 | 0.06849 | 312.48 | 0.034791 | 0 | 0 | 0.069582 | 312.6479 | 0.035155 | 0 | 0 | 0.07031 | 312.8996 | 0.035701 | 0 | 0 | 0.071402 | 313.0674 | 0.036065 | 0 | 0 | 0.07213 | 313.3191 | 0.036611 | 0 | 0 | 0.073222 | 313.5709 | 0.037157 | 0 | 0 | 0.074314 | 313.7387 | 0.037521 | 0 | 0 | 0.075042 | 313.9904 | 0.038067 | 0 | 0 | 0.076134 | 314.2422 | 0.038613 | 0 | 0 | 0.077226 | 314.3261 | 0.038795 | 0 | 0 | 0.07759 | 314.5778 | 0.039341 | 0 | 0 | 0.078682 | 314.8295 | 0.039887 | 0 | 0 | 0.079774 | 314.9973 | 0.040251 | 0 | 0 | 0.080502 | 315.2491 | 0.040797 | 0 | 0 | 0.081594 | 315.4169 | 0.041161 | 0 | 0 | 0.082322 | 315.5847 | 0.041525 | 0 | 0 | 0.08305
2017-12-08 04:00 | 287.2252 | 0.8561 |  | 301.605 | 0.011203 | 0 | 0 | 0.022406 | 310.0805 | 0.029586 | 0 | 0 | 0.059172 | 317.0149 | 0.044627 | 0 | 0 | 0.089254 | 317.2717 | 0.045184 | 0 | 0 | 0.090368 | 317.4429 | 0.045555 | 0 | 0 | 0.091111 | 317.6998 | 0.046112 | 0 | 0 | 0.092225 | 317.9566 | 0.04667 | 0 | 0 | 0.093339 | 318.2134 | 0.047227 | 0 | 0 | 0.094453 | 318.5559 | 0.047969 | 0 | 0 | 0.095939 | 318.8127 | 0.048526 | 0 | 0 | 0.097053 | 318.9839 | 0.048898 | 0 | 0 | 0.097796 | 319.2408 | 0.049455 | 0 | 0 | 0.09891 | 319.412 | 0.049826 | 0 | 0 | 0.099652 | 319.6688 | 0.050383 | 0 | 0 | 0.10077 | 319.9256 | 0.05094 | 0 | 0 | 0.10188 | 320.0969 | 0.051312 | 0 | 0 | 0.10262 | 320.3537 | 0.051869 | 0 | 0 | 0.10374 | 320.6105 | 0.052426 | 0 | 0 | 0.10485 | 320.6961 | 0.052612 | 0 | 0 | 0.10522 | 320.953 | 0.053169 | 0 | 0 | 0.10634 | 321.2098 | 0.053726 | 0 | 0 | 0.10745 | 321.381 | 0.054097 | 0 | 0 | 0.10819 | 321.6378 | 0.054654 | 0 | 0 | 0.10931 | 321.8091 | 0.055026 | 0 | 0 | 0.11005 | 321.9803 | 0.055397 | 0 | 0 | 0.11079
2017-12-08 05:00 | 276.142 | 0.82307 |  | 289.9669 | 0 | 0 | 0 | 0 | 298.1153 | 0.0036337 | 0 | 0 | 0.0072675 | 304.7822 | 0.018094 | 0 | 0 | 0.036188 | 305.0291 | 0.01863 | 0 | 0 | 0.037259 | 305.1937 | 0.018987 | 0 | 0 | 0.037974 | 305.4406 | 0.019522 | 0 | 0 | 0.039045 | 305.6875 | 0.020058 | 0 | 0 | 0.040116 | 305.9345 | 0.020593 | 0 | 0 | 0.041187 | 306.2637 | 0.021308 | 0 | 0 | 0.042615 | 306.5106 | 0.021843 | 0 | 0 | 0.043686 | 306.6752 | 0.0222 | 0 | 0 | 0.0444 | 306.9221 | 0.022736 | 0 | 0 | 0.045472 | 307.0868 | 0.023093 | 0 | 0 | 0.046186 | 307.3337 | 0.023628 | 0 | 0 | 0.047257 | 307.5806 | 0.024164 | 0 | 0 | 0.048328 | 307.7452 | 0.024521 | 0 | 0 | 0.049042 | 307.9921 | 0.025057 | 0 | 0 | 0.050113 | 308.2391 | 0.025592 | 0 | 0 | 0.051184 | 308.3214 | 0.025771 | 0 | 0 | 0.051541 | 308.5683 | 0.026306 | 0 | 0 | 0.052612 | 308.8152 | 0.026842 | 0 | 0 | 0.053684 | 308.9798 | 0.027199 | 0 | 0 | 0.054398 | 309.2267 | 0.027734 | 0 | 0 | 0.055469 | 309.3913 | 0.028091 | 0 | 0 | 0.056183 | 309.556 | 0.028449 | 0 | 0 | 0.056897
2017-12-08 06:00 | 289.1755 | 0.86192 |  | 303.653 | 0.015645 | 0 | 0 | 0.03129 | 312.186 | 0.034153 | 0 | 0 | 0.068306 | 319.1675 | 0.049296 | 0 | 0 | 0.098592 | 319.426 | 0.049857 | 0 | 0 | 0.099713 | 319.5984 | 0.050231 | 0 | 0 | 0.10046 | 319.857 | 0.050791 | 0 | 0 | 0.10158 | 320.1156 | 0.051352 | 0 | 0 | 0.1027 | 320.3742 | 0.051913 | 0 | 0 | 0.10383 | 320.7189 | 0.052661 | 0 | 0 | 0.10532 | 320.9775 | 0.053222 | 0 | 0 | 0.10644 | 321.1499 | 0.053596 | 0 | 0 | 0.10719 | 321.4085 | 0.054157 | 0 | 0 | 0.10831 | 321.5808 | 0.05453 | 0 | 0 | 0.10906 | 321.8394 | 0.055091 | 0 | 0 | 0.11018 | 322.098 | 0.055652 | 0 | 0 | 0.1113 | 322.2704 | 0.056026 | 0 | 0 | 0.11205 | 322.5289 | 0.056587 | 0 | 0 | 0.11317 | 322.7875 | 0.057148 | 0 | 0 | 0.1143 | 322.8737 | 0.057335 | 0 | 0 | 0.11467 | 323.1323 | 0.057896 | 0 | 0 | 0.11579 | 323.3909 | 0.058456 | 0 | 0 | 0.11691 | 323.5632 | 0.05883 | 0 | 0 | 0.11766 | 323.8218 | 0.059391 | 0 | 0 | 0.11878 | 323.9942 | 0.059765 | 0 | 0 | 0.11953 | 324.1666 | 0.060139 | 0 | 0 | 0.12028
2017-12-08 07:00 | 292.1908 | 0.8709 |  | 306.8193 | 0.022513 | 0 | 0 | 0.045025 | 315.4412 | 0.041214 | 0 | 0 | 0.082427 | 322.4956 | 0.056514 | 0 | 0 | 0.11303 | 322.7568 | 0.057081 | 0 | 0 | 0.11416 | 322.931 | 0.057459 | 0 | 0 | 0.11492 | 323.1923 | 0.058026 | 0 | 0 | 0.11605 | 323.4535 | 0.058592 | 0 | 0 | 0.11718 | 323.7148 | 0.059159 | 0 | 0 | 0.11832 | 324.0632 | 0.059915 | 0 | 0 | 0.11983 | 324.3244 | 0.060481 | 0 | 0 | 0.12096 | 324.4986 | 0.060859 | 0 | 0 | 0.12172 | 324.7599 | 0.061426 | 0 | 0 | 0.12285 | 324.9341 | 0.061804 | 0 | 0 | 0.12361 | 325.1954 | 0.06237 | 0 | 0 | 0.12474 | 325.4566 | 0.062937 | 0 | 0 | 0.12587 | 325.6308 | 0.063315 | 0 | 0 | 0.12663 | 325.8921 | 0.063882 | 0 | 0 | 0.12776 | 326.1533 | 0.064448 | 0 | 0 | 0.1289 | 326.2404 | 0.064637 | 0 | 0 | 0.12927 | 326.5017 | 0.065204 | 0 | 0 | 0.13041 | 326.763 | 0.065771 | 0 | 0 | 0.13154 | 326.9372 | 0.066148 | 0 | 0 | 0.1323 | 327.1984 | 0.066715 | 0 | 0 | 0.13343 | 327.3726 | 0.067093 | 0 | 0 | 0.13419 | 327.5468 | 0.067471 | 0 | 0 | 0.13494
2017-12-08 08:00 | 283.3109 | 0.84444 |  | 297.4948 | 0.0022879 | 0 | 0 | 0.0045757 | 305.8547 | 0.020421 | 0 | 0 | 0.040841 | 312.6947 | 0.035256 | 0 | 0 | 0.070513 | 312.948 | 0.035806 | 0 | 0 | 0.071612 | 313.1169 | 0.036172 | 0 | 0 | 0.072344 | 313.3702 | 0.036722 | 0 | 0 | 0.073443 | 313.6235 | 0.037271 | 0 | 0 | 0.074542 | 313.8769 | 0.037821 | 0 | 0 | 0.075641 | 314.2146 | 0.038553 | 0 | 0 | 0.077106 | 314.468 | 0.039103 | 0 | 0 | 0.078205 | 314.6369 | 0.039469 | 0 | 0 | 0.078938 | 314.8902 | 0.040018 | 0 | 0 | 0.080037 | 315.0591 | 0.040385 | 0 | 0 | 0.08077 | 315.3124 | 0.040934 | 0 | 0 | 0.081868 | 315.5657 | 0.041484 | 0 | 0 | 0.082967 | 315.7346 | 0.04185 | 0 | 0 | 0.0837 | 315.988 | 0.0424 | 0 | 0 | 0.084799 | 316.2413 | 0.042949 | 0 | 0 | 0.085898 | 316.3257 | 0.043132 | 0 | 0 | 0.086264 | 316.5791 | 0.043682 | 0 | 0 | 0.087363 | 316.8324 | 0.044231 | 0 | 0 | 0.088462 | 317.0013 | 0.044597 | 0 | 0 | 0.089195 | 317.2546 | 0.045147 | 0 | 0 | 0.090294 | 317.4235 | 0.045513 | 0 | 0 | 0.091026 | 317.5924 | 0.04588 | 0 | 0 | 0.091759
2017-12-08 09:00 | 284.8398 | 0.84899 |  | 299.1002 | 0.0057701 | 0 | 0 | 0.01154 | 307.5053 | 0.024001 | 0 | 0 | 0.048001 | 314.3821 | 0.038916 | 0 | 0 | 0.077833 | 314.6368 | 0.039469 | 0 | 0 | 0.078938 | 314.8066 | 0.039837 | 0 | 0 | 0.079674 | 315.0613 | 0.04039 | 0 | 0 | 0.080779 | 315.316 | 0.040942 | 0 | 0 | 0.081884 | 315.5707 | 0.041494 | 0 | 0 | 0.082989 | 315.9103 | 0.042231 | 0 | 0 | 0.084462 | 316.165 | 0.042784 | 0 | 0 | 0.085567 | 316.3348 | 0.043152 | 0 | 0 | 0.086304 | 316.5895 | 0.043704 | 0 | 0 | 0.087409 | 316.7593 | 0.044073 | 0 | 0 | 0.088145 | 317.014 | 0.044625 | 0 | 0 | 0.08925 | 317.2687 | 0.045177 | 0 | 0 | 0.090355 | 317.4385 | 0.045546 | 0 | 0 | 0.091091 | 317.6932 | 0.046098 | 0 | 0 | 0.092196 | 317.9479 | 0.046651 | 0 | 0 | 0.093301 | 318.0328 | 0.046835 | 0 | 0 | 0.093669 | 318.2875 | 0.047387 | 0 | 0 | 0.094774 | 318.5422 | 0.04794 | 0 | 0 | 0.095879 | 318.712 | 0.048308 | 0 | 0 | 0.096616 | 318.9667 | 0.04886 | 0 | 0 | 0.097721 | 319.1365 | 0.049229 | 0 | 0 | 0.098457 | 319.3063 | 0.049597 | 0 | 0 | 0.099194
2017-12-08 10:00 | 282.7079 | 0.84264 |  | 296.8616 | 0.00091435 | 0 | 0 | 0.0018287 | 305.2037 | 0.019008 | 0 | 0 | 0.038017 | 312.029 | 0.033813 | 0 | 0 | 0.067625 | 312.2818 | 0.034361 | 0 | 0 | 0.068722 | 312.4504 | 0.034726 | 0 | 0 | 0.069453 | 312.7032 | 0.035275 | 0 | 0 | 0.07055 | 312.956 | 0.035823 | 0 | 0 | 0.071646 | 313.2087 | 0.036371 | 0 | 0 | 0.072743 | 313.5458 | 0.037102 | 0 | 0 | 0.074205 | 313.7986 | 0.037651 | 0 | 0 | 0.075302 | 313.9671 | 0.038016 | 0 | 0 | 0.076033 | 314.2199 | 0.038565 | 0 | 0 | 0.077129 | 314.3884 | 0.03893 | 0 | 0 | 0.07786 | 314.6412 | 0.039478 | 0 | 0 | 0.078957 | 314.894 | 0.040027 | 0 | 0 | 0.080054 | 315.0625 | 0.040392 | 0 | 0 | 0.080785 | 315.3153 | 0.040941 | 0 | 0 | 0.081881 | 315.5681 | 0.041489 | 0 | 0 | 0.082978 | 315.6524 | 0.041672 | 0 | 0 | 0.083343 | 315.9052 | 0.04222 | 0 | 0 | 0.08444 | 316.158 | 0.042768 | 0 | 0 | 0.085537 | 316.3265 | 0.043134 | 0 | 0 | 0.086268 | 316.5793 | 0.043682 | 0 | 0 | 0.087364 | 316.7478 | 0.044048 | 0 | 0 | 0.088095 | 316.9164 | 0.044413 | 0 | 0 | 0.088826
2017-12-08 11:00 | 276.6976 | 0.82472 |  | 290.5504 | 0 | 0 | 0 | 0 | 298.7151 | 0.0049348 | 0 | 0 | 0.0098695 | 305.3954 | 0.019424 | 0 | 0 | 0.038849 | 305.6428 | 0.019961 | 0 | 0 | 0.039922 | 305.8078 | 0.020319 | 0 | 0 | 0.040637 | 306.0552 | 0.020855 | 0 | 0 | 0.041711 | 306.3026 | 0.021392 | 0 | 0 | 0.042784 | 306.55 | 0.021929 | 0 | 0 | 0.043857 | 306.8799 | 0.022644 | 0 | 0 | 0.045288 | 307.1273 | 0.023181 | 0 | 0 | 0.046362 | 307.2923 | 0.023539 | 0 | 0 | 0.047077 | 307.5397 | 0.024075 | 0 | 0 | 0.04815 | 307.7046 | 0.024433 | 0 | 0 | 0.048866 | 307.952 | 0.02497 | 0 | 0 | 0.049939 | 308.1995 | 0.025506 | 0 | 0 | 0.051013 | 308.3644 | 0.025864 | 0 | 0 | 0.051728 | 308.6118 | 0.026401 | 0 | 0 | 0.052801 | 308.8592 | 0.026937 | 0 | 0 | 0.053875 | 308.9417 | 0.027116 | 0 | 0 | 0.054232 | 309.1891 | 0.027653 | 0 | 0 | 0.055306 | 309.4365 | 0.02819 | 0 | 0 | 0.056379 | 309.6015 | 0.028547 | 0 | 0 | 0.057095 | 309.8489 | 0.029084 | 0 | 0 | 0.058168 | 310.0139 | 0.029442 | 0 | 0 | 0.058883 | 310.1788 | 0.029799 | 0 | 0 | 0.059599
2017-12-08 12:00 | 267.6213 | 0.79767 |  | 281.0197 | 0 | 0 | 0 | 0 | 288.9166 | 0 | 0 | 0 | 0 | 295.3778 | 0 | 0 | 0 | 0 | 295.6171 | 0 | 0 | 0 | 0 | 295.7766 | 0 | 0 | 0 | 0 | 296.0159 | 0 | 0 | 0 | 0 | 296.2552 | 0 | 0 | 0 | 0 | 296.4945 | 0.00011821 | 0 | 0 | 0.00023641 | 296.8136 | 0.00081027 | 0 | 0 | 0.0016205 | 297.0529 | 0.0013293 | 0 | 0 | 0.0026586 | 297.2124 | 0.0016753 | 0 | 0 | 0.0033507 | 297.4517 | 0.0021944 | 0 | 0 | 0.0043888 | 297.6112 | 0.0025404 | 0 | 0 | 0.0050808 | 297.8505 | 0.0030595 | 0 | 0 | 0.0061189 | 298.0898 | 0.0035785 | 0 | 0 | 0.007157 | 298.2494 | 0.0039245 | 0 | 0 | 0.0078491 | 298.4887 | 0.0044436 | 0 | 0 | 0.0088872 | 298.728 | 0.0049626 | 0 | 0 | 0.0099252 | 298.8077 | 0.0051356 | 0 | 0 | 0.010271 | 299.047 | 0.0056547 | 0 | 0 | 0.011309 | 299.2863 | 0.0061737 | 0 | 0 | 0.012347 | 299.4459 | 0.0065198 | 0 | 0 | 0.01304 | 299.6852 | 0.0070388 | 0 | 0 | 0.014078 | 299.8447 | 0.0073848 | 0 | 0 | 0.01477 | 300.0043 | 0.0077309 | 0 | 0 | 0.015462
2017-12-08 13:00 | 268.2288 | 0.79948 |  | 281.6576 | 0 | 0 | 0 | 0 | 289.5724 | 0 | 0 | 0 | 0 | 296.0482 | 0 | 0 | 0 | 0 | 296.2881 | 0 | 0 | 0 | 0 | 296.448 | 1.7287e-05 | 0 | 0 | 3.4575e-05 | 296.6878 | 0.00053751 | 0 | 0 | 0.001075 | 296.9277 | 0.0010577 | 0 | 0 | 0.0021155 | 297.1675 | 0.001578 | 0 | 0 | 0.0031559 | 297.4873 | 0.0022716 | 0 | 0 | 0.0045432 | 297.7271 | 0.0027918 | 0 | 0 | 0.0055836 | 297.887 | 0.0031386 | 0 | 0 | 0.0062773 | 298.1269 | 0.0036588 | 0 | 0 | 0.0073177 | 298.2868 | 0.0040057 | 0 | 0 | 0.0080113 | 298.5266 | 0.0045259 | 0 | 0 | 0.0090518 | 298.7665 | 0.0050461 | 0 | 0 | 0.010092 | 298.9264 | 0.0053929 | 0 | 0 | 0.010786 | 299.1662 | 0.0059131 | 0 | 0 | 0.011826 | 299.4061 | 0.0064334 | 0 | 0 | 0.012867 | 299.486 | 0.0066068 | 0 | 0 | 0.013214 | 299.7258 | 0.007127 | 0 | 0 | 0.014254 | 299.9657 | 0.0076472 | 0 | 0 | 0.015294 | 300.1256 | 0.007994 | 0 | 0 | 0.015988 | 300.3654 | 0.0085143 | 0 | 0 | 0.017029 | 300.5253 | 0.0088611 | 0 | 0 | 0.017722 | 300.6852 | 0.0092079 | 0 | 0 | 0.018416
2017-12-08 14:00 | 274.2057 | 0.8173 |  | 287.9338 | 0 | 0 | 0 | 0 | 296.025 | 0 | 0 | 0 | 0 | 302.6451 | 0.013459 | 0 | 0 | 0.026918 | 302.8903 | 0.013991 | 0 | 0 | 0.027981 | 303.0538 | 0.014345 | 0 | 0 | 0.02869 | 303.2989 | 0.014877 | 0 | 0 | 0.029754 | 303.5441 | 0.015409 | 0 | 0 | 0.030818 | 303.7893 | 0.015941 | 0 | 0 | 0.031881 | 304.1162 | 0.01665 | 0 | 0 | 0.0333 | 304.3614 | 0.017182 | 0 | 0 | 0.034363 | 304.5249 | 0.017536 | 0 | 0 | 0.035072 | 304.7701 | 0.018068 | 0 | 0 | 0.036136 | 304.9335 | 0.018422 | 0 | 0 | 0.036845 | 305.1787 | 0.018954 | 0 | 0 | 0.037909 | 305.4239 | 0.019486 | 0 | 0 | 0.038972 | 305.5874 | 0.019841 | 0 | 0 | 0.039681 | 305.8326 | 0.020372 | 0 | 0 | 0.040745 | 306.0778 | 0.020904 | 0 | 0 | 0.041809 | 306.1595 | 0.021082 | 0 | 0 | 0.042163 | 306.4047 | 0.021613 | 0 | 0 | 0.043227 | 306.6499 | 0.022145 | 0 | 0 | 0.04429 | 306.8133 | 0.0225 | 0 | 0 | 0.044999 | 307.0585 | 0.023032 | 0 | 0 | 0.046063 | 307.222 | 0.023386 | 0 | 0 | 0.046772 | 307.3854 | 0.023741 | 0 | 0 | 0.047481
2017-12-08 15:00 | 272.9961 | 0.81369 |  | 286.6636 | 0 | 0 | 0 | 0 | 294.7191 | 0 | 0 | 0 | 0 | 301.31 | 0.010563 | 0 | 0 | 0.021126 | 301.5541 | 0.011093 | 0 | 0 | 0.022185 | 301.7169 | 0.011445 | 0 | 0 | 0.022891 | 301.961 | 0.011975 | 0 | 0 | 0.02395 | 302.2051 | 0.012504 | 0 | 0 | 0.025009 | 302.4492 | 0.013034 | 0 | 0 | 0.026068 | 302.7747 | 0.01374 | 0 | 0 | 0.02748 | 303.0188 | 0.014269 | 0 | 0 | 0.028539 | 303.1815 | 0.014622 | 0 | 0 | 0.029245 | 303.4256 | 0.015152 | 0 | 0 | 0.030304 | 303.5883 | 0.015505 | 0 | 0 | 0.03101 | 303.8325 | 0.016034 | 0 | 0 | 0.032068 | 304.0766 | 0.016564 | 0 | 0 | 0.033127 | 304.2393 | 0.016917 | 0 | 0 | 0.033833 | 304.4834 | 0.017446 | 0 | 0 | 0.034892 | 304.7275 | 0.017976 | 0 | 0 | 0.035951 | 304.8089 | 0.018152 | 0 | 0 | 0.036304 | 305.053 | 0.018682 | 0 | 0 | 0.037363 | 305.2971 | 0.019211 | 0 | 0 | 0.038422 | 305.4598 | 0.019564 | 0 | 0 | 0.039128 | 305.7039 | 0.020093 | 0 | 0 | 0.040187 | 305.8667 | 0.020446 | 0 | 0 | 0.040893 | 306.0294 | 0.020799 | 0 | 0 | 0.041599
2017-12-08 16:00 | 280.9453 | 0.83739 |  | 295.0108 | 0 | 0 | 0 | 0 | 303.3009 | 0.014881 | 0 | 0 | 0.029763 | 310.0837 | 0.029593 | 0 | 0 | 0.059186 | 310.3349 | 0.030138 | 0 | 0 | 0.060276 | 310.5024 | 0.030501 | 0 | 0 | 0.061003 | 310.7536 | 0.031046 | 0 | 0 | 0.062093 | 311.0048 | 0.031591 | 0 | 0 | 0.063182 | 311.2561 | 0.032136 | 0 | 0 | 0.064272 | 311.591 | 0.032863 | 0 | 0 | 0.065725 | 311.8422 | 0.033407 | 0 | 0 | 0.066815 | 312.0097 | 0.033771 | 0 | 0 | 0.067541 | 312.2609 | 0.034316 | 0 | 0 | 0.068631 | 312.4284 | 0.034679 | 0 | 0 | 0.069358 | 312.6796 | 0.035224 | 0 | 0 | 0.070447 | 312.9308 | 0.035769 | 0 | 0 | 0.071537 | 313.0983 | 0.036132 | 0 | 0 | 0.072264 | 313.3495 | 0.036677 | 0 | 0 | 0.073354 | 313.6007 | 0.037222 | 0 | 0 | 0.074443 | 313.6845 | 0.037403 | 0 | 0 | 0.074807 | 313.9357 | 0.037948 | 0 | 0 | 0.075896 | 314.1869 | 0.038493 | 0 | 0 | 0.076986 | 314.3544 | 0.038856 | 0 | 0 | 0.077713 | 314.6056 | 0.039401 | 0 | 0 | 0.078802 | 314.7731 | 0.039764 | 0 | 0 | 0.079529 | 314.9406 | 0.040128 | 0 | 0 | 0.080255
2017-12-08 17:00 | 289.4423 | 0.86271 |  | 303.9332 | 0.016253 | 0 | 0 | 0.032505 | 312.474 | 0.034778 | 0 | 0 | 0.069556 | 319.462 | 0.049935 | 0 | 0 | 0.099869 | 319.7208 | 0.050496 | 0 | 0 | 0.10099 | 319.8933 | 0.05087 | 0 | 0 | 0.10174 | 320.1522 | 0.051432 | 0 | 0 | 0.10286 | 320.411 | 0.051993 | 0 | 0 | 0.10399 | 320.6698 | 0.052554 | 0 | 0 | 0.10511 | 321.0149 | 0.053303 | 0 | 0 | 0.10661 | 321.2737 | 0.053864 | 0 | 0 | 0.10773 | 321.4462 | 0.054239 | 0 | 0 | 0.10848 | 321.705 | 0.0548 | 0 | 0 | 0.1096 | 321.8776 | 0.055174 | 0 | 0 | 0.11035 | 322.1364 | 0.055735 | 0 | 0 | 0.11147 | 322.3952 | 0.056297 | 0 | 0 | 0.11259 | 322.5678 | 0.056671 | 0 | 0 | 0.11334 | 322.8266 | 0.057232 | 0 | 0 | 0.11446 | 323.0854 | 0.057794 | 0 | 0 | 0.11559 | 323.1716 | 0.057981 | 0 | 0 | 0.11596 | 323.4305 | 0.058542 | 0 | 0 | 0.11708 | 323.6893 | 0.059104 | 0 | 0 | 0.11821 | 323.8618 | 0.059478 | 0 | 0 | 0.11896 | 324.1206 | 0.060039 | 0 | 0 | 0.12008 | 324.2932 | 0.060414 | 0 | 0 | 0.12083 | 324.4657 | 0.060788 | 0 | 0 | 0.12158
2017-12-08 18:00 | 285.711 | 0.85159 |  | 300.0151 | 0.0077543 | 0 | 0 | 0.015509 | 308.4458 | 0.026041 | 0 | 0 | 0.052081 | 315.3437 | 0.041002 | 0 | 0 | 0.082004 | 315.5992 | 0.041556 | 0 | 0 | 0.083112 | 315.7695 | 0.041926 | 0 | 0 | 0.083851 | 316.025 | 0.04248 | 0 | 0 | 0.08496 | 316.2804 | 0.043034 | 0 | 0 | 0.086068 | 316.5359 | 0.043588 | 0 | 0 | 0.087176 | 316.8765 | 0.044327 | 0 | 0 | 0.088654 | 317.132 | 0.044881 | 0 | 0 | 0.089762 | 317.3023 | 0.04525 | 0 | 0 | 0.090501 | 317.5578 | 0.045805 | 0 | 0 | 0.091609 | 317.7281 | 0.046174 | 0 | 0 | 0.092348 | 317.9836 | 0.046728 | 0 | 0 | 0.093456 | 318.2391 | 0.047282 | 0 | 0 | 0.094564 | 318.4094 | 0.047652 | 0 | 0 | 0.095303 | 318.6649 | 0.048206 | 0 | 0 | 0.096412 | 318.9204 | 0.04876 | 0 | 0 | 0.09752 | 319.0055 | 0.048945 | 0 | 0 | 0.097889 | 319.261 | 0.049499 | 0 | 0 | 0.098997 | 319.5165 | 0.050053 | 0 | 0 | 0.10011 | 319.6868 | 0.050422 | 0 | 0 | 0.10084 | 319.9423 | 0.050976 | 0 | 0 | 0.10195 | 320.1126 | 0.051346 | 0 | 0 | 0.10269 | 320.2829 | 0.051715 | 0 | 0 | 0.10343
2017-12-08 19:00 | 288.3647 | 0.8595 |  | 302.8016 | 0.013798 | 0 | 0 | 0.027597 | 311.3106 | 0.032254 | 0 | 0 | 0.064509 | 318.2726 | 0.047355 | 0 | 0 | 0.09471 | 318.5304 | 0.047914 | 0 | 0 | 0.095828 | 318.7023 | 0.048287 | 0 | 0 | 0.096574 | 318.9602 | 0.048846 | 0 | 0 | 0.097692 | 319.218 | 0.049406 | 0 | 0 | 0.098811 | 319.4759 | 0.049965 | 0 | 0 | 0.09993 | 319.8197 | 0.05071 | 0 | 0 | 0.10142 | 320.0775 | 0.05127 | 0 | 0 | 0.10254 | 320.2494 | 0.051643 | 0 | 0 | 0.10329 | 320.5073 | 0.052202 | 0 | 0 | 0.1044 | 320.6792 | 0.052575 | 0 | 0 | 0.10515 | 320.937 | 0.053134 | 0 | 0 | 0.10627 | 321.1949 | 0.053693 | 0 | 0 | 0.10739 | 321.3668 | 0.054066 | 0 | 0 | 0.10813 | 321.6246 | 0.054625 | 0 | 0 | 0.10925 | 321.8825 | 0.055185 | 0 | 0 | 0.11037 | 321.9684 | 0.055371 | 0 | 0 | 0.11074 | 322.2263 | 0.05593 | 0 | 0 | 0.11186 | 322.4841 | 0.05649 | 0 | 0 | 0.11298 | 322.656 | 0.056863 | 0 | 0 | 0.11373 | 322.9139 | 0.057422 | 0 | 0 | 0.11484 | 323.0858 | 0.057795 | 0 | 0 | 0.11559 | 323.2577 | 0.058167 | 0 | 0 | 0.11633
2017-12-08 20:00 | 277.3614 | 0.8267 |  | 291.2474 | 0 | 0 | 0 | 0 | 299.4317 | 0.0064891 | 0 | 0 | 0.012978 | 306.128 | 0.021013 | 0 | 0 | 0.042027 | 306.376 | 0.021551 | 0 | 0 | 0.043103 | 306.5414 | 0.02191 | 0 | 0 | 0.04382 | 306.7894 | 0.022448 | 0 | 0 | 0.044896 | 307.0374 | 0.022986 | 0 | 0 | 0.045971 | 307.2854 | 0.023524 | 0 | 0 | 0.047047 | 307.6161 | 0.024241 | 0 | 0 | 0.048482 | 307.8641 | 0.024779 | 0 | 0 | 0.049558 | 308.0294 | 0.025137 | 0 | 0 | 0.050275 | 308.2774 | 0.025675 | 0 | 0 | 0.051351 | 308.4428 | 0.026034 | 0 | 0 | 0.052068 | 308.6908 | 0.026572 | 0 | 0 | 0.053144 | 308.9388 | 0.02711 | 0 | 0 | 0.05422 | 309.1041 | 0.027469 | 0 | 0 | 0.054937 | 309.3522 | 0.028006 | 0 | 0 | 0.056013 | 309.6002 | 0.028544 | 0 | 0 | 0.057089 | 309.6828 | 0.028724 | 0 | 0 | 0.057447 | 309.9309 | 0.029262 | 0 | 0 | 0.058523 | 310.1789 | 0.0298 | 0 | 0 | 0.059599 | 310.3442 | 0.030158 | 0 | 0 | 0.060316 | 310.5922 | 0.030696 | 0 | 0 | 0.061392 | 310.7576 | 0.031055 | 0 | 0 | 0.06211 | 310.9229 | 0.031413 | 0 | 0 | 0.062827
2017-12-08 21:00 | 286.1854 | 0.853 |  | 300.5132 | 0.0088348 | 0 | 0 | 0.01767 | 308.9579 | 0.027151 | 0 | 0 | 0.054303 | 315.8673 | 0.042138 | 0 | 0 | 0.084275 | 316.1232 | 0.042693 | 0 | 0 | 0.085386 | 316.2938 | 0.043063 | 0 | 0 | 0.086126 | 316.5497 | 0.043618 | 0 | 0 | 0.087236 | 316.8056 | 0.044173 | 0 | 0 | 0.088346 | 317.0615 | 0.044728 | 0 | 0 | 0.089456 | 317.4027 | 0.045468 | 0 | 0 | 0.090936 | 317.6586 | 0.046023 | 0 | 0 | 0.092046 | 317.8292 | 0.046393 | 0 | 0 | 0.092786 | 318.0851 | 0.046948 | 0 | 0 | 0.093896 | 318.2557 | 0.047318 | 0 | 0 | 0.094636 | 318.5116 | 0.047873 | 0 | 0 | 0.095747 | 318.7675 | 0.048428 | 0 | 0 | 0.096857 | 318.9381 | 0.048798 | 0 | 0 | 0.097597 | 319.194 | 0.049353 | 0 | 0 | 0.098707 | 319.4499 | 0.049908 | 0 | 0 | 0.099817 | 319.5352 | 0.050093 | 0 | 0 | 0.10019 | 319.7911 | 0.050649 | 0 | 0 | 0.1013 | 320.047 | 0.051204 | 0 | 0 | 0.10241 | 320.2176 | 0.051574 | 0 | 0 | 0.10315 | 320.4735 | 0.052129 | 0 | 0 | 0.10426 | 320.6441 | 0.052499 | 0 | 0 | 0.105 | 320.8147 | 0.052869 | 0 | 0 | 0.10574
2017-12-08 22:00 | 288.4219 | 0.85967 |  | 302.8617 | 0.013929 | 0 | 0 | 0.027857 | 311.3724 | 0.032388 | 0 | 0 | 0.064777 | 318.3357 | 0.047492 | 0 | 0 | 0.094984 | 318.5936 | 0.048051 | 0 | 0 | 0.096102 | 318.7656 | 0.048424 | 0 | 0 | 0.096848 | 319.0235 | 0.048984 | 0 | 0 | 0.097967 | 319.2814 | 0.049543 | 0 | 0 | 0.099086 | 319.5393 | 0.050102 | 0 | 0 | 0.1002 | 319.8831 | 0.050848 | 0 | 0 | 0.1017 | 320.141 | 0.051408 | 0 | 0 | 0.10282 | 320.313 | 0.05178 | 0 | 0 | 0.10356 | 320.5709 | 0.05234 | 0 | 0 | 0.10468 | 320.7428 | 0.052713 | 0 | 0 | 0.10543 | 321.0007 | 0.053272 | 0 | 0 | 0.10654 | 321.2586 | 0.053832 | 0 | 0 | 0.10766 | 321.4305 | 0.054204 | 0 | 0 | 0.10841 | 321.6884 | 0.054764 | 0 | 0 | 0.10953 | 321.9463 | 0.055323 | 0 | 0 | 0.11065 | 322.0323 | 0.05551 | 0 | 0 | 0.11102 | 322.2902 | 0.056069 | 0 | 0 | 0.11214 | 322.5481 | 0.056628 | 0 | 0 | 0.11326 | 322.72 | 0.057001 | 0 | 0 | 0.114 | 322.9779 | 0.057561 | 0 | 0 | 0.11512 | 323.1499 | 0.057934 | 0 | 0 | 0.11587 | 323.3218 | 0.058307 | 0 | 0 | 0.11661
2017-12-08 23:00 | 296.0413 | 0.88238 |  | 310.8625 | 0.031282 | 0 | 0 | 0.062565 | 319.5981 | 0.05023 | 0 | 0 | 0.10046 | 326.7453 | 0.065732 | 0 | 0 | 0.13146 | 327.01 | 0.066306 | 0 | 0 | 0.13261 | 327.1865 | 0.066689 | 0 | 0 | 0.13338 | 327.4512 | 0.067263 | 0 | 0 | 0.13453 | 327.716 | 0.067838 | 0 | 0 | 0.13568 | 327.9807 | 0.068412 | 0 | 0 | 0.13682 | 328.3336 | 0.069177 | 0 | 0 | 0.13835 | 328.5983 | 0.069751 | 0 | 0 | 0.1395 | 328.7748 | 0.070134 | 0 | 0 | 0.14027 | 329.0395 | 0.070708 | 0 | 0 | 0.14142 | 329.216 | 0.071091 | 0 | 0 | 0.14218 | 329.4807 | 0.071665 | 0 | 0 | 0.14333 | 329.7454 | 0.072239 | 0 | 0 | 0.14448 | 329.9219 | 0.072622 | 0 | 0 | 0.14524 | 330.1866 | 0.073196 | 0 | 0 | 0.14639 | 330.4513 | 0.073771 | 0 | 0 | 0.14754 | 330.5396 | 0.073962 | 0 | 0 | 0.14792 | 330.8043 | 0.074536 | 0 | 0 | 0.14907 | 331.069 | 0.07511 | 0 | 0 | 0.15022 | 331.2455 | 0.075493 | 0 | 0 | 0.15099 | 331.5102 | 0.076067 | 0 | 0 | 0.15213 | 331.6867 | 0.07645 | 0 | 0 | 0.1529 | 331.8631 | 0.076833 | 0 | 0 | 0.15367
2017-12-09 | 293.4072 | 0.87453 |  | 308.0966 | 0.025283 | 0 | 0 | 0.050566 | 316.7544 | 0.044062 | 0 | 0 | 0.088124 | 323.8381 | 0.059426 | 0 | 0 | 0.11885 | 324.1005 | 0.059996 | 0 | 0 | 0.11999 | 324.2754 | 0.060375 | 0 | 0 | 0.12075 | 324.5377 | 0.060944 | 0 | 0 | 0.12189 | 324.8001 | 0.061513 | 0 | 0 | 0.12303 | 325.0624 | 0.062082 | 0 | 0 | 0.12416 | 325.4122 | 0.062841 | 0 | 0 | 0.12568 | 325.6746 | 0.06341 | 0 | 0 | 0.12682 | 325.8495 | 0.063789 | 0 | 0 | 0.12758 | 326.1119 | 0.064358 | 0 | 0 | 0.12872 | 326.2868 | 0.064738 | 0 | 0 | 0.12948 | 326.5491 | 0.065307 | 0 | 0 | 0.13061 | 326.8115 | 0.065876 | 0 | 0 | 0.13175 | 326.9864 | 0.066255 | 0 | 0 | 0.13251 | 327.2488 | 0.066824 | 0 | 0 | 0.13365 | 327.5111 | 0.067393 | 0 | 0 | 0.13479 | 327.5986 | 0.067583 | 0 | 0 | 0.13517 | 327.8609 | 0.068152 | 0 | 0 | 0.1363 | 328.1233 | 0.068721 | 0 | 0 | 0.13744 | 328.2982 | 0.0691 | 0 | 0 | 0.1382 | 328.5605 | 0.069669 | 0 | 0 | 0.13934 | 328.7355 | 0.070049 | 0 | 0 | 0.1401 | 328.9104 | 0.070428 | 0 | 0 | 0.14086
2017-12-09 01:00 | 293.5268 | 0.87489 |  | 308.2221 | 0.025555 | 0 | 0 | 0.051111 | 316.8835 | 0.044342 | 0 | 0 | 0.088684 | 323.9701 | 0.059713 | 0 | 0 | 0.11943 | 324.2325 | 0.060282 | 0 | 0 | 0.12056 | 324.4075 | 0.060662 | 0 | 0 | 0.12132 | 324.67 | 0.061231 | 0 | 0 | 0.12246 | 324.9324 | 0.0618 | 0 | 0 | 0.1236 | 325.1949 | 0.062369 | 0 | 0 | 0.12474 | 325.5449 | 0.063128 | 0 | 0 | 0.12626 | 325.8073 | 0.063698 | 0 | 0 | 0.1274 | 325.9823 | 0.064077 | 0 | 0 | 0.12815 | 326.2448 | 0.064647 | 0 | 0 | 0.12929 | 326.4197 | 0.065026 | 0 | 0 | 0.13005 | 326.6822 | 0.065595 | 0 | 0 | 0.13119 | 326.9447 | 0.066165 | 0 | 0 | 0.13233 | 327.1197 | 0.066544 | 0 | 0 | 0.13309 | 327.3821 | 0.067113 | 0 | 0 | 0.13423 | 327.6446 | 0.067683 | 0 | 0 | 0.13537 | 327.7321 | 0.067873 | 0 | 0 | 0.13575 | 327.9945 | 0.068442 | 0 | 0 | 0.13688 | 328.257 | 0.069011 | 0 | 0 | 0.13802 | 328.432 | 0.069391 | 0 | 0 | 0.13878 | 328.6945 | 0.06996 | 0 | 0 | 0.13992 | 328.8694 | 0.070339 | 0 | 0 | 0.14068 | 329.0444 | 0.070719 | 0 | 0 | 0.14144
2017-12-09 02:00 | 301.4514 | 0.89851 |  | 316.5435 | 0.043605 | 0 | 0 | 0.087209 | 325.4387 | 0.062898 | 0 | 0 | 0.1258 | 332.7166 | 0.078684 | 0 | 0 | 0.15737 | 332.9862 | 0.079269 | 0 | 0 | 0.15854 | 333.1659 | 0.079658 | 0 | 0 | 0.15932 | 333.4354 | 0.080243 | 0 | 0 | 0.16049 | 333.705 | 0.080828 | 0 | 0 | 0.16166 | 333.9745 | 0.081412 | 0 | 0 | 0.16282 | 334.3339 | 0.082192 | 0 | 0 | 0.16438 | 334.6035 | 0.082777 | 0 | 0 | 0.16555 | 334.7832 | 0.083166 | 0 | 0 | 0.16633 | 335.0527 | 0.083751 | 0 | 0 | 0.1675 | 335.2324 | 0.084141 | 0 | 0 | 0.16828 | 335.502 | 0.084725 | 0 | 0 | 0.16945 | 335.7715 | 0.08531 | 0 | 0 | 0.17062 | 335.9512 | 0.0857 | 0 | 0 | 0.1714 | 336.2208 | 0.086285 | 0 | 0 | 0.17257 | 336.4903 | 0.086869 | 0 | 0 | 0.17374 | 336.5802 | 0.087064 | 0 | 0 | 0.17413 | 336.8497 | 0.087649 | 0 | 0 | 0.1753 | 337.1193 | 0.088233 | 0 | 0 | 0.17647 | 337.299 | 0.088623 | 0 | 0 | 0.17725 | 337.5685 | 0.089208 | 0 | 0 | 0.17842 | 337.7482 | 0.089598 | 0 | 0 | 0.1792 | 337.9279 | 0.089987 | 0 | 0 | 0.17997
2017-12-09 03:00 | 302.6092 | 0.90196 |  | 317.7592 | 0.046241 | 0 | 0 | 0.092483 | 326.6886 | 0.065609 | 0 | 0 | 0.13122 | 333.9944 | 0.081456 | 0 | 0 | 0.16291 | 334.265 | 0.082042 | 0 | 0 | 0.16408 | 334.4454 | 0.082434 | 0 | 0 | 0.16487 | 334.716 | 0.083021 | 0 | 0 | 0.16604 | 334.9866 | 0.083608 | 0 | 0 | 0.16722 | 335.2572 | 0.084194 | 0 | 0 | 0.16839 | 335.6179 | 0.084977 | 0 | 0 | 0.16995 | 335.8885 | 0.085564 | 0 | 0 | 0.17113 | 336.0689 | 0.085955 | 0 | 0 | 0.17191 | 336.3395 | 0.086542 | 0 | 0 | 0.17308 | 336.5199 | 0.086933 | 0 | 0 | 0.17387 | 336.7905 | 0.08752 | 0 | 0 | 0.17504 | 337.0611 | 0.088107 | 0 | 0 | 0.17621 | 337.2415 | 0.088498 | 0 | 0 | 0.177 | 337.512 | 0.089085 | 0 | 0 | 0.17817 | 337.7826 | 0.089672 | 0 | 0 | 0.17934 | 337.8728 | 0.089868 | 0 | 0 | 0.17974 | 338.1434 | 0.090455 | 0 | 0 | 0.18091 | 338.414 | 0.091042 | 0 | 0 | 0.18208 | 338.5944 | 0.091433 | 0 | 0 | 0.18287 | 338.865 | 0.09202 | 0 | 0 | 0.18404 | 339.0454 | 0.092411 | 0 | 0 | 0.18482 | 339.2258 | 0.092802 | 0 | 0 | 0.1856
2017-12-09 04:00 | 299.609 | 0.89301 |  | 314.6089 | 0.039408 | 0 | 0 | 0.078817 | 323.4497 | 0.058584 | 0 | 0 | 0.11717 | 330.6831 | 0.074273 | 0 | 0 | 0.14855 | 330.951 | 0.074854 | 0 | 0 | 0.14971 | 331.1296 | 0.075242 | 0 | 0 | 0.15048 | 331.3975 | 0.075823 | 0 | 0 | 0.15165 | 331.6654 | 0.076404 | 0 | 0 | 0.15281 | 331.9333 | 0.076985 | 0 | 0 | 0.15397 | 332.2905 | 0.07776 | 0 | 0 | 0.15552 | 332.5584 | 0.078341 | 0 | 0 | 0.15668 | 332.737 | 0.078728 | 0 | 0 | 0.15746 | 333.0049 | 0.079309 | 0 | 0 | 0.15862 | 333.1836 | 0.079697 | 0 | 0 | 0.15939 | 333.4515 | 0.080278 | 0 | 0 | 0.16056 | 333.7194 | 0.080859 | 0 | 0 | 0.16172 | 333.898 | 0.081246 | 0 | 0 | 0.16249 | 334.1659 | 0.081827 | 0 | 0 | 0.16365 | 334.4338 | 0.082408 | 0 | 0 | 0.16482 | 334.5231 | 0.082602 | 0 | 0 | 0.1652 | 334.791 | 0.083183 | 0 | 0 | 0.16637 | 335.0589 | 0.083764 | 0 | 0 | 0.16753 | 335.2375 | 0.084152 | 0 | 0 | 0.1683 | 335.5054 | 0.084733 | 0 | 0 | 0.16947 | 335.684 | 0.08512 | 0 | 0 | 0.17024 | 335.8626 | 0.085508 | 0 | 0 | 0.17102
2017-12-09 05:00 | 300.7131 | 0.8963 |  | 315.7682 | 0.041923 | 0 | 0 | 0.083846 | 324.6417 | 0.061169 | 0 | 0 | 0.12234 | 331.9017 | 0.076917 | 0 | 0 | 0.15383 | 332.1706 | 0.0775 | 0 | 0 | 0.155 | 332.3499 | 0.077889 | 0 | 0 | 0.15578 | 332.6188 | 0.078472 | 0 | 0 | 0.15694 | 332.8877 | 0.079055 | 0 | 0 | 0.15811 | 333.1566 | 0.079638 | 0 | 0 | 0.15928 | 333.5151 | 0.080416 | 0 | 0 | 0.16083 | 333.784 | 0.080999 | 0 | 0 | 0.162 | 333.9632 | 0.081388 | 0 | 0 | 0.16278 | 334.2321 | 0.081971 | 0 | 0 | 0.16394 | 334.4114 | 0.08236 | 0 | 0 | 0.16472 | 334.6803 | 0.082943 | 0 | 0 | 0.16589 | 334.9492 | 0.083526 | 0 | 0 | 0.16705 | 335.1284 | 0.083915 | 0 | 0 | 0.16783 | 335.3973 | 0.084498 | 0 | 0 | 0.169 | 335.6662 | 0.085082 | 0 | 0 | 0.17016 | 335.7558 | 0.085276 | 0 | 0 | 0.17055 | 336.0247 | 0.085859 | 0 | 0 | 0.17172 | 336.2936 | 0.086443 | 0 | 0 | 0.17289 | 336.4729 | 0.086831 | 0 | 0 | 0.17366 | 336.7418 | 0.087415 | 0 | 0 | 0.17483 | 336.921 | 0.087803 | 0 | 0 | 0.17561 | 337.1003 | 0.088192 | 0 | 0 | 0.17638
2017-12-09 06:00 | 298.9269 | 0.89098 |  | 313.8926 | 0.037855 | 0 | 0 | 0.07571 | 322.7133 | 0.056987 | 0 | 0 | 0.11397 | 329.9303 | 0.07264 | 0 | 0 | 0.14528 | 330.1976 | 0.07322 | 0 | 0 | 0.14644 | 330.3758 | 0.073607 | 0 | 0 | 0.14721 | 330.6431 | 0.074186 | 0 | 0 | 0.14837 | 330.9104 | 0.074766 | 0 | 0 | 0.14953 | 331.1777 | 0.075346 | 0 | 0 | 0.15069 | 331.5341 | 0.076119 | 0 | 0 | 0.15224 | 331.8014 | 0.076699 | 0 | 0 | 0.1534 | 331.9796 | 0.077085 | 0 | 0 | 0.15417 | 332.2468 | 0.077665 | 0 | 0 | 0.15533 | 332.425 | 0.078052 | 0 | 0 | 0.1561 | 332.6923 | 0.078631 | 0 | 0 | 0.15726 | 332.9596 | 0.079211 | 0 | 0 | 0.15842 | 333.1378 | 0.079598 | 0 | 0 | 0.1592 | 333.4051 | 0.080177 | 0 | 0 | 0.16035 | 333.6724 | 0.080757 | 0 | 0 | 0.16151 | 333.7615 | 0.08095 | 0 | 0 | 0.1619 | 334.0288 | 0.08153 | 0 | 0 | 0.16306 | 334.2961 | 0.08211 | 0 | 0 | 0.16422 | 334.4743 | 0.082496 | 0 | 0 | 0.16499 | 334.7416 | 0.083076 | 0 | 0 | 0.16615 | 334.9198 | 0.083463 | 0 | 0 | 0.16693 | 335.098 | 0.083849 | 0 | 0 | 0.1677
2017-12-09 07:00 | 299.9979 | 0.89417 |  | 315.0172 | 0.040294 | 0 | 0 | 0.080588 | 323.8695 | 0.059495 | 0 | 0 | 0.11899 | 331.1123 | 0.075204 | 0 | 0 | 0.15041 | 331.3806 | 0.075786 | 0 | 0 | 0.15157 | 331.5594 | 0.076174 | 0 | 0 | 0.15235 | 331.8276 | 0.076756 | 0 | 0 | 0.15351 | 332.0959 | 0.077338 | 0 | 0 | 0.15468 | 332.3641 | 0.077919 | 0 | 0 | 0.15584 | 332.7218 | 0.078695 | 0 | 0 | 0.15739 | 332.9901 | 0.079277 | 0 | 0 | 0.15855 | 333.1689 | 0.079665 | 0 | 0 | 0.15933 | 333.4372 | 0.080247 | 0 | 0 | 0.16049 | 333.616 | 0.080635 | 0 | 0 | 0.16127 | 333.8842 | 0.081217 | 0 | 0 | 0.16243 | 334.1525 | 0.081798 | 0 | 0 | 0.1636 | 334.3313 | 0.082186 | 0 | 0 | 0.16437 | 334.5996 | 0.082768 | 0 | 0 | 0.16554 | 334.8678 | 0.08335 | 0 | 0 | 0.1667 | 334.9573 | 0.083544 | 0 | 0 | 0.16709 | 335.2255 | 0.084126 | 0 | 0 | 0.16825 | 335.4938 | 0.084708 | 0 | 0 | 0.16942 | 335.6726 | 0.085095 | 0 | 0 | 0.17019 | 335.9408 | 0.085677 | 0 | 0 | 0.17135 | 336.1197 | 0.086065 | 0 | 0 | 0.17213 | 336.2985 | 0.086453 | 0 | 0 | 0.17291
2017-12-09 08:00 | 286.914 | 0.85518 |  | 301.2783 | 0.010494 | 0 | 0 | 0.020988 | 309.7445 | 0.028858 | 0 | 0 | 0.057715 | 316.6714 | 0.043882 | 0 | 0 | 0.087764 | 316.928 | 0.044438 | 0 | 0 | 0.088877 | 317.099 | 0.044809 | 0 | 0 | 0.089619 | 317.3556 | 0.045366 | 0 | 0 | 0.090732 | 317.6121 | 0.045922 | 0 | 0 | 0.091845 | 317.8687 | 0.046479 | 0 | 0 | 0.092958 | 318.2108 | 0.047221 | 0 | 0 | 0.094442 | 318.4673 | 0.047777 | 0 | 0 | 0.095554 | 318.6383 | 0.048148 | 0 | 0 | 0.096296 | 318.8949 | 0.048705 | 0 | 0 | 0.097409 | 319.0659 | 0.049076 | 0 | 0 | 0.098151 | 319.3225 | 0.049632 | 0 | 0 | 0.099264 | 319.579 | 0.050189 | 0 | 0 | 0.10038 | 319.7501 | 0.05056 | 0 | 0 | 0.10112 | 320.0066 | 0.051116 | 0 | 0 | 0.10223 | 320.2632 | 0.051672 | 0 | 0 | 0.10334 | 320.3487 | 0.051858 | 0 | 0 | 0.10372 | 320.6053 | 0.052414 | 0 | 0 | 0.10483 | 320.8618 | 0.052971 | 0 | 0 | 0.10594 | 321.0328 | 0.053342 | 0 | 0 | 0.10668 | 321.2894 | 0.053898 | 0 | 0 | 0.1078 | 321.4604 | 0.054269 | 0 | 0 | 0.10854 | 321.6315 | 0.05464 | 0 | 0 | 0.10928
2017-12-09 09:00 | 289.8631 | 0.86397 |  | 304.3751 | 0.017211 | 0 | 0 | 0.034422 | 312.9283 | 0.035763 | 0 | 0 | 0.071526 | 319.9264 | 0.050942 | 0 | 0 | 0.10188 | 320.1856 | 0.051504 | 0 | 0 | 0.10301 | 320.3584 | 0.051879 | 0 | 0 | 0.10376 | 320.6176 | 0.052441 | 0 | 0 | 0.10488 | 320.8768 | 0.053003 | 0 | 0 | 0.10601 | 321.136 | 0.053566 | 0 | 0 | 0.10713 | 321.4816 | 0.054315 | 0 | 0 | 0.10863 | 321.7408 | 0.054877 | 0 | 0 | 0.10975 | 321.9136 | 0.055252 | 0 | 0 | 0.1105 | 322.1727 | 0.055814 | 0 | 0 | 0.11163 | 322.3455 | 0.056189 | 0 | 0 | 0.11238 | 322.6047 | 0.056751 | 0 | 0 | 0.1135 | 322.8639 | 0.057313 | 0 | 0 | 0.11463 | 323.0367 | 0.057688 | 0 | 0 | 0.11538 | 323.2959 | 0.05825 | 0 | 0 | 0.1165 | 323.5551 | 0.058813 | 0 | 0 | 0.11763 | 323.6415 | 0.059 | 0 | 0 | 0.118 | 323.9007 | 0.059562 | 0 | 0 | 0.11912 | 324.1599 | 0.060124 | 0 | 0 | 0.12025 | 324.3327 | 0.060499 | 0 | 0 | 0.121 | 324.5918 | 0.061061 | 0 | 0 | 0.12212 | 324.7646 | 0.061436 | 0 | 0 | 0.12287 | 324.9374 | 0.061811 | 0 | 0 | 0.12362
2017-12-09 10:00 | 290.877 | 0.86699 |  | 305.4397 | 0.01952 | 0 | 0 | 0.039041 | 314.0229 | 0.038137 | 0 | 0 | 0.076275 | 321.0455 | 0.053369 | 0 | 0 | 0.10674 | 321.3056 | 0.053933 | 0 | 0 | 0.10787 | 321.479 | 0.05431 | 0 | 0 | 0.10862 | 321.7391 | 0.054874 | 0 | 0 | 0.10975 | 321.9992 | 0.055438 | 0 | 0 | 0.11088 | 322.2593 | 0.056002 | 0 | 0 | 0.112 | 322.6061 | 0.056754 | 0 | 0 | 0.11351 | 322.8662 | 0.057318 | 0 | 0 | 0.11464 | 323.0396 | 0.057694 | 0 | 0 | 0.11539 | 323.2997 | 0.058259 | 0 | 0 | 0.11652 | 323.4731 | 0.058635 | 0 | 0 | 0.11727 | 323.7332 | 0.059199 | 0 | 0 | 0.1184 | 323.9932 | 0.059763 | 0 | 0 | 0.11953 | 324.1666 | 0.060139 | 0 | 0 | 0.12028 | 324.4267 | 0.060703 | 0 | 0 | 0.12141 | 324.6868 | 0.061267 | 0 | 0 | 0.12253 | 324.7735 | 0.061455 | 0 | 0 | 0.12291 | 325.0336 | 0.06202 | 0 | 0 | 0.12404 | 325.2937 | 0.062584 | 0 | 0 | 0.12517 | 325.4671 | 0.06296 | 0 | 0 | 0.12592 | 325.7272 | 0.063524 | 0 | 0 | 0.12705 | 325.9006 | 0.0639 | 0 | 0 | 0.1278 | 326.074 | 0.064276 | 0 | 0 | 0.12855
2017-12-09 11:00 | 292.0834 | 0.87058 |  | 306.7064 | 0.022268 | 0 | 0 | 0.044536 | 315.3252 | 0.040962 | 0 | 0 | 0.081924 | 322.3769 | 0.056257 | 0 | 0 | 0.11251 | 322.6381 | 0.056824 | 0 | 0 | 0.11365 | 322.8122 | 0.057201 | 0 | 0 | 0.1144 | 323.0734 | 0.057768 | 0 | 0 | 0.11554 | 323.3346 | 0.058334 | 0 | 0 | 0.11667 | 323.5957 | 0.058901 | 0 | 0 | 0.1178 | 323.944 | 0.059656 | 0 | 0 | 0.11931 | 324.2051 | 0.060223 | 0 | 0 | 0.12045 | 324.3793 | 0.0606 | 0 | 0 | 0.1212 | 324.6404 | 0.061167 | 0 | 0 | 0.12233 | 324.8146 | 0.061544 | 0 | 0 | 0.12309 | 325.0757 | 0.062111 | 0 | 0 | 0.12422 | 325.3369 | 0.062677 | 0 | 0 | 0.12535 | 325.511 | 0.063055 | 0 | 0 | 0.12611 | 325.7722 | 0.063622 | 0 | 0 | 0.12724 | 326.0334 | 0.064188 | 0 | 0 | 0.12838 | 326.1204 | 0.064377 | 0 | 0 | 0.12875 | 326.3816 | 0.064943 | 0 | 0 | 0.12989 | 326.6428 | 0.06551 | 0 | 0 | 0.13102 | 326.8169 | 0.065887 | 0 | 0 | 0.13177 | 327.0781 | 0.066454 | 0 | 0 | 0.13291 | 327.2522 | 0.066832 | 0 | 0 | 0.13366 | 327.4263 | 0.067209 | 0 | 0 | 0.13442
2017-12-09 12:00 | 288.4256 | 0.85968 |  | 302.8655 | 0.013937 | 0 | 0 | 0.027874 | 311.3764 | 0.032397 | 0 | 0 | 0.064794 | 318.3398 | 0.047501 | 0 | 0 | 0.095001 | 318.5977 | 0.04806 | 0 | 0 | 0.09612 | 318.7696 | 0.048433 | 0 | 0 | 0.096866 | 319.0275 | 0.048992 | 0 | 0 | 0.097985 | 319.2854 | 0.049552 | 0 | 0 | 0.099104 | 319.5434 | 0.050111 | 0 | 0 | 0.10022 | 319.8872 | 0.050857 | 0 | 0 | 0.10171 | 320.1451 | 0.051416 | 0 | 0 | 0.10283 | 320.3171 | 0.051789 | 0 | 0 | 0.10358 | 320.575 | 0.052349 | 0 | 0 | 0.1047 | 320.7469 | 0.052722 | 0 | 0 | 0.10544 | 321.0048 | 0.053281 | 0 | 0 | 0.10656 | 321.2627 | 0.05384 | 0 | 0 | 0.10768 | 321.4347 | 0.054213 | 0 | 0 | 0.10843 | 321.6926 | 0.054773 | 0 | 0 | 0.10955 | 321.9505 | 0.055332 | 0 | 0 | 0.11066 | 322.0364 | 0.055519 | 0 | 0 | 0.11104 | 322.2943 | 0.056078 | 0 | 0 | 0.11216 | 322.5522 | 0.056637 | 0 | 0 | 0.11327 | 322.7242 | 0.05701 | 0 | 0 | 0.11402 | 322.9821 | 0.05757 | 0 | 0 | 0.11514 | 323.154 | 0.057943 | 0 | 0 | 0.11589 | 323.3259 | 0.058316 | 0 | 0 | 0.11663
2017-12-09 13:00 | 287.5108 | 0.85695 |  | 301.9049 | 0.011853 | 0 | 0 | 0.023707 | 310.3888 | 0.030255 | 0 | 0 | 0.06051 | 317.3301 | 0.045311 | 0 | 0 | 0.090621 | 317.5872 | 0.045868 | 0 | 0 | 0.091737 | 317.7586 | 0.04624 | 0 | 0 | 0.09248 | 318.0157 | 0.046798 | 0 | 0 | 0.093595 | 318.2728 | 0.047355 | 0 | 0 | 0.094711 | 318.5298 | 0.047913 | 0 | 0 | 0.095826 | 318.8726 | 0.048656 | 0 | 0 | 0.097313 | 319.1297 | 0.049214 | 0 | 0 | 0.098428 | 319.3011 | 0.049586 | 0 | 0 | 0.099171 | 319.5582 | 0.050143 | 0 | 0 | 0.10029 | 319.7296 | 0.050515 | 0 | 0 | 0.10103 | 319.9867 | 0.051073 | 0 | 0 | 0.10215 | 320.2438 | 0.05163 | 0 | 0 | 0.10326 | 320.4151 | 0.052002 | 0 | 0 | 0.104 | 320.6722 | 0.05256 | 0 | 0 | 0.10512 | 320.9293 | 0.053117 | 0 | 0 | 0.10623 | 321.015 | 0.053303 | 0 | 0 | 0.10661 | 321.2721 | 0.053861 | 0 | 0 | 0.10772 | 321.5292 | 0.054418 | 0 | 0 | 0.10884 | 321.7006 | 0.05479 | 0 | 0 | 0.10958 | 321.9577 | 0.055348 | 0 | 0 | 0.1107 | 322.1291 | 0.05572 | 0 | 0 | 0.11144 | 322.3004 | 0.056091 | 0 | 0 | 0.11218
2017-12-09 14:00 | 287.2507 | 0.85618 |  | 301.6318 | 0.011261 | 0 | 0 | 0.022522 | 310.108 | 0.029646 | 0 | 0 | 0.059292 | 317.043 | 0.044688 | 0 | 0 | 0.089376 | 317.2999 | 0.045245 | 0 | 0 | 0.09049 | 317.4711 | 0.045616 | 0 | 0 | 0.091233 | 317.728 | 0.046174 | 0 | 0 | 0.092347 | 317.9848 | 0.046731 | 0 | 0 | 0.093461 | 318.2417 | 0.047288 | 0 | 0 | 0.094576 | 318.5841 | 0.048031 | 0 | 0 | 0.096061 | 318.841 | 0.048588 | 0 | 0 | 0.097176 | 319.0122 | 0.048959 | 0 | 0 | 0.097918 | 319.2691 | 0.049516 | 0 | 0 | 0.099033 | 319.4403 | 0.049888 | 0 | 0 | 0.099775 | 319.6972 | 0.050445 | 0 | 0 | 0.10089 | 319.954 | 0.051002 | 0 | 0 | 0.102 | 320.1253 | 0.051373 | 0 | 0 | 0.10275 | 320.3821 | 0.05193 | 0 | 0 | 0.10386 | 320.639 | 0.052488 | 0 | 0 | 0.10498 | 320.7246 | 0.052673 | 0 | 0 | 0.10535 | 320.9814 | 0.05323 | 0 | 0 | 0.10646 | 321.2383 | 0.053787 | 0 | 0 | 0.10757 | 321.4095 | 0.054159 | 0 | 0 | 0.10832 | 321.6664 | 0.054716 | 0 | 0 | 0.10943 | 321.8376 | 0.055087 | 0 | 0 | 0.11017 | 322.0089 | 0.055459 | 0 | 0 | 0.11092
2017-12-09 15:00 | 293.4534 | 0.87467 |  | 308.1451 | 0.025388 | 0 | 0 | 0.050777 | 316.8043 | 0.04417 | 0 | 0 | 0.08834 | 323.8891 | 0.059537 | 0 | 0 | 0.11907 | 324.1515 | 0.060106 | 0 | 0 | 0.12021 | 324.3264 | 0.060486 | 0 | 0 | 0.12097 | 324.5888 | 0.061055 | 0 | 0 | 0.12211 | 324.8512 | 0.061624 | 0 | 0 | 0.12325 | 325.1136 | 0.062193 | 0 | 0 | 0.12439 | 325.4635 | 0.062952 | 0 | 0 | 0.1259 | 325.7259 | 0.063521 | 0 | 0 | 0.12704 | 325.9008 | 0.063901 | 0 | 0 | 0.1278 | 326.1632 | 0.06447 | 0 | 0 | 0.12894 | 326.3382 | 0.064849 | 0 | 0 | 0.1297 | 326.6006 | 0.065418 | 0 | 0 | 0.13084 | 326.863 | 0.065987 | 0 | 0 | 0.13197 | 327.0379 | 0.066367 | 0 | 0 | 0.13273 | 327.3003 | 0.066936 | 0 | 0 | 0.13387 | 327.5627 | 0.067505 | 0 | 0 | 0.13501 | 327.6502 | 0.067695 | 0 | 0 | 0.13539 | 327.9126 | 0.068264 | 0 | 0 | 0.13653 | 328.175 | 0.068833 | 0 | 0 | 0.13767 | 328.3499 | 0.069213 | 0 | 0 | 0.13843 | 328.6123 | 0.069782 | 0 | 0 | 0.13956 | 328.7872 | 0.070161 | 0 | 0 | 0.14032 | 328.9622 | 0.070541 | 0 | 0 | 0.14108
2017-12-09 16:00 | 300.5093 | 0.8957 |  | 315.5542 | 0.041459 | 0 | 0 | 0.082917 | 324.4216 | 0.060692 | 0 | 0 | 0.12138 | 331.6767 | 0.076428 | 0 | 0 | 0.15286 | 331.9455 | 0.077011 | 0 | 0 | 0.15402 | 332.1246 | 0.0774 | 0 | 0 | 0.1548 | 332.3933 | 0.077983 | 0 | 0 | 0.15597 | 332.662 | 0.078566 | 0 | 0 | 0.15713 | 332.9307 | 0.079148 | 0 | 0 | 0.1583 | 333.289 | 0.079925 | 0 | 0 | 0.15985 | 333.5577 | 0.080508 | 0 | 0 | 0.16102 | 333.7368 | 0.080897 | 0 | 0 | 0.16179 | 334.0056 | 0.08148 | 0 | 0 | 0.16296 | 334.1847 | 0.081868 | 0 | 0 | 0.16374 | 334.4534 | 0.082451 | 0 | 0 | 0.1649 | 334.7221 | 0.083034 | 0 | 0 | 0.16607 | 334.9013 | 0.083422 | 0 | 0 | 0.16684 | 335.17 | 0.084005 | 0 | 0 | 0.16801 | 335.4387 | 0.084588 | 0 | 0 | 0.16918 | 335.5282 | 0.084782 | 0 | 0 | 0.16956 | 335.797 | 0.085365 | 0 | 0 | 0.17073 | 336.0657 | 0.085948 | 0 | 0 | 0.1719 | 336.2448 | 0.086337 | 0 | 0 | 0.17267 | 336.5135 | 0.086919 | 0 | 0 | 0.17384 | 336.6927 | 0.087308 | 0 | 0 | 0.17462 | 336.8718 | 0.087697 | 0 | 0 | 0.17539
2017-12-09 17:00 | 302.125 | 0.90051 |  | 317.2508 | 0.045139 | 0 | 0 | 0.090277 | 326.1659 | 0.064475 | 0 | 0 | 0.12895 | 333.46 | 0.080296 | 0 | 0 | 0.16059 | 333.7302 | 0.080882 | 0 | 0 | 0.16176 | 333.9103 | 0.081273 | 0 | 0 | 0.16255 | 334.1804 | 0.081859 | 0 | 0 | 0.16372 | 334.4506 | 0.082445 | 0 | 0 | 0.16489 | 334.7207 | 0.083031 | 0 | 0 | 0.16606 | 335.0809 | 0.083812 | 0 | 0 | 0.16762 | 335.3511 | 0.084398 | 0 | 0 | 0.1688 | 335.5312 | 0.084789 | 0 | 0 | 0.16958 | 335.8014 | 0.085375 | 0 | 0 | 0.17075 | 335.9815 | 0.085765 | 0 | 0 | 0.17153 | 336.2516 | 0.086351 | 0 | 0 | 0.1727 | 336.5218 | 0.086937 | 0 | 0 | 0.17387 | 336.7019 | 0.087328 | 0 | 0 | 0.17466 | 336.972 | 0.087914 | 0 | 0 | 0.17583 | 337.2422 | 0.0885 | 0 | 0 | 0.177 | 337.3322 | 0.088695 | 0 | 0 | 0.17739 | 337.6024 | 0.089281 | 0 | 0 | 0.17856 | 337.8725 | 0.089867 | 0 | 0 | 0.17973 | 338.0526 | 0.090258 | 0 | 0 | 0.18052 | 338.3228 | 0.090844 | 0 | 0 | 0.18169 | 338.5029 | 0.091234 | 0 | 0 | 0.18247 | 338.683 | 0.091625 | 0 | 0 | 0.18325
2017-12-09 18:00 | 306.0381 | 0.91218 |  | 321.3598 | 0.054051 | 0 | 0 | 0.1081 | 330.3903 | 0.073638 | 0 | 0 | 0.14728 | 337.779 | 0.089664 | 0 | 0 | 0.17933 | 338.0526 | 0.090258 | 0 | 0 | 0.18052 | 338.235 | 0.090653 | 0 | 0 | 0.18131 | 338.5087 | 0.091247 | 0 | 0 | 0.18249 | 338.7824 | 0.091841 | 0 | 0 | 0.18368 | 339.056 | 0.092434 | 0 | 0 | 0.18487 | 339.4209 | 0.093226 | 0 | 0 | 0.18645 | 339.6945 | 0.093819 | 0 | 0 | 0.18764 | 339.877 | 0.094215 | 0 | 0 | 0.18843 | 340.1506 | 0.094808 | 0 | 0 | 0.18962 | 340.3331 | 0.095204 | 0 | 0 | 0.19041 | 340.6067 | 0.095798 | 0 | 0 | 0.1916 | 340.8804 | 0.096391 | 0 | 0 | 0.19278 | 341.0628 | 0.096787 | 0 | 0 | 0.19357 | 341.3364 | 0.09738 | 0 | 0 | 0.19476 | 341.6101 | 0.097974 | 0 | 0 | 0.19595 | 341.7013 | 0.098172 | 0 | 0 | 0.19634 | 341.975 | 0.098765 | 0 | 0 | 0.19753 | 342.2486 | 0.099359 | 0 | 0 | 0.19872 | 342.4311 | 0.099755 | 0 | 0 | 0.19951 | 342.7047 | 0.10035 | 0 | 0 | 0.2007 | 342.8871 | 0.10074 | 0 | 0 | 0.20149 | 343.0696 | 0.10114 | 0 | 0 | 0.20228
2017-12-09 19:00 | 309.3081 | 0.92192 |  | 324.7935 | 0.061499 | 0 | 0 | 0.123 | 333.9205 | 0.081295 | 0 | 0 | 0.16259 | 341.3881 | 0.097492 | 0 | 0 | 0.19498 | 341.6647 | 0.098092 | 0 | 0 | 0.19618 | 341.8491 | 0.098492 | 0 | 0 | 0.19698 | 342.1256 | 0.099092 | 0 | 0 | 0.19818 | 342.4022 | 0.099692 | 0 | 0 | 0.19938 | 342.6788 | 0.10029 | 0 | 0 | 0.20058 | 343.0476 | 0.10109 | 0 | 0 | 0.20218 | 343.3241 | 0.10169 | 0 | 0 | 0.20338 | 343.5085 | 0.10209 | 0 | 0 | 0.20418 | 343.7851 | 0.10269 | 0 | 0 | 0.20538 | 343.9695 | 0.10309 | 0 | 0 | 0.20618 | 344.2461 | 0.10369 | 0 | 0 | 0.20738 | 344.5226 | 0.10429 | 0 | 0 | 0.20858 | 344.707 | 0.10469 | 0 | 0 | 0.20938 | 344.9836 | 0.10529 | 0 | 0 | 0.21058 | 345.2602 | 0.10589 | 0 | 0 | 0.21178 | 345.3524 | 0.10609 | 0 | 0 | 0.21218 | 345.6289 | 0.10669 | 0 | 0 | 0.21338 | 345.9055 | 0.10729 | 0 | 0 | 0.21458 | 346.0899 | 0.10769 | 0 | 0 | 0.21538 | 346.3665 | 0.10829 | 0 | 0 | 0.21658 | 346.5509 | 0.10869 | 0 | 0 | 0.21738 | 346.7353 | 0.10909 | 0 | 0 | 0.21818
2017-12-09 20:00 | 309.7616 | 0.92327 |  | 325.2697 | 0.062532 | 0 | 0 | 0.12506 | 334.4101 | 0.082357 | 0 | 0 | 0.16471 | 341.8887 | 0.098578 | 0 | 0 | 0.19716 | 342.1657 | 0.099179 | 0 | 0 | 0.19836 | 342.3503 | 0.099579 | 0 | 0 | 0.19916 | 342.6273 | 0.10018 | 0 | 0 | 0.20036 | 342.9043 | 0.10078 | 0 | 0 | 0.20156 | 343.1813 | 0.10138 | 0 | 0 | 0.20276 | 343.5506 | 0.10218 | 0 | 0 | 0.20437 | 343.8276 | 0.10278 | 0 | 0 | 0.20557 | 344.0122 | 0.10318 | 0 | 0 | 0.20637 | 344.2892 | 0.10378 | 0 | 0 | 0.20757 | 344.4738 | 0.10419 | 0 | 0 | 0.20837 | 344.7508 | 0.10479 | 0 | 0 | 0.20957 | 345.0278 | 0.10539 | 0 | 0 | 0.21077 | 345.2125 | 0.10579 | 0 | 0 | 0.21157 | 345.4894 | 0.10639 | 0 | 0 | 0.21278 | 345.7664 | 0.10699 | 0 | 0 | 0.21398 | 345.8588 | 0.10719 | 0 | 0 | 0.21438 | 346.1357 | 0.10779 | 0 | 0 | 0.21558 | 346.4127 | 0.10839 | 0 | 0 | 0.21678 | 346.5974 | 0.10879 | 0 | 0 | 0.21758 | 346.8744 | 0.10939 | 0 | 0 | 0.21878 | 347.059 | 0.10979 | 0 | 0 | 0.21959 | 347.2437 | 0.11019 | 0 | 0 | 0.22039
2017-12-09 21:00 | 310.2488 | 0.92473 |  | 325.7813 | 0.063641 | 0 | 0 | 0.12728 | 334.9361 | 0.083498 | 0 | 0 | 0.167 | 342.4264 | 0.099744 | 0 | 0 | 0.19949 | 342.7038 | 0.10035 | 0 | 0 | 0.20069 | 342.8888 | 0.10075 | 0 | 0 | 0.20149 | 343.1662 | 0.10135 | 0 | 0 | 0.2027 | 343.4436 | 0.10195 | 0 | 0 | 0.2039 | 343.721 | 0.10255 | 0 | 0 | 0.20511 | 344.0909 | 0.10335 | 0 | 0 | 0.20671 | 344.3683 | 0.10396 | 0 | 0 | 0.20791 | 344.5533 | 0.10436 | 0 | 0 | 0.20872 | 344.8307 | 0.10496 | 0 | 0 | 0.20992 | 345.0156 | 0.10536 | 0 | 0 | 0.21072 | 345.293 | 0.10596 | 0 | 0 | 0.21192 | 345.5705 | 0.10656 | 0 | 0 | 0.21313 | 345.7554 | 0.10697 | 0 | 0 | 0.21393 | 346.0328 | 0.10757 | 0 | 0 | 0.21513 | 346.3102 | 0.10817 | 0 | 0 | 0.21634 | 346.4027 | 0.10837 | 0 | 0 | 0.21674 | 346.6801 | 0.10897 | 0 | 0 | 0.21794 | 346.9576 | 0.10957 | 0 | 0 | 0.21915 | 347.1425 | 0.10997 | 0 | 0 | 0.21995 | 347.4199 | 0.11058 | 0 | 0 | 0.22115 | 347.6049 | 0.11098 | 0 | 0 | 0.22195 | 347.7898 | 0.11138 | 0 | 0 | 0.22276
2017-12-09 22:00 | 315.5366 | 0.94049 |  | 331.3339 | 0.075685 | 0 | 0 | 0.15137 | 340.6447 | 0.09588 | 0 | 0 | 0.19176 | 348.2626 | 0.1124 | 0 | 0 | 0.22481 | 348.5448 | 0.11302 | 0 | 0 | 0.22603 | 348.7329 | 0.11342 | 0 | 0 | 0.22685 | 349.015 | 0.11404 | 0 | 0 | 0.22807 | 349.2972 | 0.11465 | 0 | 0 | 0.22929 | 349.5793 | 0.11526 | 0 | 0 | 0.23052 | 349.9555 | 0.11608 | 0 | 0 | 0.23215 | 350.2377 | 0.11669 | 0 | 0 | 0.23337 | 350.4258 | 0.1171 | 0 | 0 | 0.23419 | 350.7079 | 0.11771 | 0 | 0 | 0.23541 | 350.896 | 0.11812 | 0 | 0 | 0.23623 | 351.1782 | 0.11873 | 0 | 0 | 0.23745 | 351.4603 | 0.11934 | 0 | 0 | 0.23868 | 351.6484 | 0.11975 | 0 | 0 | 0.23949 | 351.9306 | 0.12036 | 0 | 0 | 0.24072 | 352.2127 | 0.12097 | 0 | 0 | 0.24194 | 352.3067 | 0.12117 | 0 | 0 | 0.24235 | 352.5889 | 0.12179 | 0 | 0 | 0.24357 | 352.871 | 0.1224 | 0 | 0 | 0.2448 | 353.0591 | 0.12281 | 0 | 0 | 0.24561 | 353.3413 | 0.12342 | 0 | 0 | 0.24684 | 353.5294 | 0.12383 | 0 | 0 | 0.24765 | 353.7175 | 0.12423 | 0 | 0 | 0.24847
2017-12-09 23:00 | 312.6381 | 0.93185 |  | 328.2902 | 0.069083 | 0 | 0 | 0.13817 | 337.5155 | 0.089093 | 0 | 0 | 0.17819 | 345.0635 | 0.10546 | 0 | 0 | 0.21093 | 345.343 | 0.10607 | 0 | 0 | 0.21214 | 345.5294 | 0.10647 | 0 | 0 | 0.21295 | 345.8089 | 0.10708 | 0 | 0 | 0.21416 | 346.0885 | 0.10769 | 0 | 0 | 0.21538 | 346.3681 | 0.10829 | 0 | 0 | 0.21659 | 346.7408 | 0.1091 | 0 | 0 | 0.2182 | 347.0203 | 0.10971 | 0 | 0 | 0.21942 | 347.2067 | 0.11011 | 0 | 0 | 0.22023 | 347.4863 | 0.11072 | 0 | 0 | 0.22144 | 347.6726 | 0.11112 | 0 | 0 | 0.22225 | 347.9522 | 0.11173 | 0 | 0 | 0.22346 | 348.2317 | 0.11234 | 0 | 0 | 0.22467 | 348.4181 | 0.11274 | 0 | 0 | 0.22548 | 348.6977 | 0.11335 | 0 | 0 | 0.22669 | 348.9772 | 0.11395 | 0 | 0 | 0.22791 | 349.0704 | 0.11416 | 0 | 0 | 0.22831 | 349.35 | 0.11476 | 0 | 0 | 0.22952 | 349.6295 | 0.11537 | 0 | 0 | 0.23074 | 349.8159 | 0.11577 | 0 | 0 | 0.23154 | 350.0954 | 0.11638 | 0 | 0 | 0.23276 | 350.2818 | 0.11678 | 0 | 0 | 0.23357 | 350.4682 | 0.11719 | 0 | 0 | 0.23437
2017-12-10 | 307.9874 | 0.91799 |  | 323.4067 | 0.058491 | 0 | 0 | 0.11698 | 332.4948 | 0.078203 | 0 | 0 | 0.15641 | 339.9305 | 0.094331 | 0 | 0 | 0.18866 | 340.2059 | 0.094928 | 0 | 0 | 0.18986 | 340.3895 | 0.095326 | 0 | 0 | 0.19065 | 340.6649 | 0.095924 | 0 | 0 | 0.19185 | 340.9403 | 0.096521 | 0 | 0 | 0.19304 | 341.2157 | 0.097118 | 0 | 0 | 0.19424 | 341.5829 | 0.097915 | 0 | 0 | 0.19583 | 341.8582 | 0.098512 | 0 | 0 | 0.19702 | 342.0418 | 0.09891 | 0 | 0 | 0.19782 | 342.3172 | 0.099508 | 0 | 0 | 0.19902 | 342.5008 | 0.099906 | 0 | 0 | 0.19981 | 342.7762 | 0.1005 | 0 | 0 | 0.20101 | 343.0516 | 0.1011 | 0 | 0 | 0.2022 | 343.2352 | 0.1015 | 0 | 0 | 0.203 | 343.5106 | 0.1021 | 0 | 0 | 0.20419 | 343.786 | 0.10269 | 0 | 0 | 0.20539 | 343.8778 | 0.10289 | 0 | 0 | 0.20579 | 344.1532 | 0.10349 | 0 | 0 | 0.20698 | 344.4286 | 0.10409 | 0 | 0 | 0.20817 | 344.6122 | 0.10449 | 0 | 0 | 0.20897 | 344.8876 | 0.10508 | 0 | 0 | 0.21017 | 345.0712 | 0.10548 | 0 | 0 | 0.21096 | 345.2548 | 0.10588 | 0 | 0 | 0.21176
2017-12-10 01:00 | 305.5933 | 0.91085 |  | 320.8927 | 0.053038 | 0 | 0 | 0.10608 | 329.9102 | 0.072597 | 0 | 0 | 0.14519 | 337.288 | 0.088599 | 0 | 0 | 0.1772 | 337.5613 | 0.089192 | 0 | 0 | 0.17838 | 337.7435 | 0.089587 | 0 | 0 | 0.17917 | 338.0167 | 0.09018 | 0 | 0 | 0.18036 | 338.29 | 0.090773 | 0 | 0 | 0.18155 | 338.5632 | 0.091365 | 0 | 0 | 0.18273 | 338.9276 | 0.092156 | 0 | 0 | 0.18431 | 339.2008 | 0.092748 | 0 | 0 | 0.1855 | 339.383 | 0.093143 | 0 | 0 | 0.18629 | 339.6563 | 0.093736 | 0 | 0 | 0.18747 | 339.8384 | 0.094131 | 0 | 0 | 0.18826 | 340.1117 | 0.094724 | 0 | 0 | 0.18945 | 340.3849 | 0.095317 | 0 | 0 | 0.19063 | 340.5671 | 0.095712 | 0 | 0 | 0.19142 | 340.8404 | 0.096304 | 0 | 0 | 0.19261 | 341.1136 | 0.096897 | 0 | 0 | 0.19379 | 341.2047 | 0.097095 | 0 | 0 | 0.19419 | 341.478 | 0.097687 | 0 | 0 | 0.19537 | 341.7512 | 0.09828 | 0 | 0 | 0.19656 | 341.9334 | 0.098675 | 0 | 0 | 0.19735 | 342.2066 | 0.099268 | 0 | 0 | 0.19854 | 342.3888 | 0.099663 | 0 | 0 | 0.19933 | 342.571 | 0.10006 | 0 | 0 | 0.20012
2017-12-10 02:00 | 311.754 | 0.92921 |  | 327.3618 | 0.067069 | 0 | 0 | 0.13414 | 336.561 | 0.087023 | 0 | 0 | 0.17405 | 344.0877 | 0.10335 | 0 | 0 | 0.2067 | 344.3664 | 0.10395 | 0 | 0 | 0.2079 | 344.5523 | 0.10436 | 0 | 0 | 0.20871 | 344.831 | 0.10496 | 0 | 0 | 0.20992 | 345.1098 | 0.10556 | 0 | 0 | 0.21113 | 345.3886 | 0.10617 | 0 | 0 | 0.21234 | 345.7603 | 0.10698 | 0 | 0 | 0.21395 | 346.039 | 0.10758 | 0 | 0 | 0.21516 | 346.2249 | 0.10798 | 0 | 0 | 0.21597 | 346.5036 | 0.10859 | 0 | 0 | 0.21718 | 346.6895 | 0.10899 | 0 | 0 | 0.21798 | 346.9682 | 0.1096 | 0 | 0 | 0.21919 | 347.247 | 0.1102 | 0 | 0 | 0.2204 | 347.4328 | 0.1106 | 0 | 0 | 0.22121 | 347.7116 | 0.11121 | 0 | 0 | 0.22242 | 347.9904 | 0.11181 | 0 | 0 | 0.22363 | 348.0833 | 0.11201 | 0 | 0 | 0.22403 | 348.3621 | 0.11262 | 0 | 0 | 0.22524 | 348.6408 | 0.11322 | 0 | 0 | 0.22645 | 348.8267 | 0.11363 | 0 | 0 | 0.22725 | 349.1054 | 0.11423 | 0 | 0 | 0.22846 | 349.2913 | 0.11463 | 0 | 0 | 0.22927 | 349.4771 | 0.11504 | 0 | 0 | 0.23007
2017-12-10 03:00 | 319.4917 | 0.95228 |  | 335.487 | 0.084693 | 0 | 0 | 0.16939 | 344.9145 | 0.10514 | 0 | 0 | 0.21028 | 352.628 | 0.12187 | 0 | 0 | 0.24374 | 352.9136 | 0.12249 | 0 | 0 | 0.24498 | 353.1041 | 0.1229 | 0 | 0 | 0.24581 | 353.3898 | 0.12352 | 0 | 0 | 0.24705 | 353.6755 | 0.12414 | 0 | 0 | 0.24829 | 353.9611 | 0.12476 | 0 | 0 | 0.24953 | 354.3421 | 0.12559 | 0 | 0 | 0.25118 | 354.6277 | 0.12621 | 0 | 0 | 0.25242 | 354.8182 | 0.12662 | 0 | 0 | 0.25324 | 355.1039 | 0.12724 | 0 | 0 | 0.25448 | 355.2943 | 0.12766 | 0 | 0 | 0.25531 | 355.58 | 0.12827 | 0 | 0 | 0.25655 | 355.8657 | 0.12889 | 0 | 0 | 0.25779 | 356.0561 | 0.12931 | 0 | 0 | 0.25861 | 356.3418 | 0.12993 | 0 | 0 | 0.25985 | 356.6275 | 0.13055 | 0 | 0 | 0.26109 | 356.7227 | 0.13075 | 0 | 0 | 0.26151 | 357.0084 | 0.13137 | 0 | 0 | 0.26275 | 357.2941 | 0.13199 | 0 | 0 | 0.26399 | 357.4846 | 0.13241 | 0 | 0 | 0.26481 | 357.7702 | 0.13303 | 0 | 0 | 0.26605 | 357.9607 | 0.13344 | 0 | 0 | 0.26688 | 358.1512 | 0.13385 | 0 | 0 | 0.2677
2017-12-10 04:00 | 321.9678 | 0.95966 |  | 338.0871 | 0.090333 | 0 | 0 | 0.18067 | 347.5877 | 0.11094 | 0 | 0 | 0.22188 | 355.3609 | 0.1278 | 0 | 0 | 0.2556 | 355.6488 | 0.12842 | 0 | 0 | 0.25685 | 355.8407 | 0.12884 | 0 | 0 | 0.25768 | 356.1286 | 0.12946 | 0 | 0 | 0.25893 | 356.4165 | 0.13009 | 0 | 0 | 0.26018 | 356.7044 | 0.13071 | 0 | 0 | 0.26143 | 357.0883 | 0.13155 | 0 | 0 | 0.26309 | 357.3762 | 0.13217 | 0 | 0 | 0.26434 | 357.5681 | 0.13259 | 0 | 0 | 0.26517 | 357.856 | 0.13321 | 0 | 0 | 0.26642 | 358.0479 | 0.13363 | 0 | 0 | 0.26726 | 358.3358 | 0.13425 | 0 | 0 | 0.2685 | 358.6237 | 0.13488 | 0 | 0 | 0.26975 | 358.8157 | 0.13529 | 0 | 0 | 0.27059 | 359.1036 | 0.13592 | 0 | 0 | 0.27183 | 359.3915 | 0.13654 | 0 | 0 | 0.27308 | 359.4874 | 0.13675 | 0 | 0 | 0.2735 | 359.7753 | 0.13737 | 0 | 0 | 0.27475 | 360.0632 | 0.138 | 0 | 0 | 0.276 | 360.2552 | 0.13842 | 0 | 0 | 0.27683 | 360.5431 | 0.13904 | 0 | 0 | 0.27808 | 360.735 | 0.13946 | 0 | 0 | 0.27891 | 360.9269 | 0.13987 | 0 | 0 | 0.27974
2017-12-10 05:00 | 320.5835 | 0.95553 |  | 336.6334 | 0.08718 | 0 | 0 | 0.17436 | 346.0932 | 0.1077 | 0 | 0 | 0.2154 | 353.833 | 0.12449 | 0 | 0 | 0.24897 | 354.1196 | 0.12511 | 0 | 0 | 0.25021 | 354.3108 | 0.12552 | 0 | 0 | 0.25104 | 354.5974 | 0.12614 | 0 | 0 | 0.25229 | 354.8841 | 0.12677 | 0 | 0 | 0.25353 | 355.1707 | 0.12739 | 0 | 0 | 0.25477 | 355.5529 | 0.12822 | 0 | 0 | 0.25643 | 355.8396 | 0.12884 | 0 | 0 | 0.25768 | 356.0307 | 0.12925 | 0 | 0 | 0.2585 | 356.3174 | 0.12987 | 0 | 0 | 0.25975 | 356.5085 | 0.13029 | 0 | 0 | 0.26058 | 356.7951 | 0.13091 | 0 | 0 | 0.26182 | 357.0818 | 0.13153 | 0 | 0 | 0.26306 | 357.2729 | 0.13195 | 0 | 0 | 0.26389 | 357.5596 | 0.13257 | 0 | 0 | 0.26514 | 357.8462 | 0.13319 | 0 | 0 | 0.26638 | 357.9418 | 0.1334 | 0 | 0 | 0.26679 | 358.2284 | 0.13402 | 0 | 0 | 0.26804 | 358.5151 | 0.13464 | 0 | 0 | 0.26928 | 358.7062 | 0.13506 | 0 | 0 | 0.27011 | 358.9929 | 0.13568 | 0 | 0 | 0.27135 | 359.184 | 0.13609 | 0 | 0 | 0.27218 | 359.3751 | 0.13651 | 0 | 0 | 0.27301
2017-12-10 06:00 | 318.4692 | 0.94923 |  | 334.4133 | 0.082364 | 0 | 0 | 0.16473 | 343.8106 | 0.10275 | 0 | 0 | 0.20549 | 351.4994 | 0.11942 | 0 | 0 | 0.23885 | 351.7842 | 0.12004 | 0 | 0 | 0.24008 | 351.974 | 0.12045 | 0 | 0 | 0.24091 | 352.2588 | 0.12107 | 0 | 0 | 0.24214 | 352.5435 | 0.12169 | 0 | 0 | 0.24338 | 352.8283 | 0.12231 | 0 | 0 | 0.24461 | 353.208 | 0.12313 | 0 | 0 | 0.24626 | 353.4928 | 0.12375 | 0 | 0 | 0.24749 | 353.6826 | 0.12416 | 0 | 0 | 0.24832 | 353.9674 | 0.12478 | 0 | 0 | 0.24955 | 354.1572 | 0.12519 | 0 | 0 | 0.25038 | 354.442 | 0.12581 | 0 | 0 | 0.25161 | 354.7268 | 0.12642 | 0 | 0 | 0.25285 | 354.9166 | 0.12684 | 0 | 0 | 0.25367 | 355.2014 | 0.12745 | 0 | 0 | 0.25491 | 355.4862 | 0.12807 | 0 | 0 | 0.25614 | 355.5811 | 0.12828 | 0 | 0 | 0.25655 | 355.8658 | 0.12889 | 0 | 0 | 0.25779 | 356.1506 | 0.12951 | 0 | 0 | 0.25902 | 356.3405 | 0.12992 | 0 | 0 | 0.25985 | 356.6252 | 0.13054 | 0 | 0 | 0.26108 | 356.8151 | 0.13095 | 0 | 0 | 0.26191 | 357.0049 | 0.13137 | 0 | 0 | 0.26273
2017-12-10 07:00 | 322.1299 | 0.96014 |  | 338.2573 | 0.090702 | 0 | 0 | 0.1814 | 347.7627 | 0.11132 | 0 | 0 | 0.22264 | 355.5398 | 0.12819 | 0 | 0 | 0.25637 | 355.8278 | 0.12881 | 0 | 0 | 0.25762 | 356.0199 | 0.12923 | 0 | 0 | 0.25846 | 356.3079 | 0.12985 | 0 | 0 | 0.25971 | 356.596 | 0.13048 | 0 | 0 | 0.26096 | 356.884 | 0.1311 | 0 | 0 | 0.26221 | 357.2681 | 0.13194 | 0 | 0 | 0.26387 | 357.5561 | 0.13256 | 0 | 0 | 0.26512 | 357.7481 | 0.13298 | 0 | 0 | 0.26595 | 358.0362 | 0.1336 | 0 | 0 | 0.2672 | 358.2282 | 0.13402 | 0 | 0 | 0.26804 | 358.5162 | 0.13464 | 0 | 0 | 0.26929 | 358.8043 | 0.13527 | 0 | 0 | 0.27054 | 358.9963 | 0.13568 | 0 | 0 | 0.27137 | 359.2843 | 0.13631 | 0 | 0 | 0.27262 | 359.5724 | 0.13693 | 0 | 0 | 0.27387 | 359.6684 | 0.13714 | 0 | 0 | 0.27428 | 359.9564 | 0.13777 | 0 | 0 | 0.27553 | 360.2445 | 0.13839 | 0 | 0 | 0.27678 | 360.4365 | 0.13881 | 0 | 0 | 0.27762 | 360.7246 | 0.13943 | 0 | 0 | 0.27887 | 360.9166 | 0.13985 | 0 | 0 | 0.2797 | 361.1086 | 0.14027 | 0 | 0 | 0.28053
2017-12-10 08:00 | 318.759 | 0.95009 |  | 334.7176 | 0.083024 | 0 | 0 | 0.16605 | 344.1235 | 0.10343 | 0 | 0 | 0.20685 | 351.8193 | 0.12012 | 0 | 0 | 0.24024 | 352.1043 | 0.12074 | 0 | 0 | 0.24147 | 352.2943 | 0.12115 | 0 | 0 | 0.2423 | 352.5793 | 0.12177 | 0 | 0 | 0.24353 | 352.8644 | 0.12238 | 0 | 0 | 0.24477 | 353.1494 | 0.123 | 0 | 0 | 0.24601 | 353.5294 | 0.12383 | 0 | 0 | 0.24765 | 353.8145 | 0.12445 | 0 | 0 | 0.24889 | 354.0045 | 0.12486 | 0 | 0 | 0.24971 | 354.2895 | 0.12548 | 0 | 0 | 0.25095 | 354.4795 | 0.12589 | 0 | 0 | 0.25178 | 354.7645 | 0.12651 | 0 | 0 | 0.25301 | 355.0496 | 0.12712 | 0 | 0 | 0.25425 | 355.2396 | 0.12754 | 0 | 0 | 0.25507 | 355.5246 | 0.12815 | 0 | 0 | 0.25631 | 355.8096 | 0.12877 | 0 | 0 | 0.25755 | 355.9047 | 0.12898 | 0 | 0 | 0.25796 | 356.1897 | 0.1296 | 0 | 0 | 0.25919 | 356.4747 | 0.13022 | 0 | 0 | 0.26043 | 356.6647 | 0.13063 | 0 | 0 | 0.26125 | 356.9498 | 0.13125 | 0 | 0 | 0.26249 | 357.1398 | 0.13166 | 0 | 0 | 0.26332 | 357.3298 | 0.13207 | 0 | 0 | 0.26414
2017-12-10 09:00 | 326.2309 | 0.97236 |  | 342.5636 | 0.10004 | 0 | 0 | 0.20008 | 352.19 | 0.12092 | 0 | 0 | 0.24184 | 360.0661 | 0.13801 | 0 | 0 | 0.27601 | 360.3578 | 0.13864 | 0 | 0 | 0.27728 | 360.5523 | 0.13906 | 0 | 0 | 0.27812 | 360.844 | 0.13969 | 0 | 0 | 0.27938 | 361.1357 | 0.14033 | 0 | 0 | 0.28065 | 361.4274 | 0.14096 | 0 | 0 | 0.28192 | 361.8164 | 0.1418 | 0 | 0 | 0.2836 | 362.1081 | 0.14243 | 0 | 0 | 0.28487 | 362.3026 | 0.14286 | 0 | 0 | 0.28571 | 362.5943 | 0.14349 | 0 | 0 | 0.28698 | 362.7888 | 0.14391 | 0 | 0 | 0.28782 | 363.0805 | 0.14454 | 0 | 0 | 0.28909 | 363.3722 | 0.14518 | 0 | 0 | 0.29035 | 363.5666 | 0.1456 | 0 | 0 | 0.2912 | 363.8584 | 0.14623 | 0 | 0 | 0.29246 | 364.1501 | 0.14686 | 0 | 0 | 0.29373 | 364.2473 | 0.14707 | 0 | 0 | 0.29415 | 364.539 | 0.14771 | 0.0090563 | 0 | 0.30447 | 364.8307 | 0.14834 | 0.028061 | 0 | 0.32474 | 365.0252 | 0.14876 | 0.040731 | 0 | 0.33825 | 365.3169 | 0.14939 | 0.059736 | 0 | 0.35852 | 365.5114 | 0.14982 | 0.072406 | 0 | 0.37204 | 365.7058 | 0.15024 | 0.085076 | 0 | 0.38555
2017-12-10 10:00 | 328.0466 | 0.97777 |  | 344.4701 | 0.10418 | 0 | 0 | 0.20835 | 354.1501 | 0.12517 | 0 | 0 | 0.25035 | 362.0701 | 0.14235 | 0 | 0 | 0.2847 | 362.3634 | 0.14299 | 0 | 0 | 0.28598 | 362.559 | 0.14341 | 0 | 0 | 0.28682 | 362.8523 | 0.14405 | 0 | 0 | 0.2881 | 363.1456 | 0.14468 | 0 | 0 | 0.28937 | 363.4389 | 0.14532 | 0 | 0 | 0.29064 | 363.8301 | 0.14617 | 0 | 0 | 0.29234 | 364.1234 | 0.14681 | 0 | 0 | 0.29361 | 364.3189 | 0.14723 | 0 | 0 | 0.29446 | 364.6123 | 0.14787 | 0.01383 | 0 | 0.30956 | 364.8078 | 0.14829 | 0.02657 | 0 | 0.32315 | 365.1012 | 0.14893 | 0.045681 | 0 | 0.34353 | 365.3945 | 0.14956 | 0.064792 | 0 | 0.36392 | 365.5901 | 0.14999 | 0.077532 | 0 | 0.3775 | 365.8834 | 0.15062 | 0.096643 | 0 | 0.39789 | 366.1767 | 0.15126 | 0.11575 | 0 | 0.41827 | 366.2745 | 0.15147 | 0.12212 | 0 | 0.42507 | 366.5678 | 0.15211 | 0.14123 | 0 | 0.44545 | 366.8612 | 0.15274 | 0.16034 | 0 | 0.46583 | 367.0567 | 0.15317 | 0.17309 | 0 | 0.47942 | 367.35 | 0.1538 | 0.1922 | 0.0078212 | 0.51545 | 367.5456 | 0.15423 | 0.20494 | 0.020562 | 0.55452 | 367.7412 | 0.15465 | 0.21768 | 0.033302 | 0.59358
2017-12-10 11:00 | 320.3718 | 0.9549 |  | 336.4111 | 0.086697 | 0 | 0 | 0.17339 | 345.8646 | 0.1072 | 0 | 0 | 0.2144 | 353.5993 | 0.12398 | 0 | 0 | 0.24796 | 353.8858 | 0.1246 | 0 | 0 | 0.2492 | 354.0768 | 0.12501 | 0 | 0 | 0.25003 | 354.3632 | 0.12564 | 0 | 0 | 0.25127 | 354.6497 | 0.12626 | 0 | 0 | 0.25251 | 354.9362 | 0.12688 | 0 | 0 | 0.25376 | 355.3181 | 0.12771 | 0 | 0 | 0.25541 | 355.6046 | 0.12833 | 0 | 0 | 0.25666 | 355.7956 | 0.12874 | 0 | 0 | 0.25748 | 356.082 | 0.12936 | 0 | 0 | 0.25873 | 356.273 | 0.12978 | 0 | 0 | 0.25956 | 356.5595 | 0.1304 | 0 | 0 | 0.2608 | 356.846 | 0.13102 | 0 | 0 | 0.26204 | 357.0369 | 0.13143 | 0 | 0 | 0.26287 | 357.3234 | 0.13206 | 0 | 0 | 0.26411 | 357.6099 | 0.13268 | 0 | 0 | 0.26535 | 357.7054 | 0.13288 | 0 | 0 | 0.26577 | 357.9918 | 0.13351 | 0 | 0 | 0.26701 | 358.2783 | 0.13413 | 0 | 0 | 0.26825 | 358.4693 | 0.13454 | 0 | 0 | 0.26908 | 358.7558 | 0.13516 | 0 | 0 | 0.27033 | 358.9467 | 0.13558 | 0 | 0 | 0.27115 | 359.1377 | 0.13599 | 0 | 0 | 0.27198
2017-12-10 12:00 | 315.7065 | 0.94099 |  | 331.5122 | 0.076072 | 0 | 0 | 0.15214 | 340.8281 | 0.096278 | 0 | 0 | 0.19256 | 348.4501 | 0.11281 | 0 | 0 | 0.22562 | 348.7324 | 0.11342 | 0 | 0 | 0.22684 | 348.9206 | 0.11383 | 0 | 0 | 0.22766 | 349.2029 | 0.11444 | 0 | 0 | 0.22889 | 349.4852 | 0.11506 | 0 | 0 | 0.23011 | 349.7675 | 0.11567 | 0 | 0 | 0.23133 | 350.1439 | 0.11648 | 0 | 0 | 0.23297 | 350.4262 | 0.1171 | 0 | 0 | 0.23419 | 350.6144 | 0.1175 | 0 | 0 | 0.23501 | 350.8967 | 0.11812 | 0 | 0 | 0.23623 | 351.0849 | 0.11852 | 0 | 0 | 0.23705 | 351.3672 | 0.11914 | 0 | 0 | 0.23827 | 351.6495 | 0.11975 | 0 | 0 | 0.2395 | 351.8377 | 0.12016 | 0 | 0 | 0.24032 | 352.12 | 0.12077 | 0 | 0 | 0.24154 | 352.4023 | 0.12138 | 0 | 0 | 0.24276 | 352.4964 | 0.12159 | 0 | 0 | 0.24317 | 352.7787 | 0.1222 | 0 | 0 | 0.2444 | 353.061 | 0.12281 | 0 | 0 | 0.24562 | 353.2492 | 0.12322 | 0 | 0 | 0.24644 | 353.5315 | 0.12383 | 0 | 0 | 0.24766 | 353.7197 | 0.12424 | 0 | 0 | 0.24848 | 353.9079 | 0.12465 | 0 | 0 | 0.2493
2017-12-10 13:00 | 311.3562 | 0.92803 |  | 326.9441 | 0.066163 | 0 | 0 | 0.13233 | 336.1316 | 0.086091 | 0 | 0 | 0.17218 | 343.6486 | 0.1024 | 0 | 0 | 0.20479 | 343.927 | 0.103 | 0 | 0 | 0.206 | 344.1126 | 0.1034 | 0 | 0 | 0.2068 | 344.391 | 0.10401 | 0 | 0 | 0.20801 | 344.6695 | 0.10461 | 0 | 0 | 0.20922 | 344.9479 | 0.10521 | 0 | 0 | 0.21043 | 345.3191 | 0.10602 | 0 | 0 | 0.21204 | 345.5975 | 0.10662 | 0 | 0 | 0.21325 | 345.7831 | 0.10703 | 0 | 0 | 0.21405 | 346.0615 | 0.10763 | 0 | 0 | 0.21526 | 346.2471 | 0.10803 | 0 | 0 | 0.21606 | 346.5255 | 0.10864 | 0 | 0 | 0.21727 | 346.8039 | 0.10924 | 0 | 0 | 0.21848 | 346.9895 | 0.10964 | 0 | 0 | 0.21928 | 347.2679 | 0.11025 | 0 | 0 | 0.22049 | 347.5463 | 0.11085 | 0 | 0 | 0.2217 | 347.6391 | 0.11105 | 0 | 0 | 0.2221 | 347.9175 | 0.11165 | 0 | 0 | 0.22331 | 348.196 | 0.11226 | 0 | 0 | 0.22452 | 348.3816 | 0.11266 | 0 | 0 | 0.22532 | 348.66 | 0.11327 | 0 | 0 | 0.22653 | 348.8456 | 0.11367 | 0 | 0 | 0.22734 | 349.0312 | 0.11407 | 0 | 0 | 0.22814
2017-12-10 14:00 | 314.1463 | 0.93634 |  | 329.8739 | 0.072518 | 0 | 0 | 0.14504 | 339.1438 | 0.092624 | 0 | 0 | 0.18525 | 346.7281 | 0.10907 | 0 | 0 | 0.21815 | 347.009 | 0.10968 | 0 | 0 | 0.21937 | 347.1963 | 0.11009 | 0 | 0 | 0.22018 | 347.4772 | 0.1107 | 0 | 0 | 0.2214 | 347.7581 | 0.11131 | 0 | 0 | 0.22262 | 348.039 | 0.11192 | 0 | 0 | 0.22384 | 348.4136 | 0.11273 | 0 | 0 | 0.22546 | 348.6945 | 0.11334 | 0 | 0 | 0.22668 | 348.8817 | 0.11375 | 0 | 0 | 0.22749 | 349.1626 | 0.11436 | 0 | 0 | 0.22871 | 349.3499 | 0.11476 | 0 | 0 | 0.22952 | 349.6308 | 0.11537 | 0 | 0 | 0.23074 | 349.9117 | 0.11598 | 0 | 0 | 0.23196 | 350.099 | 0.11639 | 0 | 0 | 0.23277 | 350.3799 | 0.117 | 0 | 0 | 0.23399 | 350.6608 | 0.1176 | 0 | 0 | 0.23521 | 350.7544 | 0.11781 | 0 | 0 | 0.23562 | 351.0353 | 0.11842 | 0 | 0 | 0.23683 | 351.3162 | 0.11903 | 0 | 0 | 0.23805 | 351.5035 | 0.11943 | 0 | 0 | 0.23887 | 351.7844 | 0.12004 | 0 | 0 | 0.24008 | 351.9717 | 0.12045 | 0 | 0 | 0.2409 | 352.1589 | 0.12085 | 0 | 0 | 0.24171
2017-12-10 15:00 | 319.2002 | 0.95141 |  | 335.1809 | 0.084029 | 0 | 0 | 0.16806 | 344.5998 | 0.10446 | 0 | 0 | 0.20892 | 352.3062 | 0.12117 | 0 | 0 | 0.24235 | 352.5917 | 0.12179 | 0 | 0 | 0.24359 | 352.7819 | 0.12221 | 0 | 0 | 0.24441 | 353.0674 | 0.12282 | 0 | 0 | 0.24565 | 353.3528 | 0.12344 | 0 | 0 | 0.24689 | 353.6382 | 0.12406 | 0 | 0 | 0.24813 | 354.0188 | 0.12489 | 0 | 0 | 0.24978 | 354.3042 | 0.12551 | 0 | 0 | 0.25101 | 354.4945 | 0.12592 | 0 | 0 | 0.25184 | 354.7799 | 0.12654 | 0 | 0 | 0.25308 | 354.9702 | 0.12695 | 0 | 0 | 0.2539 | 355.2556 | 0.12757 | 0 | 0 | 0.25514 | 355.541 | 0.12819 | 0 | 0 | 0.25638 | 355.7313 | 0.1286 | 0 | 0 | 0.25721 | 356.0167 | 0.12922 | 0 | 0 | 0.25844 | 356.3021 | 0.12984 | 0 | 0 | 0.25968 | 356.3973 | 0.13005 | 0 | 0 | 0.26009 | 356.6827 | 0.13067 | 0 | 0 | 0.26133 | 356.9681 | 0.13129 | 0 | 0 | 0.26257 | 357.1584 | 0.1317 | 0 | 0 | 0.2634 | 357.4438 | 0.13232 | 0 | 0 | 0.26463 | 357.6341 | 0.13273 | 0 | 0 | 0.26546 | 357.8244 | 0.13314 | 0 | 0 | 0.26629
2017-12-10 16:00 | 318.4171 | 0.94907 |  | 334.3586 | 0.082245 | 0 | 0 | 0.16449 | 343.7544 | 0.10262 | 0 | 0 | 0.20525 | 351.4419 | 0.1193 | 0 | 0 | 0.2386 | 351.7266 | 0.11992 | 0 | 0 | 0.23983 | 351.9165 | 0.12033 | 0 | 0 | 0.24066 | 352.2012 | 0.12095 | 0 | 0 | 0.24189 | 352.4859 | 0.12156 | 0 | 0 | 0.24313 | 352.7706 | 0.12218 | 0 | 0 | 0.24436 | 353.1503 | 0.123 | 0 | 0 | 0.24601 | 353.435 | 0.12362 | 0 | 0 | 0.24724 | 353.6248 | 0.12403 | 0 | 0 | 0.24807 | 353.9095 | 0.12465 | 0 | 0 | 0.2493 | 354.0993 | 0.12506 | 0 | 0 | 0.25013 | 354.384 | 0.12568 | 0 | 0 | 0.25136 | 354.6688 | 0.1263 | 0 | 0 | 0.2526 | 354.8586 | 0.12671 | 0 | 0 | 0.25342 | 355.1433 | 0.12733 | 0 | 0 | 0.25465 | 355.428 | 0.12795 | 0 | 0 | 0.25589 | 355.5229 | 0.12815 | 0 | 0 | 0.2563 | 355.8077 | 0.12877 | 0 | 0 | 0.25754 | 356.0924 | 0.12939 | 0 | 0 | 0.25877 | 356.2822 | 0.1298 | 0 | 0 | 0.2596 | 356.5669 | 0.13042 | 0 | 0 | 0.26083 | 356.7567 | 0.13083 | 0 | 0 | 0.26165 | 356.9465 | 0.13124 | 0 | 0 | 0.26248
2017-12-10 17:00 | 320.9085 | 0.9565 |  | 336.9747 | 0.08792 | 0 | 0 | 0.17584 | 346.4441 | 0.10846 | 0 | 0 | 0.21692 | 354.1917 | 0.12526 | 0 | 0 | 0.25053 | 354.4787 | 0.12589 | 0 | 0 | 0.25177 | 354.67 | 0.1263 | 0 | 0 | 0.2526 | 354.9569 | 0.12692 | 0 | 0 | 0.25385 | 355.2439 | 0.12755 | 0 | 0 | 0.25509 | 355.5308 | 0.12817 | 0 | 0 | 0.25634 | 355.9134 | 0.129 | 0 | 0 | 0.258 | 356.2004 | 0.12962 | 0 | 0 | 0.25924 | 356.3917 | 0.13004 | 0 | 0 | 0.26007 | 356.6786 | 0.13066 | 0 | 0 | 0.26132 | 356.8699 | 0.13107 | 0 | 0 | 0.26214 | 357.1569 | 0.13169 | 0 | 0 | 0.26339 | 357.4438 | 0.13232 | 0 | 0 | 0.26463 | 357.6351 | 0.13273 | 0 | 0 | 0.26546 | 357.9221 | 0.13335 | 0 | 0 | 0.26671 | 358.209 | 0.13398 | 0 | 0 | 0.26795 | 358.3047 | 0.13418 | 0 | 0 | 0.26837 | 358.5916 | 0.13481 | 0 | 0 | 0.26961 | 358.8786 | 0.13543 | 0 | 0 | 0.27086 | 359.0699 | 0.13584 | 0 | 0 | 0.27169 | 359.3568 | 0.13647 | 0 | 0 | 0.27293 | 359.5481 | 0.13688 | 0 | 0 | 0.27376 | 359.7394 | 0.1373 | 0 | 0 | 0.27459
2017-12-10 18:00 | 320.3318 | 0.95478 |  | 336.3692 | 0.086606 | 0 | 0 | 0.17321 | 345.8215 | 0.10711 | 0 | 0 | 0.21422 | 353.5552 | 0.12388 | 0 | 0 | 0.24777 | 353.8417 | 0.1245 | 0 | 0 | 0.24901 | 354.0326 | 0.12492 | 0 | 0 | 0.24984 | 354.319 | 0.12554 | 0 | 0 | 0.25108 | 354.6055 | 0.12616 | 0 | 0 | 0.25232 | 354.8919 | 0.12678 | 0 | 0 | 0.25356 | 355.2738 | 0.12761 | 0 | 0 | 0.25522 | 355.5603 | 0.12823 | 0 | 0 | 0.25646 | 355.7512 | 0.12865 | 0 | 0 | 0.25729 | 356.0377 | 0.12927 | 0 | 0 | 0.25853 | 356.2286 | 0.12968 | 0 | 0 | 0.25936 | 356.515 | 0.1303 | 0 | 0 | 0.26061 | 356.8015 | 0.13092 | 0 | 0 | 0.26185 | 356.9924 | 0.13134 | 0 | 0 | 0.26268 | 357.2789 | 0.13196 | 0 | 0 | 0.26392 | 357.5653 | 0.13258 | 0 | 0 | 0.26516 | 357.6608 | 0.13279 | 0 | 0 | 0.26558 | 357.9472 | 0.13341 | 0 | 0 | 0.26682 | 358.2336 | 0.13403 | 0 | 0 | 0.26806 | 358.4246 | 0.13444 | 0 | 0 | 0.26889 | 358.711 | 0.13507 | 0 | 0 | 0.27013 | 358.902 | 0.13548 | 0 | 0 | 0.27096 | 359.093 | 0.13589 | 0 | 0 | 0.27179
2017-12-10 19:00 | 324.6784 | 0.96774 |  | 340.9333 | 0.096506 | 0 | 0 | 0.19301 | 350.5139 | 0.11729 | 0 | 0 | 0.23457 | 358.3525 | 0.13429 | 0 | 0 | 0.26858 | 358.6429 | 0.13492 | 0 | 0 | 0.26984 | 358.8364 | 0.13534 | 0 | 0 | 0.27068 | 359.1267 | 0.13597 | 0 | 0 | 0.27194 | 359.417 | 0.1366 | 0 | 0 | 0.27319 | 359.7074 | 0.13723 | 0 | 0 | 0.27445 | 360.0945 | 0.13807 | 0 | 0 | 0.27613 | 360.3848 | 0.1387 | 0 | 0 | 0.27739 | 360.5783 | 0.13912 | 0 | 0 | 0.27823 | 360.8686 | 0.13975 | 0 | 0 | 0.27949 | 361.0622 | 0.14017 | 0 | 0 | 0.28033 | 361.3525 | 0.1408 | 0 | 0 | 0.28159 | 361.6428 | 0.14142 | 0 | 0 | 0.28285 | 361.8364 | 0.14184 | 0 | 0 | 0.28369 | 362.1267 | 0.14247 | 0 | 0 | 0.28495 | 362.417 | 0.1431 | 0 | 0 | 0.28621 | 362.5138 | 0.14331 | 0 | 0 | 0.28663 | 362.8041 | 0.14394 | 0 | 0 | 0.28789 | 363.0944 | 0.14457 | 0 | 0 | 0.28915 | 363.288 | 0.14499 | 0 | 0 | 0.28999 | 363.5783 | 0.14562 | 0 | 0 | 0.29125 | 363.7719 | 0.14604 | 0 | 0 | 0.29209 | 363.9654 | 0.14646 | 0 | 0 | 0.29293
2017-12-10 20:00 | 318.1287 | 0.94821 |  | 334.0557 | 0.081588 | 0 | 0 | 0.16318 | 343.443 | 0.10195 | 0 | 0 | 0.2039 | 351.1235 | 0.11861 | 0 | 0 | 0.23722 | 351.408 | 0.11923 | 0 | 0 | 0.23845 | 351.5977 | 0.11964 | 0 | 0 | 0.23927 | 351.8821 | 0.12025 | 0 | 0 | 0.24051 | 352.1666 | 0.12087 | 0 | 0 | 0.24174 | 352.451 | 0.12149 | 0 | 0 | 0.24298 | 352.8303 | 0.12231 | 0 | 0 | 0.24462 | 353.1148 | 0.12293 | 0 | 0 | 0.24586 | 353.3044 | 0.12334 | 0 | 0 | 0.24668 | 353.5889 | 0.12396 | 0 | 0 | 0.24791 | 353.7785 | 0.12437 | 0 | 0 | 0.24873 | 354.063 | 0.12498 | 0 | 0 | 0.24997 | 354.3475 | 0.1256 | 0 | 0 | 0.2512 | 354.5371 | 0.12601 | 0 | 0 | 0.25203 | 354.8216 | 0.12663 | 0 | 0 | 0.25326 | 355.106 | 0.12725 | 0 | 0 | 0.25449 | 355.2009 | 0.12745 | 0 | 0 | 0.2549 | 355.4853 | 0.12807 | 0 | 0 | 0.25614 | 355.7698 | 0.12869 | 0 | 0 | 0.25737 | 355.9594 | 0.1291 | 0 | 0 | 0.2582 | 356.2439 | 0.12971 | 0 | 0 | 0.25943 | 356.4335 | 0.13013 | 0 | 0 | 0.26025 | 356.6232 | 0.13054 | 0 | 0 | 0.26107
2017-12-10 21:00 | 326.0124 | 0.97171 |  | 342.3341 | 0.099544 | 0 | 0 | 0.19909 | 351.954 | 0.12041 | 0 | 0 | 0.24082 | 359.8249 | 0.13748 | 0 | 0 | 0.27496 | 360.1164 | 0.13811 | 0 | 0 | 0.27623 | 360.3107 | 0.13854 | 0 | 0 | 0.27707 | 360.6023 | 0.13917 | 0 | 0 | 0.27834 | 360.8938 | 0.1398 | 0 | 0 | 0.2796 | 361.1853 | 0.14043 | 0 | 0 | 0.28087 | 361.574 | 0.14128 | 0 | 0 | 0.28255 | 361.8655 | 0.14191 | 0 | 0 | 0.28382 | 362.0598 | 0.14233 | 0 | 0 | 0.28466 | 362.3513 | 0.14296 | 0 | 0 | 0.28592 | 362.5457 | 0.14338 | 0 | 0 | 0.28677 | 362.8372 | 0.14402 | 0 | 0 | 0.28803 | 363.1287 | 0.14465 | 0 | 0 | 0.2893 | 363.323 | 0.14507 | 0 | 0 | 0.29014 | 363.6146 | 0.1457 | 0 | 0 | 0.2914 | 363.9061 | 0.14633 | 0 | 0 | 0.29267 | 364.0032 | 0.14654 | 0 | 0 | 0.29309 | 364.2948 | 0.14718 | 0 | 0 | 0.29435 | 364.5863 | 0.14781 | 0.012136 | 0 | 0.30775 | 364.7806 | 0.14823 | 0.024797 | 0 | 0.32126 | 365.0721 | 0.14886 | 0.043789 | 0 | 0.34152 | 365.2665 | 0.14928 | 0.05645 | 0 | 0.35502 | 365.4608 | 0.14971 | 0.069112 | 0 | 0.36852
2017-12-10 22:00 | 281.8979 | 0.84022 |  | 296.0111 | 0 | 0 | 0 | 0 | 304.3293 | 0.017112 | 0 | 0 | 0.034224 | 311.1351 | 0.031874 | 0 | 0 | 0.063747 | 311.3872 | 0.03242 | 0 | 0 | 0.064841 | 311.5552 | 0.032785 | 0 | 0 | 0.06557 | 311.8073 | 0.033332 | 0 | 0 | 0.066663 | 312.0594 | 0.033878 | 0 | 0 | 0.067757 | 312.3114 | 0.034425 | 0 | 0 | 0.06885 | 312.6475 | 0.035154 | 0 | 0 | 0.070308 | 312.8996 | 0.035701 | 0 | 0 | 0.071402 | 313.0676 | 0.036065 | 0 | 0 | 0.072131 | 313.3197 | 0.036612 | 0 | 0 | 0.073224 | 313.4877 | 0.036977 | 0 | 0 | 0.073953 | 313.7398 | 0.037523 | 0 | 0 | 0.075047 | 313.9919 | 0.03807 | 0 | 0 | 0.07614 | 314.1599 | 0.038435 | 0 | 0 | 0.076869 | 314.412 | 0.038981 | 0 | 0 | 0.077963 | 314.6641 | 0.039528 | 0 | 0 | 0.079056 | 314.7481 | 0.03971 | 0 | 0 | 0.07942 | 315.0001 | 0.040257 | 0 | 0 | 0.080514 | 315.2522 | 0.040804 | 0 | 0 | 0.081607 | 315.4203 | 0.041168 | 0 | 0 | 0.082336 | 315.6723 | 0.041715 | 0 | 0 | 0.08343 | 315.8404 | 0.042079 | 0 | 0 | 0.084159 | 316.0084 | 0.042444 | 0 | 0 | 0.084888
2017-12-10 23:00 | 284.4419 | 0.84781 |  | 298.6824 | 0.0048637 | 0 | 0 | 0.0097274 | 307.0757 | 0.023069 | 0 | 0 | 0.046137 | 313.9429 | 0.037964 | 0 | 0 | 0.075928 | 314.1972 | 0.038515 | 0 | 0 | 0.077031 | 314.3668 | 0.038883 | 0 | 0 | 0.077766 | 314.6211 | 0.039435 | 0 | 0 | 0.07887 | 314.8755 | 0.039987 | 0 | 0 | 0.079973 | 315.1298 | 0.040538 | 0 | 0 | 0.081076 | 315.4689 | 0.041274 | 0 | 0 | 0.082548 | 315.7233 | 0.041825 | 0 | 0 | 0.083651 | 315.8929 | 0.042193 | 0 | 0 | 0.084386 | 316.1472 | 0.042745 | 0 | 0 | 0.08549 | 316.3168 | 0.043113 | 0 | 0 | 0.086225 | 316.5711 | 0.043664 | 0 | 0 | 0.087329 | 316.8254 | 0.044216 | 0 | 0 | 0.088432 | 316.995 | 0.044584 | 0 | 0 | 0.089168 | 317.2493 | 0.045135 | 0 | 0 | 0.090271 | 317.5037 | 0.045687 | 0 | 0 | 0.091374 | 317.5885 | 0.045871 | 0 | 0 | 0.091742 | 317.8428 | 0.046423 | 0 | 0 | 0.092845 | 318.0971 | 0.046974 | 0 | 0 | 0.093949 | 318.2667 | 0.047342 | 0 | 0 | 0.094684 | 318.5211 | 0.047894 | 0 | 0 | 0.095788 | 318.6906 | 0.048262 | 0 | 0 | 0.096523 | 318.8602 | 0.048629 | 0 | 0 | 0.097259
2017-12-11 | 309.916 | 0.92373 |  | 325.4318 | 0.062883 | 0 | 0 | 0.12577 | 334.5768 | 0.082719 | 0 | 0 | 0.16544 | 342.0591 | 0.098948 | 0 | 0 | 0.1979 | 342.3362 | 0.099549 | 0 | 0 | 0.1991 | 342.5209 | 0.09995 | 0 | 0 | 0.1999 | 342.7981 | 0.10055 | 0 | 0 | 0.2011 | 343.0752 | 0.10115 | 0 | 0 | 0.2023 | 343.3523 | 0.10175 | 0 | 0 | 0.20351 | 343.7218 | 0.10255 | 0 | 0 | 0.20511 | 343.9989 | 0.10316 | 0 | 0 | 0.20631 | 344.1837 | 0.10356 | 0 | 0 | 0.20711 | 344.4608 | 0.10416 | 0 | 0 | 0.20831 | 344.6455 | 0.10456 | 0 | 0 | 0.20912 | 344.9226 | 0.10516 | 0 | 0 | 0.21032 | 345.1998 | 0.10576 | 0 | 0 | 0.21152 | 345.3845 | 0.10616 | 0 | 0 | 0.21232 | 345.6616 | 0.10676 | 0 | 0 | 0.21352 | 345.9388 | 0.10736 | 0 | 0 | 0.21473 | 346.0311 | 0.10756 | 0 | 0 | 0.21513 | 346.3082 | 0.10816 | 0 | 0 | 0.21633 | 346.5854 | 0.10877 | 0 | 0 | 0.21753 | 346.7701 | 0.10917 | 0 | 0 | 0.21833 | 347.0472 | 0.10977 | 0 | 0 | 0.21953 | 347.232 | 0.11017 | 0 | 0 | 0.22034 | 347.4167 | 0.11057 | 0 | 0 | 0.22114
2017-12-11 01:00 | 317.4888 | 0.94631 |  | 333.3838 | 0.080131 | 0 | 0 | 0.16026 | 342.7522 | 0.10045 | 0 | 0 | 0.2009 | 350.4173 | 0.11708 | 0 | 0 | 0.23415 | 350.7012 | 0.11769 | 0 | 0 | 0.23539 | 350.8905 | 0.1181 | 0 | 0 | 0.23621 | 351.1744 | 0.11872 | 0 | 0 | 0.23744 | 351.4582 | 0.11933 | 0 | 0 | 0.23867 | 351.7421 | 0.11995 | 0 | 0 | 0.2399 | 352.1207 | 0.12077 | 0 | 0 | 0.24154 | 352.4046 | 0.12139 | 0 | 0 | 0.24277 | 352.5938 | 0.1218 | 0 | 0 | 0.2436 | 352.8777 | 0.12241 | 0 | 0 | 0.24483 | 353.067 | 0.12282 | 0 | 0 | 0.24565 | 353.3509 | 0.12344 | 0 | 0 | 0.24688 | 353.6347 | 0.12406 | 0 | 0 | 0.24811 | 353.824 | 0.12447 | 0 | 0 | 0.24893 | 354.1079 | 0.12508 | 0 | 0 | 0.25016 | 354.3918 | 0.1257 | 0 | 0 | 0.25139 | 354.4864 | 0.1259 | 0 | 0 | 0.25181 | 354.7703 | 0.12652 | 0 | 0 | 0.25304 | 355.0542 | 0.12713 | 0 | 0 | 0.25427 | 355.2435 | 0.12754 | 0 | 0 | 0.25509 | 355.5274 | 0.12816 | 0 | 0 | 0.25632 | 355.7166 | 0.12857 | 0 | 0 | 0.25714 | 355.9059 | 0.12898 | 0 | 0 | 0.25796
2017-12-11 02:00 | 316.1036 | 0.94218 |  | 331.9293 | 0.076976 | 0 | 0 | 0.15395 | 341.2568 | 0.097208 | 0 | 0 | 0.19442 | 348.8885 | 0.11376 | 0 | 0 | 0.22752 | 349.1711 | 0.11437 | 0 | 0 | 0.22875 | 349.3596 | 0.11478 | 0 | 0 | 0.22957 | 349.6422 | 0.1154 | 0 | 0 | 0.23079 | 349.9249 | 0.11601 | 0 | 0 | 0.23202 | 350.2075 | 0.11662 | 0 | 0 | 0.23324 | 350.5844 | 0.11744 | 0 | 0 | 0.23488 | 350.8671 | 0.11805 | 0 | 0 | 0.2361 | 351.0555 | 0.11846 | 0 | 0 | 0.23692 | 351.3382 | 0.11907 | 0 | 0 | 0.23815 | 351.5266 | 0.11948 | 0 | 0 | 0.23897 | 351.8092 | 0.1201 | 0 | 0 | 0.24019 | 352.0919 | 0.12071 | 0 | 0 | 0.24142 | 352.2803 | 0.12112 | 0 | 0 | 0.24224 | 352.563 | 0.12173 | 0 | 0 | 0.24346 | 352.8456 | 0.12234 | 0 | 0 | 0.24469 | 352.9399 | 0.12255 | 0 | 0 | 0.2451 | 353.2225 | 0.12316 | 0 | 0 | 0.24632 | 353.5052 | 0.12377 | 0 | 0 | 0.24755 | 353.6936 | 0.12418 | 0 | 0 | 0.24837 | 353.9763 | 0.1248 | 0 | 0 | 0.24959 | 354.1647 | 0.1252 | 0 | 0 | 0.25041 | 354.3531 | 0.12561 | 0 | 0 | 0.25123
2017-12-11 03:00 | 316.3478 | 0.94291 |  | 332.1857 | 0.077532 | 0 | 0 | 0.15506 | 341.5204 | 0.097779 | 0 | 0 | 0.19556 | 349.158 | 0.11435 | 0 | 0 | 0.22869 | 349.4408 | 0.11496 | 0 | 0 | 0.22992 | 349.6294 | 0.11537 | 0 | 0 | 0.23074 | 349.9123 | 0.11598 | 0 | 0 | 0.23196 | 350.1952 | 0.11659 | 0 | 0 | 0.23319 | 350.478 | 0.11721 | 0 | 0 | 0.23442 | 350.8552 | 0.11803 | 0 | 0 | 0.23605 | 351.1381 | 0.11864 | 0 | 0 | 0.23728 | 351.3266 | 0.11905 | 0 | 0 | 0.2381 | 351.6095 | 0.11966 | 0 | 0 | 0.23933 | 351.7981 | 0.12007 | 0 | 0 | 0.24014 | 352.081 | 0.12069 | 0 | 0 | 0.24137 | 352.3638 | 0.1213 | 0 | 0 | 0.2426 | 352.5524 | 0.12171 | 0 | 0 | 0.24342 | 352.8353 | 0.12232 | 0 | 0 | 0.24464 | 353.1182 | 0.12293 | 0 | 0 | 0.24587 | 353.2125 | 0.12314 | 0 | 0 | 0.24628 | 353.4953 | 0.12375 | 0 | 0 | 0.24751 | 353.7782 | 0.12437 | 0 | 0 | 0.24873 | 353.9668 | 0.12478 | 0 | 0 | 0.24955 | 354.2497 | 0.12539 | 0 | 0 | 0.25078 | 354.4382 | 0.1258 | 0 | 0 | 0.2516 | 354.6268 | 0.12621 | 0 | 0 | 0.25241
2017-12-11 04:00 | 316.0514 | 0.94202 |  | 331.8744 | 0.076857 | 0 | 0 | 0.15371 | 341.2004 | 0.097085 | 0 | 0 | 0.19417 | 348.8308 | 0.11364 | 0 | 0 | 0.22727 | 349.1134 | 0.11425 | 0 | 0 | 0.2285 | 349.3018 | 0.11466 | 0 | 0 | 0.22931 | 349.5844 | 0.11527 | 0 | 0 | 0.23054 | 349.867 | 0.11588 | 0 | 0 | 0.23177 | 350.1496 | 0.1165 | 0 | 0 | 0.23299 | 350.5265 | 0.11731 | 0 | 0 | 0.23463 | 350.8091 | 0.11793 | 0 | 0 | 0.23585 | 350.9975 | 0.11834 | 0 | 0 | 0.23667 | 351.2801 | 0.11895 | 0 | 0 | 0.2379 | 351.4685 | 0.11936 | 0 | 0 | 0.23871 | 351.7511 | 0.11997 | 0 | 0 | 0.23994 | 352.0337 | 0.12058 | 0 | 0 | 0.24117 | 352.2221 | 0.12099 | 0 | 0 | 0.24198 | 352.5047 | 0.1216 | 0 | 0 | 0.24321 | 352.7873 | 0.12222 | 0 | 0 | 0.24443 | 352.8815 | 0.12242 | 0 | 0 | 0.24484 | 353.1641 | 0.12303 | 0 | 0 | 0.24607 | 353.4467 | 0.12365 | 0 | 0 | 0.2473 | 353.6351 | 0.12406 | 0 | 0 | 0.24811 | 353.9177 | 0.12467 | 0 | 0 | 0.24934 | 354.1061 | 0.12508 | 0 | 0 | 0.25016 | 354.2945 | 0.12549 | 0 | 0 | 0.25097
2017-12-11 05:00 | 319.5582 | 0.95247 |  | 335.5568 | 0.084844 | 0 | 0 | 0.16969 | 344.9863 | 0.1053 | 0 | 0 | 0.21059 | 352.7014 | 0.12203 | 0 | 0 | 0.24406 | 352.9871 | 0.12265 | 0 | 0 | 0.2453 | 353.1776 | 0.12306 | 0 | 0 | 0.24613 | 353.4634 | 0.12368 | 0 | 0 | 0.24737 | 353.7491 | 0.1243 | 0 | 0 | 0.24861 | 354.0348 | 0.12492 | 0 | 0 | 0.24985 | 354.4158 | 0.12575 | 0 | 0 | 0.2515 | 354.7016 | 0.12637 | 0 | 0 | 0.25274 | 354.8921 | 0.12678 | 0 | 0 | 0.25357 | 355.1778 | 0.1274 | 0 | 0 | 0.2548 | 355.3683 | 0.12782 | 0 | 0 | 0.25563 | 355.6541 | 0.12844 | 0 | 0 | 0.25687 | 355.9398 | 0.12906 | 0 | 0 | 0.25811 | 356.1303 | 0.12947 | 0 | 0 | 0.25894 | 356.416 | 0.13009 | 0 | 0 | 0.26018 | 356.7018 | 0.13071 | 0 | 0 | 0.26142 | 356.797 | 0.13091 | 0 | 0 | 0.26183 | 357.0828 | 0.13153 | 0 | 0 | 0.26307 | 357.3685 | 0.13215 | 0 | 0 | 0.26431 | 357.559 | 0.13257 | 0 | 0 | 0.26513 | 357.8447 | 0.13319 | 0 | 0 | 0.26637 | 358.0352 | 0.1336 | 0 | 0 | 0.2672 | 358.2257 | 0.13401 | 0 | 0 | 0.26803
2017-12-11 06:00 | 318.7575 | 0.95009 |  | 334.716 | 0.083021 | 0 | 0 | 0.16604 | 344.1218 | 0.10342 | 0 | 0 | 0.20684 | 351.8175 | 0.12011 | 0 | 0 | 0.24023 | 352.1026 | 0.12073 | 0 | 0 | 0.24146 | 352.2926 | 0.12114 | 0 | 0 | 0.24229 | 352.5776 | 0.12176 | 0 | 0 | 0.24352 | 352.8626 | 0.12238 | 0 | 0 | 0.24476 | 353.1477 | 0.123 | 0 | 0 | 0.246 | 353.5277 | 0.12382 | 0 | 0 | 0.24765 | 353.8127 | 0.12444 | 0 | 0 | 0.24888 | 354.0028 | 0.12485 | 0 | 0 | 0.24971 | 354.2878 | 0.12547 | 0 | 0 | 0.25094 | 354.4778 | 0.12588 | 0 | 0 | 0.25177 | 354.7628 | 0.1265 | 0 | 0 | 0.253 | 355.0478 | 0.12712 | 0 | 0 | 0.25424 | 355.2379 | 0.12753 | 0 | 0 | 0.25507 | 355.5229 | 0.12815 | 0 | 0 | 0.2563 | 355.8079 | 0.12877 | 0 | 0 | 0.25754 | 355.9029 | 0.12898 | 0 | 0 | 0.25795 | 356.188 | 0.12959 | 0 | 0 | 0.25919 | 356.473 | 0.13021 | 0 | 0 | 0.26042 | 356.663 | 0.13062 | 0 | 0 | 0.26125 | 356.948 | 0.13124 | 0 | 0 | 0.26248 | 357.138 | 0.13165 | 0 | 0 | 0.26331 | 357.3281 | 0.13207 | 0 | 0 | 0.26413
2017-12-11 07:00 | 322.523 | 0.96131 |  | 338.67 | 0.091597 | 0 | 0 | 0.18319 | 348.187 | 0.11224 | 0 | 0 | 0.22448 | 355.9736 | 0.12913 | 0 | 0 | 0.25826 | 356.262 | 0.12975 | 0 | 0 | 0.25951 | 356.4543 | 0.13017 | 0 | 0 | 0.26034 | 356.7427 | 0.1308 | 0 | 0 | 0.26159 | 357.0311 | 0.13142 | 0 | 0 | 0.26284 | 357.3195 | 0.13205 | 0 | 0 | 0.2641 | 357.704 | 0.13288 | 0 | 0 | 0.26576 | 357.9924 | 0.13351 | 0 | 0 | 0.26701 | 358.1847 | 0.13392 | 0 | 0 | 0.26785 | 358.473 | 0.13455 | 0 | 0 | 0.2691 | 358.6653 | 0.13497 | 0 | 0 | 0.26993 | 358.9537 | 0.13559 | 0 | 0 | 0.27118 | 359.2421 | 0.13622 | 0 | 0 | 0.27244 | 359.4344 | 0.13663 | 0 | 0 | 0.27327 | 359.7227 | 0.13726 | 0 | 0 | 0.27452 | 360.0111 | 0.13789 | 0 | 0 | 0.27577 | 360.1073 | 0.13809 | 0 | 0 | 0.27619 | 360.3957 | 0.13872 | 0 | 0 | 0.27744 | 360.6841 | 0.13935 | 0 | 0 | 0.27869 | 360.8763 | 0.13976 | 0 | 0 | 0.27952 | 361.1647 | 0.14039 | 0 | 0 | 0.28078 | 361.357 | 0.1408 | 0 | 0 | 0.28161 | 361.5492 | 0.14122 | 0 | 0 | 0.28244
2017-12-11 08:00 | 316.4174 | 0.94311 |  | 332.2588 | 0.077691 | 0 | 0 | 0.15538 | 341.5956 | 0.097942 | 0 | 0 | 0.19588 | 349.2348 | 0.11451 | 0 | 0 | 0.22902 | 349.5177 | 0.11513 | 0 | 0 | 0.23025 | 349.7063 | 0.11553 | 0 | 0 | 0.23107 | 349.9893 | 0.11615 | 0 | 0 | 0.2323 | 350.2722 | 0.11676 | 0 | 0 | 0.23352 | 350.5551 | 0.11738 | 0 | 0 | 0.23475 | 350.9324 | 0.11819 | 0 | 0 | 0.23639 | 351.2153 | 0.11881 | 0 | 0 | 0.23762 | 351.404 | 0.11922 | 0 | 0 | 0.23843 | 351.6869 | 0.11983 | 0 | 0 | 0.23966 | 351.8755 | 0.12024 | 0 | 0 | 0.24048 | 352.1584 | 0.12085 | 0 | 0 | 0.24171 | 352.4414 | 0.12147 | 0 | 0 | 0.24293 | 352.63 | 0.12188 | 0 | 0 | 0.24375 | 352.9129 | 0.12249 | 0 | 0 | 0.24498 | 353.1959 | 0.1231 | 0 | 0 | 0.24621 | 353.2902 | 0.12331 | 0 | 0 | 0.24662 | 353.5731 | 0.12392 | 0 | 0 | 0.24784 | 353.856 | 0.12454 | 0 | 0 | 0.24907 | 354.0447 | 0.12494 | 0 | 0 | 0.24989 | 354.3276 | 0.12556 | 0 | 0 | 0.25112 | 354.5162 | 0.12597 | 0 | 0 | 0.25193 | 354.7048 | 0.12638 | 0 | 0 | 0.25275
2017-12-11 09:00 | 321.1196 | 0.95713 |  | 337.1964 | 0.088401 | 0 | 0 | 0.1768 | 346.6719 | 0.10895 | 0 | 0 | 0.21791 | 354.4247 | 0.12577 | 0 | 0 | 0.25154 | 354.7118 | 0.12639 | 0 | 0 | 0.25278 | 354.9032 | 0.12681 | 0 | 0 | 0.25361 | 355.1904 | 0.12743 | 0 | 0 | 0.25486 | 355.4775 | 0.12805 | 0 | 0 | 0.2561 | 355.7646 | 0.12868 | 0 | 0 | 0.25735 | 356.1475 | 0.12951 | 0 | 0 | 0.25901 | 356.4346 | 0.13013 | 0 | 0 | 0.26026 | 356.6261 | 0.13054 | 0 | 0 | 0.26109 | 356.9132 | 0.13117 | 0 | 0 | 0.26233 | 357.1046 | 0.13158 | 0 | 0 | 0.26316 | 357.3918 | 0.1322 | 0 | 0 | 0.26441 | 357.6789 | 0.13283 | 0 | 0 | 0.26565 | 357.8703 | 0.13324 | 0 | 0 | 0.26648 | 358.1575 | 0.13387 | 0 | 0 | 0.26773 | 358.4446 | 0.13449 | 0 | 0 | 0.26898 | 358.5403 | 0.1347 | 0 | 0 | 0.26939 | 358.8275 | 0.13532 | 0 | 0 | 0.27064 | 359.1146 | 0.13594 | 0 | 0 | 0.27188 | 359.306 | 0.13636 | 0 | 0 | 0.27271 | 359.5932 | 0.13698 | 0 | 0 | 0.27396 | 359.7846 | 0.13739 | 0 | 0 | 0.27479 | 359.976 | 0.13781 | 0 | 0 | 0.27562
2017-12-11 10:00 | 313.8496 | 0.93546 |  | 329.5624 | 0.071843 | 0 | 0 | 0.14369 | 338.8235 | 0.09193 | 0 | 0 | 0.18386 | 346.4007 | 0.10836 | 0 | 0 | 0.21673 | 346.6813 | 0.10897 | 0 | 0 | 0.21795 | 346.8684 | 0.10938 | 0 | 0 | 0.21876 | 347.1491 | 0.10999 | 0 | 0 | 0.21998 | 347.4297 | 0.1106 | 0 | 0 | 0.22119 | 347.7103 | 0.11121 | 0 | 0 | 0.22241 | 348.0845 | 0.11202 | 0 | 0 | 0.22403 | 348.3652 | 0.11263 | 0 | 0 | 0.22525 | 348.5522 | 0.11303 | 0 | 0 | 0.22606 | 348.8329 | 0.11364 | 0 | 0 | 0.22728 | 349.02 | 0.11405 | 0 | 0 | 0.22809 | 349.3006 | 0.11465 | 0 | 0 | 0.22931 | 349.5813 | 0.11526 | 0 | 0 | 0.23053 | 349.7683 | 0.11567 | 0 | 0 | 0.23134 | 350.049 | 0.11628 | 0 | 0 | 0.23256 | 350.3296 | 0.11689 | 0 | 0 | 0.23377 | 350.4232 | 0.11709 | 0 | 0 | 0.23418 | 350.7038 | 0.1177 | 0 | 0 | 0.2354 | 350.9844 | 0.11831 | 0 | 0 | 0.23661 | 351.1715 | 0.11871 | 0 | 0 | 0.23743 | 351.4522 | 0.11932 | 0 | 0 | 0.23864 | 351.6393 | 0.11973 | 0 | 0 | 0.23945 | 351.8264 | 0.12013 | 0 | 0 | 0.24027
2017-12-11 11:00 | 305.79 | 0.91144 |  | 321.0993 | 0.053486 | 0 | 0 | 0.10697 | 330.1225 | 0.073057 | 0 | 0 | 0.14611 | 337.5051 | 0.08907 | 0 | 0 | 0.17814 | 337.7786 | 0.089663 | 0 | 0 | 0.17933 | 337.9608 | 0.090059 | 0 | 0 | 0.18012 | 338.2343 | 0.090652 | 0 | 0 | 0.1813 | 338.5077 | 0.091245 | 0 | 0 | 0.18249 | 338.7811 | 0.091838 | 0 | 0 | 0.18368 | 339.1457 | 0.092629 | 0 | 0 | 0.18526 | 339.4191 | 0.093222 | 0 | 0 | 0.18644 | 339.6014 | 0.093617 | 0 | 0 | 0.18723 | 339.8749 | 0.09421 | 0 | 0 | 0.18842 | 340.0572 | 0.094606 | 0 | 0 | 0.18921 | 340.3306 | 0.095199 | 0 | 0 | 0.1904 | 340.604 | 0.095792 | 0 | 0 | 0.19158 | 340.7863 | 0.096187 | 0 | 0 | 0.19237 | 341.0597 | 0.09678 | 0 | 0 | 0.19356 | 341.3332 | 0.097373 | 0 | 0 | 0.19475 | 341.4243 | 0.097571 | 0 | 0 | 0.19514 | 341.6977 | 0.098164 | 0 | 0 | 0.19633 | 341.9712 | 0.098757 | 0 | 0 | 0.19751 | 342.1535 | 0.099152 | 0 | 0 | 0.1983 | 342.4269 | 0.099746 | 0 | 0 | 0.19949 | 342.6092 | 0.10014 | 0 | 0 | 0.20028 | 342.7915 | 0.10054 | 0 | 0 | 0.20107
2017-12-11 12:00 | 301.7653 | 0.89944 |  | 316.8731 | 0.044319 | 0 | 0 | 0.088639 | 325.7776 | 0.063633 | 0 | 0 | 0.12727 | 333.063 | 0.079435 | 0 | 0 | 0.15887 | 333.3329 | 0.080021 | 0 | 0 | 0.16004 | 333.5128 | 0.080411 | 0 | 0 | 0.16082 | 333.7826 | 0.080996 | 0 | 0 | 0.16199 | 334.0524 | 0.081581 | 0 | 0 | 0.16316 | 334.3223 | 0.082167 | 0 | 0 | 0.16433 | 334.682 | 0.082947 | 0 | 0 | 0.16589 | 334.9519 | 0.083532 | 0 | 0 | 0.16706 | 335.1318 | 0.083922 | 0 | 0 | 0.16784 | 335.4016 | 0.084508 | 0 | 0 | 0.16902 | 335.5815 | 0.084898 | 0 | 0 | 0.1698 | 335.8513 | 0.085483 | 0 | 0 | 0.17097 | 336.1211 | 0.086068 | 0 | 0 | 0.17214 | 336.301 | 0.086459 | 0 | 0 | 0.17292 | 336.5709 | 0.087044 | 0 | 0 | 0.17409 | 336.8407 | 0.087629 | 0 | 0 | 0.17526 | 336.9306 | 0.087824 | 0 | 0 | 0.17565 | 337.2005 | 0.088409 | 0 | 0 | 0.17682 | 337.4703 | 0.088995 | 0 | 0 | 0.17799 | 337.6502 | 0.089385 | 0 | 0 | 0.17877 | 337.92 | 0.08997 | 0 | 0 | 0.17994 | 338.0999 | 0.09036 | 0 | 0 | 0.18072 | 338.2798 | 0.090751 | 0 | 0 | 0.1815
2017-12-11 13:00 | 309.0516 | 0.92116 |  | 324.5242 | 0.060915 | 0 | 0 | 0.12183 | 333.6437 | 0.080695 | 0 | 0 | 0.16139 | 341.1051 | 0.096878 | 0 | 0 | 0.19376 | 341.3814 | 0.097478 | 0 | 0 | 0.19496 | 341.5656 | 0.097877 | 0 | 0 | 0.19575 | 341.842 | 0.098477 | 0 | 0 | 0.19695 | 342.1183 | 0.099076 | 0 | 0 | 0.19815 | 342.3947 | 0.099676 | 0 | 0 | 0.19935 | 342.7631 | 0.10047 | 0 | 0 | 0.20095 | 343.0395 | 0.10107 | 0 | 0 | 0.20215 | 343.2237 | 0.10147 | 0 | 0 | 0.20295 | 343.5001 | 0.10207 | 0 | 0 | 0.20415 | 343.6843 | 0.10247 | 0 | 0 | 0.20495 | 343.9606 | 0.10307 | 0 | 0 | 0.20614 | 344.237 | 0.10367 | 0 | 0 | 0.20734 | 344.4212 | 0.10407 | 0 | 0 | 0.20814 | 344.6976 | 0.10467 | 0 | 0 | 0.20934 | 344.9739 | 0.10527 | 0 | 0 | 0.21054 | 345.066 | 0.10547 | 0 | 0 | 0.21094 | 345.3424 | 0.10607 | 0 | 0 | 0.21214 | 345.6187 | 0.10667 | 0 | 0 | 0.21334 | 345.803 | 0.10707 | 0 | 0 | 0.21414 | 346.0793 | 0.10767 | 0 | 0 | 0.21534 | 346.2635 | 0.10807 | 0 | 0 | 0.21613 | 346.4478 | 0.10847 | 0 | 0 | 0.21693
2017-12-11 14:00 | 314.4791 | 0.93734 |  | 330.2234 | 0.073276 | 0 | 0 | 0.14655 | 339.5031 | 0.093404 | 0 | 0 | 0.18681 | 347.0955 | 0.10987 | 0 | 0 | 0.21974 | 347.3767 | 0.11048 | 0 | 0 | 0.22096 | 347.5642 | 0.11089 | 0 | 0 | 0.22178 | 347.8454 | 0.1115 | 0 | 0 | 0.223 | 348.1266 | 0.11211 | 0 | 0 | 0.22422 | 348.4078 | 0.11272 | 0 | 0 | 0.22544 | 348.7827 | 0.11353 | 0 | 0 | 0.22706 | 349.0639 | 0.11414 | 0 | 0 | 0.22828 | 349.2514 | 0.11455 | 0 | 0 | 0.2291 | 349.5326 | 0.11516 | 0 | 0 | 0.23032 | 349.72 | 0.11556 | 0 | 0 | 0.23113 | 350.0012 | 0.11617 | 0 | 0 | 0.23235 | 350.2824 | 0.11678 | 0 | 0 | 0.23357 | 350.4699 | 0.11719 | 0 | 0 | 0.23438 | 350.7511 | 0.1178 | 0 | 0 | 0.2356 | 351.0323 | 0.11841 | 0 | 0 | 0.23682 | 351.126 | 0.11861 | 0 | 0 | 0.23723 | 351.4072 | 0.11922 | 0 | 0 | 0.23845 | 351.6884 | 0.11983 | 0 | 0 | 0.23967 | 351.8759 | 0.12024 | 0 | 0 | 0.24048 | 352.1571 | 0.12085 | 0 | 0 | 0.2417 | 352.3446 | 0.12126 | 0 | 0 | 0.24251 | 352.532 | 0.12166 | 0 | 0 | 0.24333
2017-12-11 15:00 | 309.5424 | 0.92262 |  | 325.0396 | 0.062032 | 0 | 0 | 0.12406 | 334.1735 | 0.081844 | 0 | 0 | 0.16369 | 341.6468 | 0.098053 | 0 | 0 | 0.19611 | 341.9235 | 0.098654 | 0 | 0 | 0.19731 | 342.1081 | 0.099054 | 0 | 0 | 0.19811 | 342.3849 | 0.099654 | 0 | 0 | 0.19931 | 342.6616 | 0.10025 | 0 | 0 | 0.20051 | 342.9384 | 0.10086 | 0 | 0 | 0.20171 | 343.3075 | 0.10166 | 0 | 0 | 0.20331 | 343.5843 | 0.10226 | 0 | 0 | 0.20451 | 343.7688 | 0.10266 | 0 | 0 | 0.20531 | 344.0456 | 0.10326 | 0 | 0 | 0.20651 | 344.2301 | 0.10366 | 0 | 0 | 0.20731 | 344.5069 | 0.10426 | 0 | 0 | 0.20851 | 344.7837 | 0.10486 | 0 | 0 | 0.20971 | 344.9682 | 0.10526 | 0 | 0 | 0.21052 | 345.245 | 0.10586 | 0 | 0 | 0.21172 | 345.5218 | 0.10646 | 0 | 0 | 0.21292 | 345.614 | 0.10666 | 0 | 0 | 0.21332 | 345.8908 | 0.10726 | 0 | 0 | 0.21452 | 346.1676 | 0.10786 | 0 | 0 | 0.21572 | 346.3521 | 0.10826 | 0 | 0 | 0.21652 | 346.6289 | 0.10886 | 0 | 0 | 0.21772 | 346.8134 | 0.10926 | 0 | 0 | 0.21852 | 346.998 | 0.10966 | 0 | 0 | 0.21932
2017-12-11 16:00 | 322.0981 | 0.96005 |  | 338.2239 | 0.090629 | 0 | 0 | 0.18126 | 347.7283 | 0.11124 | 0 | 0 | 0.22249 | 355.5047 | 0.12811 | 0 | 0 | 0.25622 | 355.7927 | 0.12874 | 0 | 0 | 0.25747 | 355.9847 | 0.12915 | 0 | 0 | 0.2583 | 356.2727 | 0.12978 | 0 | 0 | 0.25955 | 356.5607 | 0.1304 | 0 | 0 | 0.2608 | 356.8487 | 0.13103 | 0 | 0 | 0.26205 | 357.2328 | 0.13186 | 0 | 0 | 0.26372 | 357.5208 | 0.13248 | 0 | 0 | 0.26497 | 357.7128 | 0.1329 | 0 | 0 | 0.2658 | 358.0008 | 0.13353 | 0 | 0 | 0.26705 | 358.1928 | 0.13394 | 0 | 0 | 0.26788 | 358.4808 | 0.13457 | 0 | 0 | 0.26913 | 358.7688 | 0.13519 | 0 | 0 | 0.27038 | 358.9608 | 0.13561 | 0 | 0 | 0.27122 | 359.2489 | 0.13623 | 0 | 0 | 0.27246 | 359.5369 | 0.13686 | 0 | 0 | 0.27371 | 359.6329 | 0.13707 | 0 | 0 | 0.27413 | 359.9209 | 0.13769 | 0 | 0 | 0.27538 | 360.2089 | 0.13831 | 0 | 0 | 0.27663 | 360.4009 | 0.13873 | 0 | 0 | 0.27746 | 360.6889 | 0.13936 | 0 | 0 | 0.27871 | 360.8809 | 0.13977 | 0 | 0 | 0.27954 | 361.0729 | 0.14019 | 0 | 0 | 0.28038
2017-12-11 17:00 | 317.999 | 0.94783 |  | 333.9195 | 0.081293 | 0 | 0 | 0.16259 | 343.303 | 0.10165 | 0 | 0 | 0.20329 | 350.9804 | 0.1183 | 0 | 0 | 0.2366 | 351.2648 | 0.11891 | 0 | 0 | 0.23783 | 351.4543 | 0.11933 | 0 | 0 | 0.23865 | 351.7387 | 0.11994 | 0 | 0 | 0.23989 | 352.023 | 0.12056 | 0 | 0 | 0.24112 | 352.3074 | 0.12118 | 0 | 0 | 0.24235 | 352.6865 | 0.122 | 0 | 0 | 0.244 | 352.9709 | 0.12262 | 0 | 0 | 0.24523 | 353.1604 | 0.12303 | 0 | 0 | 0.24605 | 353.4448 | 0.12364 | 0 | 0 | 0.24729 | 353.6343 | 0.12405 | 0 | 0 | 0.24811 | 353.9187 | 0.12467 | 0 | 0 | 0.24934 | 354.203 | 0.12529 | 0 | 0 | 0.25058 | 354.3926 | 0.1257 | 0 | 0 | 0.2514 | 354.6769 | 0.12632 | 0 | 0 | 0.25263 | 354.9613 | 0.12693 | 0 | 0 | 0.25387 | 355.0561 | 0.12714 | 0 | 0 | 0.25428 | 355.3404 | 0.12776 | 0 | 0 | 0.25551 | 355.6248 | 0.12837 | 0 | 0 | 0.25674 | 355.8143 | 0.12878 | 0 | 0 | 0.25757 | 356.0987 | 0.1294 | 0 | 0 | 0.2588 | 356.2882 | 0.12981 | 0 | 0 | 0.25962 | 356.4778 | 0.13022 | 0 | 0 | 0.26044
2017-12-11 18:00 | 315.5394 | 0.9405 |  | 331.3368 | 0.075691 | 0 | 0 | 0.15138 | 340.6478 | 0.095887 | 0 | 0 | 0.19177 | 348.2658 | 0.11241 | 0 | 0 | 0.22482 | 348.5479 | 0.11302 | 0 | 0 | 0.22604 | 348.736 | 0.11343 | 0 | 0 | 0.22686 | 349.0182 | 0.11404 | 0 | 0 | 0.22808 | 349.3003 | 0.11465 | 0 | 0 | 0.22931 | 349.5825 | 0.11527 | 0 | 0 | 0.23053 | 349.9587 | 0.11608 | 0 | 0 | 0.23216 | 350.2408 | 0.11669 | 0 | 0 | 0.23339 | 350.4289 | 0.1171 | 0 | 0 | 0.2342 | 350.7111 | 0.11771 | 0 | 0 | 0.23543 | 350.8992 | 0.11812 | 0 | 0 | 0.23624 | 351.1813 | 0.11873 | 0 | 0 | 0.23747 | 351.4635 | 0.11935 | 0 | 0 | 0.23869 | 351.6516 | 0.11975 | 0 | 0 | 0.23951 | 351.9337 | 0.12037 | 0 | 0 | 0.24073 | 352.2159 | 0.12098 | 0 | 0 | 0.24196 | 352.3099 | 0.12118 | 0 | 0 | 0.24236 | 352.5921 | 0.12179 | 0 | 0 | 0.24359 | 352.8742 | 0.12241 | 0 | 0 | 0.24481 | 353.0623 | 0.12281 | 0 | 0 | 0.24563 | 353.3445 | 0.12343 | 0 | 0 | 0.24685 | 353.5326 | 0.12383 | 0 | 0 | 0.24767 | 353.7207 | 0.12424 | 0 | 0 | 0.24848
2017-12-11 19:00 | 316.9838 | 0.9448 |  | 332.8535 | 0.078981 | 0 | 0 | 0.15796 | 342.207 | 0.099269 | 0 | 0 | 0.19854 | 349.8599 | 0.11587 | 0 | 0 | 0.23174 | 350.1433 | 0.11648 | 0 | 0 | 0.23297 | 350.3323 | 0.11689 | 0 | 0 | 0.23378 | 350.6157 | 0.11751 | 0 | 0 | 0.23501 | 350.8992 | 0.11812 | 0 | 0 | 0.23624 | 351.1826 | 0.11874 | 0 | 0 | 0.23747 | 351.5605 | 0.11956 | 0 | 0 | 0.23911 | 351.844 | 0.12017 | 0 | 0 | 0.24034 | 352.0329 | 0.12058 | 0 | 0 | 0.24116 | 352.3164 | 0.1212 | 0 | 0 | 0.24239 | 352.5053 | 0.12161 | 0 | 0 | 0.24321 | 352.7888 | 0.12222 | 0 | 0 | 0.24444 | 353.0722 | 0.12284 | 0 | 0 | 0.24567 | 353.2612 | 0.12325 | 0 | 0 | 0.24649 | 353.5446 | 0.12386 | 0 | 0 | 0.24772 | 353.828 | 0.12447 | 0 | 0 | 0.24895 | 353.9225 | 0.12468 | 0 | 0 | 0.24936 | 354.206 | 0.12529 | 0 | 0 | 0.25059 | 354.4894 | 0.12591 | 0 | 0 | 0.25182 | 354.6784 | 0.12632 | 0 | 0 | 0.25264 | 354.9618 | 0.12693 | 0 | 0 | 0.25387 | 355.1508 | 0.12734 | 0 | 0 | 0.25469 | 355.3397 | 0.12775 | 0 | 0 | 0.25551
2017-12-11 20:00 | 308.2797 | 0.91886 |  | 323.7137 | 0.059157 | 0 | 0 | 0.11831 | 332.8104 | 0.078887 | 0 | 0 | 0.15777 | 340.2531 | 0.095031 | 0 | 0 | 0.19006 | 340.5288 | 0.095629 | 0 | 0 | 0.19126 | 340.7126 | 0.096027 | 0 | 0 | 0.19205 | 340.9882 | 0.096625 | 0 | 0 | 0.19325 | 341.2639 | 0.097223 | 0 | 0 | 0.19445 | 341.5395 | 0.097821 | 0 | 0 | 0.19564 | 341.9071 | 0.098618 | 0 | 0 | 0.19724 | 342.1827 | 0.099216 | 0 | 0 | 0.19843 | 342.3665 | 0.099615 | 0 | 0 | 0.19923 | 342.6422 | 0.10021 | 0 | 0 | 0.20042 | 342.8259 | 0.10061 | 0 | 0 | 0.20122 | 343.1016 | 0.10121 | 0 | 0 | 0.20242 | 343.3772 | 0.10181 | 0 | 0 | 0.20361 | 343.561 | 0.10221 | 0 | 0 | 0.20441 | 343.8367 | 0.1028 | 0 | 0 | 0.20561 | 344.1123 | 0.1034 | 0 | 0 | 0.2068 | 344.2042 | 0.1036 | 0 | 0 | 0.2072 | 344.4799 | 0.1042 | 0 | 0 | 0.2084 | 344.7555 | 0.1048 | 0 | 0 | 0.20959 | 344.9393 | 0.1052 | 0 | 0 | 0.21039 | 345.215 | 0.10579 | 0 | 0 | 0.21159 | 345.3987 | 0.10619 | 0 | 0 | 0.21238 | 345.5825 | 0.10659 | 0 | 0 | 0.21318
2017-12-11 21:00 | 305.7889 | 0.91143 |  | 321.0981 | 0.053483 | 0 | 0 | 0.10697 | 330.1213 | 0.073055 | 0 | 0 | 0.14611 | 337.5039 | 0.089068 | 0 | 0 | 0.17814 | 337.7774 | 0.089661 | 0 | 0 | 0.17932 | 337.9596 | 0.090056 | 0 | 0 | 0.18011 | 338.2331 | 0.090649 | 0 | 0 | 0.1813 | 338.5065 | 0.091242 | 0 | 0 | 0.18248 | 338.7799 | 0.091835 | 0 | 0 | 0.18367 | 339.1445 | 0.092626 | 0 | 0 | 0.18525 | 339.4179 | 0.093219 | 0 | 0 | 0.18644 | 339.6002 | 0.093615 | 0 | 0 | 0.18723 | 339.8737 | 0.094208 | 0 | 0 | 0.18842 | 340.0559 | 0.094603 | 0 | 0 | 0.18921 | 340.3294 | 0.095196 | 0 | 0 | 0.19039 | 340.6028 | 0.095789 | 0 | 0 | 0.19158 | 340.7851 | 0.096185 | 0 | 0 | 0.19237 | 341.0585 | 0.096778 | 0 | 0 | 0.19356 | 341.332 | 0.097371 | 0 | 0 | 0.19474 | 341.4231 | 0.097568 | 0 | 0 | 0.19514 | 341.6965 | 0.098161 | 0 | 0 | 0.19632 | 341.97 | 0.098754 | 0 | 0 | 0.19751 | 342.1522 | 0.09915 | 0 | 0 | 0.1983 | 342.4257 | 0.099743 | 0 | 0 | 0.19949 | 342.608 | 0.10014 | 0 | 0 | 0.20028 | 342.7902 | 0.10053 | 0 | 0 | 0.20107
2017-12-11 22:00 | 311.1046 | 0.92728 |  | 326.68 | 0.065591 | 0 | 0 | 0.13118 | 335.86 | 0.085502 | 0 | 0 | 0.171 | 343.371 | 0.10179 | 0 | 0 | 0.20359 | 343.6492 | 0.1024 | 0 | 0 | 0.20479 | 343.8346 | 0.1028 | 0 | 0 | 0.2056 | 344.1128 | 0.1034 | 0 | 0 | 0.2068 | 344.391 | 0.10401 | 0 | 0 | 0.20801 | 344.6692 | 0.10461 | 0 | 0 | 0.20922 | 345.0401 | 0.10541 | 0 | 0 | 0.21083 | 345.3183 | 0.10602 | 0 | 0 | 0.21203 | 345.5037 | 0.10642 | 0 | 0 | 0.21284 | 345.7819 | 0.10702 | 0 | 0 | 0.21405 | 345.9674 | 0.10742 | 0 | 0 | 0.21485 | 346.2455 | 0.10803 | 0 | 0 | 0.21606 | 346.5237 | 0.10863 | 0 | 0 | 0.21726 | 346.7092 | 0.10903 | 0 | 0 | 0.21807 | 346.9874 | 0.10964 | 0 | 0 | 0.21927 | 347.2655 | 0.11024 | 0 | 0 | 0.22048 | 347.3583 | 0.11044 | 0 | 0 | 0.22088 | 347.6365 | 0.11105 | 0 | 0 | 0.22209 | 347.9146 | 0.11165 | 0 | 0 | 0.2233 | 348.1001 | 0.11205 | 0 | 0 | 0.2241 | 348.3783 | 0.11265 | 0 | 0 | 0.22531 | 348.5637 | 0.11306 | 0 | 0 | 0.22611 | 348.7492 | 0.11346 | 0 | 0 | 0.22692
2017-12-11 23:00 | 308.3036 | 0.91893 |  | 323.7387 | 0.059211 | 0 | 0 | 0.11842 | 332.8361 | 0.078943 | 0 | 0 | 0.15789 | 340.2795 | 0.095088 | 0 | 0 | 0.19018 | 340.5551 | 0.095686 | 0 | 0 | 0.19137 | 340.7389 | 0.096084 | 0 | 0 | 0.19217 | 341.0146 | 0.096682 | 0 | 0 | 0.19336 | 341.2903 | 0.09728 | 0 | 0 | 0.19456 | 341.566 | 0.097878 | 0 | 0 | 0.19576 | 341.9335 | 0.098675 | 0 | 0 | 0.19735 | 342.2092 | 0.099273 | 0 | 0 | 0.19855 | 342.393 | 0.099672 | 0 | 0 | 0.19934 | 342.6687 | 0.10027 | 0 | 0 | 0.20054 | 342.8525 | 0.10067 | 0 | 0 | 0.20134 | 343.1281 | 0.10127 | 0 | 0 | 0.20253 | 343.4038 | 0.10186 | 0 | 0 | 0.20373 | 343.5876 | 0.10226 | 0 | 0 | 0.20453 | 343.8633 | 0.10286 | 0 | 0 | 0.20572 | 344.139 | 0.10346 | 0 | 0 | 0.20692 | 344.2309 | 0.10366 | 0 | 0 | 0.20732 | 344.5065 | 0.10426 | 0 | 0 | 0.20851 | 344.7822 | 0.10485 | 0 | 0 | 0.20971 | 344.966 | 0.10525 | 0 | 0 | 0.21051 | 345.2417 | 0.10585 | 0 | 0 | 0.2117 | 345.4255 | 0.10625 | 0 | 0 | 0.2125 | 345.6092 | 0.10665 | 0 | 0 | 0.2133
2017-12-12 | 307.6519 | 0.91699 |  | 323.0544 | 0.057727 | 0 | 0 | 0.11545 | 332.1326 | 0.077417 | 0 | 0 | 0.15483 | 339.5601 | 0.093528 | 0 | 0 | 0.18706 | 339.8352 | 0.094124 | 0 | 0 | 0.18825 | 340.0186 | 0.094522 | 0 | 0 | 0.18904 | 340.2937 | 0.095119 | 0 | 0 | 0.19024 | 340.5688 | 0.095715 | 0 | 0 | 0.19143 | 340.8439 | 0.096312 | 0 | 0 | 0.19262 | 341.2107 | 0.097108 | 0 | 0 | 0.19422 | 341.4858 | 0.097704 | 0 | 0 | 0.19541 | 341.6692 | 0.098102 | 0 | 0 | 0.1962 | 341.9443 | 0.098699 | 0 | 0 | 0.1974 | 342.1277 | 0.099097 | 0 | 0 | 0.19819 | 342.4028 | 0.099693 | 0 | 0 | 0.19939 | 342.6779 | 0.10029 | 0 | 0 | 0.20058 | 342.8613 | 0.10069 | 0 | 0 | 0.20138 | 343.1364 | 0.10128 | 0 | 0 | 0.20257 | 343.4115 | 0.10188 | 0 | 0 | 0.20376 | 343.5032 | 0.10208 | 0 | 0 | 0.20416 | 343.7783 | 0.10268 | 0 | 0 | 0.20535 | 344.0534 | 0.10327 | 0 | 0 | 0.20655 | 344.2368 | 0.10367 | 0 | 0 | 0.20734 | 344.5119 | 0.10427 | 0 | 0 | 0.20854 | 344.6953 | 0.10467 | 0 | 0 | 0.20933 | 344.8787 | 0.10506 | 0 | 0 | 0.21013
2017-12-12 01:00 | 294.3164 | 0.87724 |  | 309.0512 | 0.027354 | 0 | 0 | 0.054708 | 317.7359 | 0.046191 | 0 | 0 | 0.092382 | 324.8415 | 0.061603 | 0 | 0 | 0.12321 | 325.1047 | 0.062174 | 0 | 0 | 0.12435 | 325.2801 | 0.062554 | 0 | 0 | 0.12511 | 325.5433 | 0.063125 | 0 | 0 | 0.12625 | 325.8065 | 0.063696 | 0 | 0 | 0.12739 | 326.0697 | 0.064267 | 0 | 0 | 0.12853 | 326.4206 | 0.065028 | 0 | 0 | 0.13006 | 326.6837 | 0.065599 | 0 | 0 | 0.1312 | 326.8592 | 0.065979 | 0 | 0 | 0.13196 | 327.1223 | 0.06655 | 0 | 0 | 0.1331 | 327.2978 | 0.066931 | 0 | 0 | 0.13386 | 327.561 | 0.067501 | 0 | 0 | 0.135 | 327.8241 | 0.068072 | 0 | 0 | 0.13614 | 327.9996 | 0.068453 | 0 | 0 | 0.13691 | 328.2628 | 0.069024 | 0 | 0 | 0.13805 | 328.5259 | 0.069594 | 0 | 0 | 0.13919 | 328.6137 | 0.069785 | 0 | 0 | 0.13957 | 328.8768 | 0.070355 | 0 | 0 | 0.14071 | 329.14 | 0.070926 | 0 | 0 | 0.14185 | 329.3154 | 0.071307 | 0 | 0 | 0.14261 | 329.5786 | 0.071878 | 0 | 0 | 0.14376 | 329.7541 | 0.072258 | 0 | 0 | 0.14452 | 329.9295 | 0.072639 | 0 | 0 | 0.14528
2017-12-12 02:00 | 311.5062 | 0.92847 |  | 327.1017 | 0.066505 | 0 | 0 | 0.13301 | 336.2936 | 0.086442 | 0 | 0 | 0.17288 | 343.8142 | 0.10275 | 0 | 0 | 0.20551 | 344.0927 | 0.10336 | 0 | 0 | 0.20672 | 344.2784 | 0.10376 | 0 | 0 | 0.20752 | 344.557 | 0.10437 | 0 | 0 | 0.20873 | 344.8355 | 0.10497 | 0 | 0 | 0.20994 | 345.1141 | 0.10557 | 0 | 0 | 0.21115 | 345.4855 | 0.10638 | 0 | 0 | 0.21276 | 345.764 | 0.10698 | 0 | 0 | 0.21397 | 345.9497 | 0.10739 | 0 | 0 | 0.21477 | 346.2282 | 0.10799 | 0 | 0 | 0.21598 | 346.4139 | 0.10839 | 0 | 0 | 0.21679 | 346.6925 | 0.109 | 0 | 0 | 0.218 | 346.971 | 0.1096 | 0 | 0 | 0.2192 | 347.1567 | 0.11 | 0 | 0 | 0.22001 | 347.4352 | 0.11061 | 0 | 0 | 0.22122 | 347.7138 | 0.11121 | 0 | 0 | 0.22243 | 347.8066 | 0.11141 | 0 | 0 | 0.22283 | 348.0852 | 0.11202 | 0 | 0 | 0.22404 | 348.3637 | 0.11262 | 0 | 0 | 0.22525 | 348.5494 | 0.11303 | 0 | 0 | 0.22605 | 348.828 | 0.11363 | 0 | 0 | 0.22726 | 349.0137 | 0.11403 | 0 | 0 | 0.22806 | 349.1993 | 0.11444 | 0 | 0 | 0.22887
2017-12-12 03:00 | 310.9189 | 0.92672 |  | 326.485 | 0.065168 | 0 | 0 | 0.13034 | 335.6596 | 0.085067 | 0 | 0 | 0.17013 | 343.166 | 0.10135 | 0 | 0 | 0.2027 | 343.444 | 0.10195 | 0 | 0 | 0.2039 | 343.6294 | 0.10235 | 0 | 0 | 0.20471 | 343.9074 | 0.10296 | 0 | 0 | 0.20591 | 344.1854 | 0.10356 | 0 | 0 | 0.20712 | 344.4634 | 0.10416 | 0 | 0 | 0.20833 | 344.8341 | 0.10497 | 0 | 0 | 0.20993 | 345.1121 | 0.10557 | 0 | 0 | 0.21114 | 345.2975 | 0.10597 | 0 | 0 | 0.21194 | 345.5755 | 0.10657 | 0 | 0 | 0.21315 | 345.7609 | 0.10698 | 0 | 0 | 0.21395 | 346.0389 | 0.10758 | 0 | 0 | 0.21516 | 346.3169 | 0.10818 | 0 | 0 | 0.21637 | 346.5022 | 0.10858 | 0 | 0 | 0.21717 | 346.7802 | 0.10919 | 0 | 0 | 0.21838 | 347.0583 | 0.10979 | 0 | 0 | 0.21958 | 347.1509 | 0.10999 | 0 | 0 | 0.21998 | 347.429 | 0.1106 | 0 | 0 | 0.22119 | 347.707 | 0.1112 | 0 | 0 | 0.2224 | 347.8923 | 0.1116 | 0 | 0 | 0.2232 | 348.1703 | 0.1122 | 0 | 0 | 0.22441 | 348.3557 | 0.11261 | 0 | 0 | 0.22521 | 348.541 | 0.11301 | 0 | 0 | 0.22601
2017-12-12 04:00 | 307.5834 | 0.91678 |  | 322.9825 | 0.057571 | 0 | 0 | 0.11514 | 332.0586 | 0.077257 | 0 | 0 | 0.15451 | 339.4846 | 0.093364 | 0 | 0 | 0.18673 | 339.7596 | 0.09396 | 0 | 0 | 0.18792 | 339.943 | 0.094358 | 0 | 0 | 0.18872 | 340.218 | 0.094954 | 0 | 0 | 0.18991 | 340.493 | 0.095551 | 0 | 0 | 0.1911 | 340.7681 | 0.096148 | 0 | 0 | 0.1923 | 341.1348 | 0.096943 | 0 | 0 | 0.19389 | 341.4098 | 0.09754 | 0 | 0 | 0.19508 | 341.5932 | 0.097937 | 0 | 0 | 0.19587 | 341.8682 | 0.098534 | 0 | 0 | 0.19707 | 342.0516 | 0.098931 | 0 | 0 | 0.19786 | 342.3266 | 0.099528 | 0 | 0 | 0.19906 | 342.6016 | 0.10012 | 0 | 0 | 0.20025 | 342.785 | 0.10052 | 0 | 0 | 0.20104 | 343.06 | 0.10112 | 0 | 0 | 0.20224 | 343.3351 | 0.10172 | 0 | 0 | 0.20343 | 343.4267 | 0.10191 | 0 | 0 | 0.20383 | 343.7018 | 0.10251 | 0 | 0 | 0.20502 | 343.9768 | 0.10311 | 0 | 0 | 0.20621 | 344.1602 | 0.10351 | 0 | 0 | 0.20701 | 344.4352 | 0.1041 | 0 | 0 | 0.2082 | 344.6186 | 0.1045 | 0 | 0 | 0.209 | 344.8019 | 0.1049 | 0 | 0 | 0.20979
2017-12-12 05:00 | 311.9931 | 0.92993 |  | 327.6129 | 0.067614 | 0 | 0 | 0.13523 | 336.8192 | 0.087582 | 0 | 0 | 0.17516 | 344.3516 | 0.10392 | 0 | 0 | 0.20784 | 344.6306 | 0.10453 | 0 | 0 | 0.20905 | 344.8165 | 0.10493 | 0 | 0 | 0.20986 | 345.0955 | 0.10553 | 0 | 0 | 0.21107 | 345.3745 | 0.10614 | 0 | 0 | 0.21228 | 345.6535 | 0.10674 | 0 | 0 | 0.21349 | 346.0254 | 0.10755 | 0 | 0 | 0.2151 | 346.3044 | 0.10816 | 0 | 0 | 0.21631 | 346.4904 | 0.10856 | 0 | 0 | 0.21712 | 346.7694 | 0.10916 | 0 | 0 | 0.21833 | 346.9554 | 0.10957 | 0 | 0 | 0.21914 | 347.2343 | 0.11017 | 0 | 0 | 0.22035 | 347.5133 | 0.11078 | 0 | 0 | 0.22156 | 347.6993 | 0.11118 | 0 | 0 | 0.22236 | 347.9783 | 0.11179 | 0 | 0 | 0.22357 | 348.2573 | 0.11239 | 0 | 0 | 0.22478 | 348.3503 | 0.11259 | 0 | 0 | 0.22519 | 348.6292 | 0.1132 | 0 | 0 | 0.2264 | 348.9082 | 0.1138 | 0 | 0 | 0.22761 | 349.0942 | 0.11421 | 0 | 0 | 0.22841 | 349.3732 | 0.11481 | 0 | 0 | 0.22962 | 349.5592 | 0.11522 | 0 | 0 | 0.23043 | 349.7451 | 0.11562 | 0 | 0 | 0.23124
2017-12-12 06:00 | 311.5041 | 0.92847 |  | 327.0994 | 0.0665 | 0 | 0 | 0.133 | 336.2913 | 0.086437 | 0 | 0 | 0.17287 | 343.8118 | 0.10275 | 0 | 0 | 0.2055 | 344.0904 | 0.10335 | 0 | 0 | 0.20671 | 344.2761 | 0.10376 | 0 | 0 | 0.20751 | 344.5546 | 0.10436 | 0 | 0 | 0.20872 | 344.8332 | 0.10496 | 0 | 0 | 0.20993 | 345.1117 | 0.10557 | 0 | 0 | 0.21114 | 345.4831 | 0.10637 | 0 | 0 | 0.21275 | 345.7616 | 0.10698 | 0 | 0 | 0.21396 | 345.9473 | 0.10738 | 0 | 0 | 0.21476 | 346.2259 | 0.10799 | 0 | 0 | 0.21597 | 346.4116 | 0.10839 | 0 | 0 | 0.21678 | 346.6901 | 0.10899 | 0 | 0 | 0.21798 | 346.9686 | 0.1096 | 0 | 0 | 0.21919 | 347.1543 | 0.11 | 0 | 0 | 0.22 | 347.4329 | 0.1106 | 0 | 0 | 0.22121 | 347.7114 | 0.11121 | 0 | 0 | 0.22242 | 347.8043 | 0.11141 | 0 | 0 | 0.22282 | 348.0828 | 0.11201 | 0 | 0 | 0.22403 | 348.3613 | 0.11262 | 0 | 0 | 0.22523 | 348.547 | 0.11302 | 0 | 0 | 0.22604 | 348.8256 | 0.11362 | 0 | 0 | 0.22725 | 349.0113 | 0.11403 | 0 | 0 | 0.22805 | 349.197 | 0.11443 | 0 | 0 | 0.22886
2017-12-12 07:00 | 278.8158 | 0.83104 |  | 292.7747 | 0 | 0 | 0 | 0 | 301.0019 | 0.0098949 | 0 | 0 | 0.01979 | 307.7334 | 0.024495 | 0 | 0 | 0.048991 | 307.9827 | 0.025036 | 0 | 0 | 0.050072 | 308.1489 | 0.025397 | 0 | 0 | 0.050793 | 308.3982 | 0.025937 | 0 | 0 | 0.051875 | 308.6475 | 0.026478 | 0 | 0 | 0.052956 | 308.8968 | 0.027019 | 0 | 0 | 0.054038 | 309.2292 | 0.02774 | 0 | 0 | 0.05548 | 309.4785 | 0.028281 | 0 | 0 | 0.056561 | 309.6447 | 0.028641 | 0 | 0 | 0.057282 | 309.894 | 0.029182 | 0 | 0 | 0.058364 | 310.0603 | 0.029542 | 0 | 0 | 0.059085 | 310.3096 | 0.030083 | 0 | 0 | 0.060166 | 310.5589 | 0.030624 | 0 | 0 | 0.061248 | 310.7251 | 0.030984 | 0 | 0 | 0.061969 | 310.9744 | 0.031525 | 0 | 0 | 0.06305 | 311.2237 | 0.032066 | 0 | 0 | 0.064132 | 311.3068 | 0.032246 | 0 | 0 | 0.064492 | 311.5561 | 0.032787 | 0 | 0 | 0.065574 | 311.8054 | 0.033328 | 0 | 0 | 0.066655 | 311.9716 | 0.033688 | 0 | 0 | 0.067376 | 312.221 | 0.034229 | 0 | 0 | 0.068458 | 312.3872 | 0.034589 | 0 | 0 | 0.069179 | 312.5534 | 0.03495 | 0 | 0 | 0.0699
2017-12-12 08:00 | 282.8538 | 0.84307 |  | 297.0148 | 0.0012468 | 0 | 0 | 0.0024937 | 305.3613 | 0.01935 | 0 | 0 | 0.0387 | 312.1902 | 0.034162 | 0 | 0 | 0.068324 | 312.4431 | 0.034711 | 0 | 0 | 0.069421 | 312.6117 | 0.035076 | 0 | 0 | 0.070153 | 312.8646 | 0.035625 | 0 | 0 | 0.07125 | 313.1176 | 0.036174 | 0 | 0 | 0.072347 | 313.3705 | 0.036722 | 0 | 0 | 0.073444 | 313.7077 | 0.037454 | 0 | 0 | 0.074907 | 313.9606 | 0.038002 | 0 | 0 | 0.076004 | 314.1292 | 0.038368 | 0 | 0 | 0.076736 | 314.3822 | 0.038917 | 0 | 0 | 0.077833 | 314.5508 | 0.039282 | 0 | 0 | 0.078565 | 314.8037 | 0.039831 | 0 | 0 | 0.079662 | 315.0566 | 0.040379 | 0 | 0 | 0.080759 | 315.2252 | 0.040745 | 0 | 0 | 0.08149 | 315.4782 | 0.041294 | 0 | 0 | 0.082588 | 315.7311 | 0.041842 | 0 | 0 | 0.083685 | 315.8154 | 0.042025 | 0 | 0 | 0.08405 | 316.0683 | 0.042574 | 0 | 0 | 0.085148 | 316.3212 | 0.043122 | 0 | 0 | 0.086245 | 316.4898 | 0.043488 | 0 | 0 | 0.086976 | 316.7428 | 0.044037 | 0 | 0 | 0.088073 | 316.9114 | 0.044402 | 0 | 0 | 0.088805 | 317.08 | 0.044768 | 0 | 0 | 0.089536
2017-12-12 09:00 | 294.6506 | 0.87823 |  | 309.4022 | 0.028115 | 0 | 0 | 0.05623 | 318.0967 | 0.046973 | 0 | 0 | 0.093947 | 325.2104 | 0.062403 | 0 | 0 | 0.12481 | 325.4739 | 0.062975 | 0 | 0 | 0.12595 | 325.6495 | 0.063355 | 0 | 0 | 0.12671 | 325.913 | 0.063927 | 0 | 0 | 0.12785 | 326.1765 | 0.064498 | 0 | 0 | 0.129 | 326.4399 | 0.06507 | 0 | 0 | 0.13014 | 326.7912 | 0.065832 | 0 | 0 | 0.13166 | 327.0547 | 0.066403 | 0 | 0 | 0.13281 | 327.2304 | 0.066784 | 0 | 0 | 0.13357 | 327.4938 | 0.067356 | 0 | 0 | 0.13471 | 327.6695 | 0.067737 | 0 | 0 | 0.13547 | 327.9329 | 0.068308 | 0 | 0 | 0.13662 | 328.1964 | 0.06888 | 0 | 0 | 0.13776 | 328.3721 | 0.069261 | 0 | 0 | 0.13852 | 328.6355 | 0.069832 | 0 | 0 | 0.13966 | 328.899 | 0.070404 | 0 | 0 | 0.14081 | 328.9868 | 0.070594 | 0 | 0 | 0.14119 | 329.2503 | 0.071166 | 0 | 0 | 0.14233 | 329.5138 | 0.071737 | 0 | 0 | 0.14347 | 329.6894 | 0.072118 | 0 | 0 | 0.14424 | 329.9529 | 0.072689 | 0 | 0 | 0.14538 | 330.1285 | 0.07307 | 0 | 0 | 0.14614 | 330.3042 | 0.073451 | 0 | 0 | 0.1469
2017-12-12 10:00 | 300.9522 | 0.89702 |  | 316.0193 | 0.042467 | 0 | 0 | 0.084935 | 324.8997 | 0.061729 | 0 | 0 | 0.12346 | 332.1656 | 0.077489 | 0 | 0 | 0.15498 | 332.4347 | 0.078072 | 0 | 0 | 0.15614 | 332.6141 | 0.078462 | 0 | 0 | 0.15692 | 332.8832 | 0.079045 | 0 | 0 | 0.15809 | 333.1523 | 0.079629 | 0 | 0 | 0.15926 | 333.4214 | 0.080213 | 0 | 0 | 0.16043 | 333.7802 | 0.080991 | 0 | 0 | 0.16198 | 334.0493 | 0.081575 | 0 | 0 | 0.16315 | 334.2287 | 0.081964 | 0 | 0 | 0.16393 | 334.4978 | 0.082547 | 0 | 0 | 0.16509 | 334.6772 | 0.082937 | 0 | 0 | 0.16587 | 334.9463 | 0.08352 | 0 | 0 | 0.16704 | 335.2154 | 0.084104 | 0 | 0 | 0.16821 | 335.3948 | 0.084493 | 0 | 0 | 0.16899 | 335.6639 | 0.085077 | 0 | 0 | 0.17015 | 335.933 | 0.08566 | 0 | 0 | 0.17132 | 336.0227 | 0.085855 | 0 | 0 | 0.17171 | 336.2919 | 0.086439 | 0 | 0 | 0.17288 | 336.561 | 0.087022 | 0 | 0 | 0.17404 | 336.7404 | 0.087411 | 0 | 0 | 0.17482 | 337.0095 | 0.087995 | 0 | 0 | 0.17599 | 337.1889 | 0.088384 | 0 | 0 | 0.17677 | 337.3683 | 0.088773 | 0 | 0 | 0.17755
2017-12-12 11:00 | 289.863 | 0.86397 |  | 304.3749 | 0.017211 | 0 | 0 | 0.034422 | 312.9282 | 0.035763 | 0 | 0 | 0.071526 | 319.9263 | 0.050942 | 0 | 0 | 0.10188 | 320.1855 | 0.051504 | 0 | 0 | 0.10301 | 320.3583 | 0.051879 | 0 | 0 | 0.10376 | 320.6175 | 0.052441 | 0 | 0 | 0.10488 | 320.8766 | 0.053003 | 0 | 0 | 0.10601 | 321.1358 | 0.053565 | 0 | 0 | 0.10713 | 321.4814 | 0.054315 | 0 | 0 | 0.10863 | 321.7406 | 0.054877 | 0 | 0 | 0.10975 | 321.9134 | 0.055252 | 0 | 0 | 0.1105 | 322.1726 | 0.055814 | 0 | 0 | 0.11163 | 322.3454 | 0.056189 | 0 | 0 | 0.11238 | 322.6046 | 0.056751 | 0 | 0 | 0.1135 | 322.8638 | 0.057313 | 0 | 0 | 0.11463 | 323.0366 | 0.057688 | 0 | 0 | 0.11538 | 323.2957 | 0.05825 | 0 | 0 | 0.1165 | 323.5549 | 0.058812 | 0 | 0 | 0.11762 | 323.6413 | 0.059 | 0 | 0 | 0.118 | 323.9005 | 0.059562 | 0 | 0 | 0.11912 | 324.1597 | 0.060124 | 0 | 0 | 0.12025 | 324.3325 | 0.060499 | 0 | 0 | 0.121 | 324.5917 | 0.061061 | 0 | 0 | 0.12212 | 324.7645 | 0.061436 | 0 | 0 | 0.12287 | 324.9373 | 0.061811 | 0 | 0 | 0.12362
2017-12-12 12:00 | 289.888 | 0.86404 |  | 304.4012 | 0.017268 | 0 | 0 | 0.034536 | 312.9552 | 0.035821 | 0 | 0 | 0.071643 | 319.9539 | 0.051002 | 0 | 0 | 0.102 | 320.2131 | 0.051564 | 0 | 0 | 0.10313 | 320.3859 | 0.051939 | 0 | 0 | 0.10388 | 320.6451 | 0.052501 | 0 | 0 | 0.105 | 320.9043 | 0.053063 | 0 | 0 | 0.10613 | 321.1635 | 0.053625 | 0 | 0 | 0.10725 | 321.5092 | 0.054375 | 0 | 0 | 0.10875 | 321.7684 | 0.054937 | 0 | 0 | 0.10987 | 321.9412 | 0.055312 | 0 | 0 | 0.11062 | 322.2004 | 0.055874 | 0 | 0 | 0.11175 | 322.3732 | 0.056249 | 0 | 0 | 0.1125 | 322.6324 | 0.056811 | 0 | 0 | 0.11362 | 322.8916 | 0.057374 | 0 | 0 | 0.11475 | 323.0644 | 0.057748 | 0 | 0 | 0.1155 | 323.3236 | 0.058311 | 0 | 0 | 0.11662 | 323.5829 | 0.058873 | 0 | 0 | 0.11775 | 323.6693 | 0.05906 | 0 | 0 | 0.11812 | 323.9285 | 0.059622 | 0 | 0 | 0.11924 | 324.1877 | 0.060185 | 0 | 0 | 0.12037 | 324.3605 | 0.06056 | 0 | 0 | 0.12112 | 324.6197 | 0.061122 | 0 | 0 | 0.12224 | 324.7925 | 0.061497 | 0 | 0 | 0.12299 | 324.9653 | 0.061871 | 0 | 0 | 0.12374
2017-12-12 13:00 | 262.7389 | 0.78312 |  | 275.8929 | 0 | 0 | 0 | 0 | 283.6458 | 0 | 0 | 0 | 0 | 289.989 | 0 | 0 | 0 | 0 | 290.224 | 0 | 0 | 0 | 0 | 290.3806 | 0 | 0 | 0 | 0 | 290.6155 | 0 | 0 | 0 | 0 | 290.8505 | 0 | 0 | 0 | 0 | 291.0854 | 0 | 0 | 0 | 0 | 291.3986 | 0 | 0 | 0 | 0 | 291.6336 | 0 | 0 | 0 | 0 | 291.7902 | 0 | 0 | 0 | 0 | 292.0251 | 0 | 0 | 0 | 0 | 292.1818 | 0 | 0 | 0 | 0 | 292.4167 | 0 | 0 | 0 | 0 | 292.6516 | 0 | 0 | 0 | 0 | 292.8083 | 0 | 0 | 0 | 0 | 293.0432 | 0 | 0 | 0 | 0 | 293.2781 | 0 | 0 | 0 | 0 | 293.3564 | 0 | 0 | 0 | 0 | 293.5914 | 0 | 0 | 0 | 0 | 293.8263 | 0 | 0 | 0 | 0 | 293.9829 | 0 | 0 | 0 | 0 | 294.2179 | 0 | 0 | 0 | 0 | 294.3745 | 0 | 0 | 0 | 0 | 294.5311 | 0 | 0 | 0 | 0
2017-12-12 14:00 | 263.6873 | 0.78595 |  | 276.8888 | 0 | 0 | 0 | 0 | 284.6696 | 0 | 0 | 0 | 0 | 291.0358 | 0 | 0 | 0 | 0 | 291.2716 | 0 | 0 | 0 | 0 | 291.4288 | 0 | 0 | 0 | 0 | 291.6645 | 0 | 0 | 0 | 0 | 291.9003 | 0 | 0 | 0 | 0 | 292.1361 | 0 | 0 | 0 | 0 | 292.4505 | 0 | 0 | 0 | 0 | 292.6863 | 0 | 0 | 0 | 0 | 292.8435 | 0 | 0 | 0 | 0 | 293.0792 | 0 | 0 | 0 | 0 | 293.2364 | 0 | 0 | 0 | 0 | 293.4722 | 0 | 0 | 0 | 0 | 293.708 | 0 | 0 | 0 | 0 | 293.8652 | 0 | 0 | 0 | 0 | 294.101 | 0 | 0 | 0 | 0 | 294.3368 | 0 | 0 | 0 | 0 | 294.4154 | 0 | 0 | 0 | 0 | 294.6511 | 0 | 0 | 0 | 0 | 294.8869 | 0 | 0 | 0 | 0 | 295.0441 | 0 | 0 | 0 | 0 | 295.2799 | 0 | 0 | 0 | 0 | 295.4371 | 0 | 0 | 0 | 0 | 295.5943 | 0 | 0 | 0 | 0
2017-12-12 15:00 | 272.4459 | 0.81205 |  | 286.0858 | 0 | 0 | 0 | 0 | 294.1251 | 0 | 0 | 0 | 0 | 300.7028 | 0.0092459 | 0 | 0 | 0.018492 | 300.9464 | 0.0097743 | 0 | 0 | 0.019549 | 301.1088 | 0.010127 | 0 | 0 | 0.020253 | 301.3524 | 0.010655 | 0 | 0 | 0.02131 | 301.596 | 0.011183 | 0 | 0 | 0.022367 | 301.8396 | 0.011712 | 0 | 0 | 0.023424 | 302.1644 | 0.012416 | 0 | 0 | 0.024833 | 302.4081 | 0.012945 | 0 | 0 | 0.025889 | 302.5705 | 0.013297 | 0 | 0 | 0.026594 | 302.8141 | 0.013825 | 0 | 0 | 0.027651 | 302.9765 | 0.014178 | 0 | 0 | 0.028355 | 303.2201 | 0.014706 | 0 | 0 | 0.029412 | 303.4637 | 0.015234 | 0 | 0 | 0.030469 | 303.6261 | 0.015587 | 0 | 0 | 0.031173 | 303.8698 | 0.016115 | 0 | 0 | 0.03223 | 304.1134 | 0.016644 | 0 | 0 | 0.033287 | 304.1946 | 0.01682 | 0 | 0 | 0.033639 | 304.4382 | 0.017348 | 0 | 0 | 0.034696 | 304.6818 | 0.017876 | 0 | 0 | 0.035753 | 304.8442 | 0.018229 | 0 | 0 | 0.036457 | 305.0878 | 0.018757 | 0 | 0 | 0.037514 | 305.2502 | 0.019109 | 0 | 0 | 0.038219 | 305.4127 | 0.019462 | 0 | 0 | 0.038923
2017-12-12 16:00 | 284.9957 | 0.84946 |  | 299.264 | 0.0061252 | 0 | 0 | 0.01225 | 307.6736 | 0.024366 | 0 | 0 | 0.048731 | 314.5542 | 0.03929 | 0 | 0 | 0.078579 | 314.809 | 0.039842 | 0 | 0 | 0.079685 | 314.9789 | 0.040211 | 0 | 0 | 0.080422 | 315.2338 | 0.040764 | 0 | 0 | 0.081527 | 315.4886 | 0.041316 | 0 | 0 | 0.082633 | 315.7434 | 0.041869 | 0 | 0 | 0.083738 | 316.0832 | 0.042606 | 0 | 0 | 0.085212 | 316.3381 | 0.043159 | 0 | 0 | 0.086318 | 316.5079 | 0.043527 | 0 | 0 | 0.087055 | 316.7628 | 0.04408 | 0 | 0 | 0.08816 | 316.9327 | 0.044449 | 0 | 0 | 0.088897 | 317.1875 | 0.045001 | 0 | 0 | 0.090003 | 317.4423 | 0.045554 | 0 | 0 | 0.091108 | 317.6122 | 0.045923 | 0 | 0 | 0.091845 | 317.8671 | 0.046475 | 0 | 0 | 0.092951 | 318.1219 | 0.047028 | 0 | 0 | 0.094056 | 318.2069 | 0.047212 | 0 | 0 | 0.094425 | 318.4617 | 0.047765 | 0 | 0 | 0.09553 | 318.7165 | 0.048318 | 0 | 0 | 0.096636 | 318.8864 | 0.048686 | 0 | 0 | 0.097373 | 319.1413 | 0.049239 | 0 | 0 | 0.098478 | 319.3112 | 0.049608 | 0 | 0 | 0.099215 | 319.481 | 0.049976 | 0 | 0 | 0.099952
2017-12-12 17:00 | 284.6376 | 0.84839 |  | 298.8879 | 0.0053095 | 0 | 0 | 0.010619 | 307.287 | 0.023527 | 0 | 0 | 0.047054 | 314.1589 | 0.038432 | 0 | 0 | 0.076865 | 314.4134 | 0.038984 | 0 | 0 | 0.077969 | 314.5831 | 0.039352 | 0 | 0 | 0.078705 | 314.8376 | 0.039904 | 0 | 0 | 0.079809 | 315.0922 | 0.040457 | 0 | 0 | 0.080913 | 315.3467 | 0.041009 | 0 | 0 | 0.082017 | 315.686 | 0.041745 | 0 | 0 | 0.083489 | 315.9406 | 0.042297 | 0 | 0 | 0.084593 | 316.1102 | 0.042665 | 0 | 0 | 0.085329 | 316.3647 | 0.043217 | 0 | 0 | 0.086434 | 316.5344 | 0.043585 | 0 | 0 | 0.08717 | 316.7889 | 0.044137 | 0 | 0 | 0.088274 | 317.0435 | 0.044689 | 0 | 0 | 0.089378 | 317.2131 | 0.045057 | 0 | 0 | 0.090114 | 317.4677 | 0.045609 | 0 | 0 | 0.091218 | 317.7222 | 0.046161 | 0 | 0 | 0.092322 | 317.807 | 0.046345 | 0 | 0 | 0.09269 | 318.0615 | 0.046897 | 0 | 0 | 0.093794 | 318.316 | 0.047449 | 0 | 0 | 0.094898 | 318.4857 | 0.047817 | 0 | 0 | 0.095634 | 318.7402 | 0.048369 | 0 | 0 | 0.096738 | 318.9099 | 0.048737 | 0 | 0 | 0.097475 | 319.0796 | 0.049105 | 0 | 0 | 0.098211
2017-12-12 18:00 | 290.6194 | 0.86622 |  | 305.1692 | 0.018934 | 0 | 0 | 0.037867 | 313.7448 | 0.037534 | 0 | 0 | 0.075068 | 320.7612 | 0.052753 | 0 | 0 | 0.10551 | 321.021 | 0.053316 | 0 | 0 | 0.10663 | 321.1943 | 0.053692 | 0 | 0 | 0.10738 | 321.4541 | 0.054256 | 0 | 0 | 0.10851 | 321.714 | 0.054819 | 0 | 0 | 0.10964 | 321.9739 | 0.055383 | 0 | 0 | 0.11077 | 322.3203 | 0.056134 | 0 | 0 | 0.11227 | 322.5802 | 0.056698 | 0 | 0 | 0.1134 | 322.7535 | 0.057074 | 0 | 0 | 0.11415 | 323.0133 | 0.057638 | 0 | 0 | 0.11528 | 323.1866 | 0.058013 | 0 | 0 | 0.11603 | 323.4464 | 0.058577 | 0 | 0 | 0.11715 | 323.7063 | 0.059141 | 0 | 0 | 0.11828 | 323.8795 | 0.059516 | 0 | 0 | 0.11903 | 324.1394 | 0.06008 | 0 | 0 | 0.12016 | 324.3993 | 0.060644 | 0 | 0 | 0.12129 | 324.4859 | 0.060832 | 0 | 0 | 0.12166 | 324.7458 | 0.061395 | 0 | 0 | 0.12279 | 325.0056 | 0.061959 | 0 | 0 | 0.12392 | 325.1789 | 0.062335 | 0 | 0 | 0.12467 | 325.4387 | 0.062898 | 0 | 0 | 0.1258 | 325.612 | 0.063274 | 0 | 0 | 0.12655 | 325.7852 | 0.06365 | 0 | 0 | 0.1273
2017-12-12 19:00 | 286.1311 | 0.85284 |  | 300.4562 | 0.0087112 | 0 | 0 | 0.017422 | 308.8993 | 0.027024 | 0 | 0 | 0.054049 | 315.8074 | 0.042008 | 0 | 0 | 0.084016 | 316.0632 | 0.042563 | 0 | 0 | 0.085126 | 316.2338 | 0.042933 | 0 | 0 | 0.085865 | 316.4896 | 0.043488 | 0 | 0 | 0.086975 | 316.7455 | 0.044043 | 0 | 0 | 0.088085 | 317.0013 | 0.044598 | 0 | 0 | 0.089195 | 317.3425 | 0.045337 | 0 | 0 | 0.090675 | 317.5983 | 0.045892 | 0 | 0 | 0.091785 | 317.7689 | 0.046262 | 0 | 0 | 0.092525 | 318.0248 | 0.046817 | 0 | 0 | 0.093635 | 318.1953 | 0.047187 | 0 | 0 | 0.094375 | 318.4512 | 0.047742 | 0 | 0 | 0.095484 | 318.707 | 0.048297 | 0 | 0 | 0.096594 | 318.8776 | 0.048667 | 0 | 0 | 0.097334 | 319.1334 | 0.049222 | 0 | 0 | 0.098444 | 319.3893 | 0.049777 | 0 | 0 | 0.099554 | 319.4746 | 0.049962 | 0 | 0 | 0.099924 | 319.7304 | 0.050517 | 0 | 0 | 0.10103 | 319.9863 | 0.051072 | 0 | 0 | 0.10214 | 320.1569 | 0.051442 | 0 | 0 | 0.10288 | 320.4127 | 0.051997 | 0 | 0 | 0.10399 | 320.5833 | 0.052367 | 0 | 0 | 0.10473 | 320.7538 | 0.052737 | 0 | 0 | 0.10547
2017-12-12 20:00 | 278.5594 | 0.83027 |  | 292.5054 | 0 | 0 | 0 | 0 | 300.7251 | 0.0092944 | 0 | 0 | 0.018589 | 307.4503 | 0.023881 | 0 | 0 | 0.047763 | 307.6994 | 0.024422 | 0 | 0 | 0.048843 | 307.8654 | 0.024782 | 0 | 0 | 0.049564 | 308.1145 | 0.025322 | 0 | 0 | 0.050644 | 308.3636 | 0.025862 | 0 | 0 | 0.051725 | 308.6127 | 0.026403 | 0 | 0 | 0.052805 | 308.9448 | 0.027123 | 0 | 0 | 0.054246 | 309.1939 | 0.027663 | 0 | 0 | 0.055326 | 309.3599 | 0.028023 | 0 | 0 | 0.056047 | 309.609 | 0.028564 | 0 | 0 | 0.057127 | 309.7751 | 0.028924 | 0 | 0 | 0.057848 | 310.0242 | 0.029464 | 0 | 0 | 0.058928 | 310.2732 | 0.030004 | 0 | 0 | 0.060009 | 310.4393 | 0.030364 | 0 | 0 | 0.060729 | 310.6884 | 0.030905 | 0 | 0 | 0.061809 | 310.9375 | 0.031445 | 0 | 0 | 0.06289 | 311.0205 | 0.031625 | 0 | 0 | 0.06325 | 311.2696 | 0.032165 | 0 | 0 | 0.064331 | 311.5186 | 0.032706 | 0 | 0 | 0.065411 | 311.6847 | 0.033066 | 0 | 0 | 0.066131 | 311.9338 | 0.033606 | 0 | 0 | 0.067212 | 312.0998 | 0.033966 | 0 | 0 | 0.067932 | 312.2659 | 0.034326 | 0 | 0 | 0.068653
2017-12-12 21:00 | 280.7302 | 0.83674 |  | 294.7849 | 0 | 0 | 0 | 0 | 303.0687 | 0.014378 | 0 | 0 | 0.028755 | 309.8463 | 0.029078 | 0 | 0 | 0.058157 | 310.0973 | 0.029623 | 0 | 0 | 0.059245 | 310.2647 | 0.029986 | 0 | 0 | 0.059971 | 310.5157 | 0.03053 | 0 | 0 | 0.06106 | 310.7667 | 0.031075 | 0 | 0 | 0.062149 | 311.0177 | 0.031619 | 0 | 0 | 0.063238 | 311.3524 | 0.032345 | 0 | 0 | 0.06469 | 311.6035 | 0.03289 | 0 | 0 | 0.065779 | 311.7708 | 0.033253 | 0 | 0 | 0.066505 | 312.0218 | 0.033797 | 0 | 0 | 0.067594 | 312.1892 | 0.03416 | 0 | 0 | 0.06832 | 312.4402 | 0.034704 | 0 | 0 | 0.069409 | 312.6912 | 0.035249 | 0 | 0 | 0.070498 | 312.8586 | 0.035612 | 0 | 0 | 0.071224 | 313.1096 | 0.036156 | 0 | 0 | 0.072313 | 313.3606 | 0.036701 | 0 | 0 | 0.073402 | 313.4443 | 0.036882 | 0 | 0 | 0.073765 | 313.6953 | 0.037427 | 0 | 0 | 0.074854 | 313.9464 | 0.037971 | 0 | 0 | 0.075943 | 314.1137 | 0.038334 | 0 | 0 | 0.076669 | 314.3647 | 0.038879 | 0 | 0 | 0.077757 | 314.5321 | 0.039242 | 0 | 0 | 0.078483 | 314.6994 | 0.039605 | 0 | 0 | 0.079209
2017-12-12 22:00 | 278.2761 | 0.82943 |  | 292.2079 | 0 | 0 | 0 | 0 | 300.4192 | 0.008631 | 0 | 0 | 0.017262 | 307.1376 | 0.023203 | 0 | 0 | 0.046406 | 307.3864 | 0.023743 | 0 | 0 | 0.047486 | 307.5523 | 0.024103 | 0 | 0 | 0.048205 | 307.8012 | 0.024642 | 0 | 0 | 0.049285 | 308.05 | 0.025182 | 0 | 0 | 0.050364 | 308.2988 | 0.025722 | 0 | 0 | 0.051444 | 308.6306 | 0.026441 | 0 | 0 | 0.052883 | 308.8794 | 0.026981 | 0 | 0 | 0.053962 | 309.0453 | 0.027341 | 0 | 0 | 0.054682 | 309.2941 | 0.027881 | 0 | 0 | 0.055761 | 309.46 | 0.02824 | 0 | 0 | 0.056481 | 309.7088 | 0.02878 | 0 | 0 | 0.05756 | 309.9577 | 0.02932 | 0 | 0 | 0.05864 | 310.1236 | 0.02968 | 0 | 0 | 0.059359 | 310.3724 | 0.030219 | 0 | 0 | 0.060439 | 310.6212 | 0.030759 | 0 | 0 | 0.061518 | 310.7042 | 0.030939 | 0 | 0 | 0.061878 | 310.953 | 0.031479 | 0 | 0 | 0.062957 | 311.2018 | 0.032018 | 0 | 0 | 0.064037 | 311.3677 | 0.032378 | 0 | 0 | 0.064756 | 311.6165 | 0.032918 | 0 | 0 | 0.065836 | 311.7824 | 0.033278 | 0 | 0 | 0.066555 | 311.9483 | 0.033637 | 0 | 0 | 0.067275
2017-12-12 23:00 | 277.4188 | 0.82687 |  | 291.3077 | 0 | 0 | 0 | 0 | 299.4937 | 0.0066236 | 0 | 0 | 0.013247 | 306.1914 | 0.021151 | 0 | 0 | 0.042302 | 306.4395 | 0.021689 | 0 | 0 | 0.043378 | 306.6049 | 0.022048 | 0 | 0 | 0.044095 | 306.8529 | 0.022586 | 0 | 0 | 0.045171 | 307.101 | 0.023124 | 0 | 0 | 0.046247 | 307.349 | 0.023662 | 0 | 0 | 0.047323 | 307.6798 | 0.024379 | 0 | 0 | 0.048758 | 307.9279 | 0.024917 | 0 | 0 | 0.049834 | 308.0932 | 0.025276 | 0 | 0 | 0.050552 | 308.3413 | 0.025814 | 0 | 0 | 0.051628 | 308.5067 | 0.026173 | 0 | 0 | 0.052345 | 308.7547 | 0.026711 | 0 | 0 | 0.053421 | 309.0028 | 0.027249 | 0 | 0 | 0.054497 | 309.1682 | 0.027607 | 0 | 0 | 0.055215 | 309.4162 | 0.028145 | 0 | 0 | 0.056291 | 309.6643 | 0.028683 | 0 | 0 | 0.057367 | 309.747 | 0.028863 | 0 | 0 | 0.057726 | 309.995 | 0.029401 | 0 | 0 | 0.058802 | 310.2431 | 0.029939 | 0 | 0 | 0.059878 | 310.4085 | 0.030298 | 0 | 0 | 0.060595 | 310.6565 | 0.030836 | 0 | 0 | 0.061671 | 310.8219 | 0.031194 | 0 | 0 | 0.062389 | 310.9873 | 0.031553 | 0 | 0 | 0.063106
2017-12-13 | 274.043 | 0.81681 |  | 287.7629 | 0 | 0 | 0 | 0 | 295.8494 | 0 | 0 | 0 | 0 | 302.4655 | 0.013069 | 0 | 0 | 0.026139 | 302.7106 | 0.013601 | 0 | 0 | 0.027202 | 302.8739 | 0.013955 | 0 | 0 | 0.02791 | 303.119 | 0.014487 | 0 | 0 | 0.028973 | 303.364 | 0.015018 | 0 | 0 | 0.030036 | 303.6091 | 0.01555 | 0 | 0 | 0.031099 | 303.9358 | 0.016258 | 0 | 0 | 0.032517 | 304.1808 | 0.01679 | 0 | 0 | 0.03358 | 304.3442 | 0.017144 | 0 | 0 | 0.034288 | 304.5892 | 0.017676 | 0 | 0 | 0.035351 | 304.7526 | 0.01803 | 0 | 0 | 0.03606 | 304.9976 | 0.018562 | 0 | 0 | 0.037123 | 305.2427 | 0.019093 | 0 | 0 | 0.038186 | 305.4061 | 0.019447 | 0 | 0 | 0.038895 | 305.6511 | 0.019979 | 0 | 0 | 0.039958 | 305.8961 | 0.02051 | 0 | 0 | 0.041021 | 305.9778 | 0.020688 | 0 | 0 | 0.041375 | 306.2229 | 0.021219 | 0 | 0 | 0.042438 | 306.4679 | 0.021751 | 0 | 0 | 0.043501 | 306.6313 | 0.022105 | 0 | 0 | 0.04421 | 306.8763 | 0.022636 | 0 | 0 | 0.045273 | 307.0397 | 0.022991 | 0 | 0 | 0.045981 | 307.203 | 0.023345 | 0 | 0 | 0.04669
2017-12-13 01:00 | 267.1504 | 0.79627 |  | 280.5252 | 0 | 0 | 0 | 0 | 288.4083 | 0 | 0 | 0 | 0 | 294.8581 | 0 | 0 | 0 | 0 | 295.0969 | 0 | 0 | 0 | 0 | 295.2562 | 0 | 0 | 0 | 0 | 295.4951 | 0 | 0 | 0 | 0 | 295.7339 | 0 | 0 | 0 | 0 | 295.9728 | 0 | 0 | 0 | 0 | 296.2913 | 0 | 0 | 0 | 0 | 296.5302 | 0.00019568 | 0 | 0 | 0.00039136 | 296.6895 | 0.0005411 | 0 | 0 | 0.0010822 | 296.9284 | 0.0010592 | 0 | 0 | 0.0021185 | 297.0876 | 0.0014047 | 0 | 0 | 0.0028093 | 297.3265 | 0.0019228 | 0 | 0 | 0.0038456 | 297.5654 | 0.0024409 | 0 | 0 | 0.0048818 | 297.7246 | 0.0027863 | 0 | 0 | 0.0055727 | 297.9635 | 0.0033045 | 0 | 0 | 0.0066089 | 298.2024 | 0.0038226 | 0 | 0 | 0.0076452 | 298.282 | 0.0039953 | 0 | 0 | 0.0079906 | 298.5209 | 0.0045134 | 0 | 0 | 0.0090269 | 298.7598 | 0.0050316 | 0 | 0 | 0.010063 | 298.919 | 0.005377 | 0 | 0 | 0.010754 | 299.1579 | 0.0058951 | 0 | 0 | 0.01179 | 299.3172 | 0.0062405 | 0 | 0 | 0.012481 | 299.4764 | 0.006586 | 0 | 0 | 0.013172
2017-12-13 02:00 | 269.0025 | 0.80179 |  | 282.4701 | 0 | 0 | 0 | 0 | 290.4078 | 0 | 0 | 0 | 0 | 296.9023 | 0.0010027 | 0 | 0 | 0.0020054 | 297.1428 | 0.0015244 | 0 | 0 | 0.0030488 | 297.3032 | 0.0018722 | 0 | 0 | 0.0037444 | 297.5437 | 0.0023939 | 0 | 0 | 0.0047879 | 297.7842 | 0.0029157 | 0 | 0 | 0.0058313 | 298.0248 | 0.0034374 | 0 | 0 | 0.0068748 | 298.3455 | 0.004133 | 0 | 0 | 0.0082661 | 298.586 | 0.0046548 | 0 | 0 | 0.0093095 | 298.7464 | 0.0050026 | 0 | 0 | 0.010005 | 298.9869 | 0.0055243 | 0 | 0 | 0.011049 | 299.1473 | 0.0058721 | 0 | 0 | 0.011744 | 299.3878 | 0.0063938 | 0 | 0 | 0.012788 | 299.6284 | 0.0069156 | 0 | 0 | 0.013831 | 299.7887 | 0.0072634 | 0 | 0 | 0.014527 | 300.0293 | 0.0077851 | 0 | 0 | 0.01557 | 300.2698 | 0.0083068 | 0 | 0 | 0.016614 | 300.35 | 0.0084807 | 0 | 0 | 0.016961 | 300.5905 | 0.0090024 | 0 | 0 | 0.018005 | 300.831 | 0.0095242 | 0 | 0 | 0.019048 | 300.9914 | 0.009872 | 0 | 0 | 0.019744 | 301.2319 | 0.010394 | 0 | 0 | 0.020787 | 301.3923 | 0.010742 | 0 | 0 | 0.021483 | 301.5527 | 0.011089 | 0 | 0 | 0.022179
2017-12-13 03:00 | 270.7166 | 0.8069 |  | 284.27 | 0 | 0 | 0 | 0 | 292.2582 | 0 | 0 | 0 | 0 | 298.7941 | 0.0051061 | 0 | 0 | 0.010212 | 299.0362 | 0.0056311 | 0 | 0 | 0.011262 | 299.1976 | 0.0059811 | 0 | 0 | 0.011962 | 299.4396 | 0.0065062 | 0 | 0 | 0.013012 | 299.6817 | 0.0070312 | 0 | 0 | 0.014062 | 299.9238 | 0.0075563 | 0 | 0 | 0.015113 | 300.2465 | 0.0082564 | 0 | 0 | 0.016513 | 300.4886 | 0.0087814 | 0 | 0 | 0.017563 | 300.65 | 0.0091314 | 0 | 0 | 0.018263 | 300.892 | 0.0096565 | 0 | 0 | 0.019313 | 301.0534 | 0.010007 | 0 | 0 | 0.020013 | 301.2955 | 0.010532 | 0 | 0 | 0.021063 | 301.5376 | 0.011057 | 0 | 0 | 0.022113 | 301.6989 | 0.011407 | 0 | 0 | 0.022813 | 301.941 | 0.011932 | 0 | 0 | 0.023863 | 302.1831 | 0.012457 | 0 | 0 | 0.024913 | 302.2638 | 0.012632 | 0 | 0 | 0.025264 | 302.5058 | 0.013157 | 0 | 0 | 0.026314 | 302.7479 | 0.013682 | 0 | 0 | 0.027364 | 302.9093 | 0.014032 | 0 | 0 | 0.028064 | 303.1514 | 0.014557 | 0 | 0 | 0.029114 | 303.3127 | 0.014907 | 0 | 0 | 0.029814 | 303.4741 | 0.015257 | 0 | 0 | 0.030514
2017-12-13 04:00 | 274.5643 | 0.81837 |  | 288.3103 | 0 | 0 | 0 | 0 | 296.4121 | 0 | 0 | 0 | 0 | 303.0409 | 0.014317 | 0 | 0 | 0.028634 | 303.2864 | 0.01485 | 0 | 0 | 0.0297 | 303.45 | 0.015205 | 0 | 0 | 0.03041 | 303.6955 | 0.015737 | 0 | 0 | 0.031475 | 303.9411 | 0.01627 | 0 | 0 | 0.03254 | 304.1866 | 0.016802 | 0 | 0 | 0.033605 | 304.5139 | 0.017512 | 0 | 0 | 0.035025 | 304.7594 | 0.018045 | 0 | 0 | 0.03609 | 304.9231 | 0.0184 | 0 | 0 | 0.0368 | 305.1686 | 0.018932 | 0 | 0 | 0.037865 | 305.3323 | 0.019287 | 0 | 0 | 0.038575 | 305.5778 | 0.01982 | 0 | 0 | 0.03964 | 305.8233 | 0.020352 | 0 | 0 | 0.040705 | 305.987 | 0.020707 | 0 | 0 | 0.041415 | 306.2325 | 0.02124 | 0 | 0 | 0.04248 | 306.478 | 0.021772 | 0 | 0 | 0.043545 | 306.5598 | 0.02195 | 0 | 0 | 0.0439 | 306.8053 | 0.022482 | 0 | 0 | 0.044965 | 307.0508 | 0.023015 | 0 | 0 | 0.04603 | 307.2145 | 0.02337 | 0 | 0 | 0.04674 | 307.46 | 0.023902 | 0 | 0 | 0.047805 | 307.6237 | 0.024257 | 0 | 0 | 0.048515 | 307.7874 | 0.024612 | 0 | 0 | 0.049225
2017-12-13 05:00 | 270.0036 | 0.80477 |  | 283.5213 | 0 | 0 | 0 | 0 | 291.4885 | 0 | 0 | 0 | 0 | 298.0072 | 0.0033992 | 0 | 0 | 0.0067985 | 298.2486 | 0.0039229 | 0 | 0 | 0.0078458 | 298.4096 | 0.004272 | 0 | 0 | 0.008544 | 298.651 | 0.0047957 | 0 | 0 | 0.0095914 | 298.8924 | 0.0053194 | 0 | 0 | 0.010639 | 299.1339 | 0.005843 | 0 | 0 | 0.011686 | 299.4558 | 0.0065412 | 0 | 0 | 0.013082 | 299.6972 | 0.0070649 | 0 | 0 | 0.01413 | 299.8582 | 0.007414 | 0 | 0 | 0.014828 | 300.0996 | 0.0079377 | 0 | 0 | 0.015875 | 300.2606 | 0.0082868 | 0 | 0 | 0.016574 | 300.502 | 0.0088105 | 0 | 0 | 0.017621 | 300.7434 | 0.0093341 | 0 | 0 | 0.018668 | 300.9044 | 0.0096832 | 0 | 0 | 0.019366 | 301.1458 | 0.010207 | 0 | 0 | 0.020414 | 301.3872 | 0.010731 | 0 | 0 | 0.021461 | 301.4677 | 0.010905 | 0 | 0 | 0.02181 | 301.7091 | 0.011429 | 0 | 0 | 0.022858 | 301.9506 | 0.011952 | 0 | 0 | 0.023905 | 302.1115 | 0.012302 | 0 | 0 | 0.024603 | 302.353 | 0.012825 | 0 | 0 | 0.02565 | 302.5139 | 0.013174 | 0 | 0 | 0.026349 | 302.6749 | 0.013523 | 0 | 0 | 0.027047
2017-12-13 06:00 | 279.0407 | 0.83171 |  | 293.0108 | 0 | 0 | 0 | 0 | 301.2447 | 0.010421 | 0 | 0 | 0.020843 | 307.9815 | 0.025034 | 0 | 0 | 0.050067 | 308.231 | 0.025575 | 0 | 0 | 0.051149 | 308.3974 | 0.025936 | 0 | 0 | 0.051871 | 308.6469 | 0.026477 | 0 | 0 | 0.052953 | 308.8964 | 0.027018 | 0 | 0 | 0.054036 | 309.1459 | 0.027559 | 0 | 0 | 0.055118 | 309.4786 | 0.028281 | 0 | 0 | 0.056561 | 309.7281 | 0.028822 | 0 | 0 | 0.057644 | 309.8944 | 0.029183 | 0 | 0 | 0.058365 | 310.1439 | 0.029724 | 0 | 0 | 0.059448 | 310.3103 | 0.030085 | 0 | 0 | 0.060169 | 310.5598 | 0.030626 | 0 | 0 | 0.061252 | 310.8093 | 0.031167 | 0 | 0 | 0.062334 | 310.9757 | 0.031528 | 0 | 0 | 0.063056 | 311.2252 | 0.032069 | 0 | 0 | 0.064138 | 311.4747 | 0.03261 | 0 | 0 | 0.06522 | 311.5578 | 0.032791 | 0 | 0 | 0.065581 | 311.8074 | 0.033332 | 0 | 0 | 0.066664 | 312.0569 | 0.033873 | 0 | 0 | 0.067746 | 312.2232 | 0.034234 | 0 | 0 | 0.068468 | 312.4727 | 0.034775 | 0 | 0 | 0.06955 | 312.6391 | 0.035136 | 0 | 0 | 0.070272 | 312.8054 | 0.035497 | 0 | 0 | 0.070993
2017-12-13 07:00 | 277.4298 | 0.82691 |  | 291.3192 | 0 | 0 | 0 | 0 | 299.5056 | 0.0066493 | 0 | 0 | 0.013299 | 306.2035 | 0.021177 | 0 | 0 | 0.042354 | 306.4516 | 0.021715 | 0 | 0 | 0.04343 | 306.617 | 0.022074 | 0 | 0 | 0.044148 | 306.8651 | 0.022612 | 0 | 0 | 0.045224 | 307.1131 | 0.02315 | 0 | 0 | 0.0463 | 307.3612 | 0.023688 | 0 | 0 | 0.047376 | 307.692 | 0.024406 | 0 | 0 | 0.048811 | 307.94 | 0.024944 | 0 | 0 | 0.049887 | 308.1054 | 0.025302 | 0 | 0 | 0.050605 | 308.3535 | 0.02584 | 0 | 0 | 0.051681 | 308.5189 | 0.026199 | 0 | 0 | 0.052398 | 308.7669 | 0.026737 | 0 | 0 | 0.053474 | 309.015 | 0.027275 | 0 | 0 | 0.05455 | 309.1804 | 0.027634 | 0 | 0 | 0.055268 | 309.4285 | 0.028172 | 0 | 0 | 0.056344 | 309.6765 | 0.02871 | 0 | 0 | 0.05742 | 309.7592 | 0.028889 | 0 | 0 | 0.057779 | 310.0073 | 0.029427 | 0 | 0 | 0.058855 | 310.2554 | 0.029966 | 0 | 0 | 0.059931 | 310.4208 | 0.030324 | 0 | 0 | 0.060649 | 310.6688 | 0.030862 | 0 | 0 | 0.061725 | 310.8342 | 0.031221 | 0 | 0 | 0.062442 | 310.9996 | 0.03158 | 0 | 0 | 0.063159
2017-12-13 08:00 | 271.0796 | 0.80798 |  | 284.6511 | 0 | 0 | 0 | 0 | 292.6501 | 0 | 0 | 0 | 0 | 299.1948 | 0.0059751 | 0 | 0 | 0.01195 | 299.4372 | 0.0065009 | 0 | 0 | 0.013002 | 299.5988 | 0.0068514 | 0 | 0 | 0.013703 | 299.8412 | 0.0073771 | 0 | 0 | 0.014754 | 300.0836 | 0.0079029 | 0 | 0 | 0.015806 | 300.3259 | 0.0084286 | 0 | 0 | 0.016857 | 300.6491 | 0.0091296 | 0 | 0 | 0.018259 | 300.8915 | 0.0096554 | 0 | 0 | 0.019311 | 301.0531 | 0.010006 | 0 | 0 | 0.020012 | 301.2955 | 0.010532 | 0 | 0 | 0.021063 | 301.4571 | 0.010882 | 0 | 0 | 0.021764 | 301.6995 | 0.011408 | 0 | 0 | 0.022816 | 301.9419 | 0.011934 | 0 | 0 | 0.023867 | 302.1035 | 0.012284 | 0 | 0 | 0.024568 | 302.3459 | 0.01281 | 0 | 0 | 0.02562 | 302.5883 | 0.013336 | 0 | 0 | 0.026671 | 302.6691 | 0.013511 | 0 | 0 | 0.027022 | 302.9115 | 0.014037 | 0 | 0 | 0.028073 | 303.1539 | 0.014562 | 0 | 0 | 0.029125 | 303.3155 | 0.014913 | 0 | 0 | 0.029826 | 303.5579 | 0.015439 | 0 | 0 | 0.030877 | 303.7195 | 0.015789 | 0 | 0 | 0.031578 | 303.8811 | 0.01614 | 0 | 0 | 0.032279
2017-12-13 09:00 | 270.6254 | 0.80663 |  | 284.1742 | 0 | 0 | 0 | 0 | 292.1598 | 0 | 0 | 0 | 0 | 298.6935 | 0.0048878 | 0 | 0 | 0.0097756 | 298.9355 | 0.0054127 | 0 | 0 | 0.010825 | 299.0968 | 0.0057626 | 0 | 0 | 0.011525 | 299.3388 | 0.0062875 | 0 | 0 | 0.012575 | 299.5808 | 0.0068123 | 0 | 0 | 0.013625 | 299.8228 | 0.0073372 | 0 | 0 | 0.014674 | 300.1454 | 0.008037 | 0 | 0 | 0.016074 | 300.3874 | 0.0085619 | 0 | 0 | 0.017124 | 300.5487 | 0.0089118 | 0 | 0 | 0.017824 | 300.7907 | 0.0094367 | 0 | 0 | 0.018873 | 300.952 | 0.0097866 | 0 | 0 | 0.019573 | 301.194 | 0.010311 | 0 | 0 | 0.020623 | 301.436 | 0.010836 | 0 | 0 | 0.021673 | 301.5973 | 0.011186 | 0 | 0 | 0.022373 | 301.8393 | 0.011711 | 0 | 0 | 0.023422 | 302.0813 | 0.012236 | 0 | 0 | 0.024472 | 302.162 | 0.012411 | 0 | 0 | 0.024822 | 302.404 | 0.012936 | 0 | 0 | 0.025872 | 302.6459 | 0.013461 | 0 | 0 | 0.026921 | 302.8073 | 0.013811 | 0 | 0 | 0.027621 | 303.0493 | 0.014335 | 0 | 0 | 0.028671 | 303.2106 | 0.014685 | 0 | 0 | 0.029371 | 303.3719 | 0.015035 | 0 | 0 | 0.030071
2017-12-13 10:00 | 270.3957 | 0.80594 |  | 283.933 | 0 | 0 | 0 | 0 | 291.9118 | 0 | 0 | 0 | 0 | 298.4399 | 0.0043378 | 0 | 0 | 0.0086757 | 298.6817 | 0.0048623 | 0 | 0 | 0.0097245 | 298.8429 | 0.0052119 | 0 | 0 | 0.010424 | 299.0847 | 0.0057363 | 0 | 0 | 0.011473 | 299.3265 | 0.0062607 | 0 | 0 | 0.012521 | 299.5682 | 0.0067851 | 0 | 0 | 0.01357 | 299.8906 | 0.0074844 | 0 | 0 | 0.014969 | 300.1324 | 0.0080088 | 0 | 0 | 0.016018 | 300.2936 | 0.0083584 | 0 | 0 | 0.016717 | 300.5354 | 0.0088829 | 0 | 0 | 0.017766 | 300.6966 | 0.0092325 | 0 | 0 | 0.018465 | 300.9383 | 0.0097569 | 0 | 0 | 0.019514 | 301.1801 | 0.010281 | 0 | 0 | 0.020563 | 301.3413 | 0.010631 | 0 | 0 | 0.021262 | 301.5831 | 0.011155 | 0 | 0 | 0.022311 | 301.8249 | 0.01168 | 0 | 0 | 0.02336 | 301.9055 | 0.011855 | 0 | 0 | 0.023709 | 302.1472 | 0.012379 | 0 | 0 | 0.024758 | 302.389 | 0.012903 | 0 | 0 | 0.025807 | 302.5502 | 0.013253 | 0 | 0 | 0.026506 | 302.792 | 0.013777 | 0 | 0 | 0.027555 | 302.9532 | 0.014127 | 0 | 0 | 0.028254 | 303.1144 | 0.014477 | 0 | 0 | 0.028953
2017-12-13 11:00 | 267.6874 | 0.79787 |  | 281.0891 | 0 | 0 | 0 | 0 | 288.988 | 0 | 0 | 0 | 0 | 295.4508 | 0 | 0 | 0 | 0 | 295.6901 | 0 | 0 | 0 | 0 | 295.8497 | 0 | 0 | 0 | 0 | 296.0891 | 0 | 0 | 0 | 0 | 296.3284 | 0 | 0 | 0 | 0 | 296.5678 | 0.00027716 | 0 | 0 | 0.00055431 | 296.8869 | 0.00096939 | 0 | 0 | 0.0019388 | 297.1263 | 0.0014886 | 0 | 0 | 0.0029771 | 297.2859 | 0.0018347 | 0 | 0 | 0.0036694 | 297.5252 | 0.0023538 | 0 | 0 | 0.0047077 | 297.6848 | 0.0027 | 0 | 0 | 0.0053999 | 297.9242 | 0.0032191 | 0 | 0 | 0.0064383 | 298.1635 | 0.0037383 | 0 | 0 | 0.0074766 | 298.3231 | 0.0040844 | 0 | 0 | 0.0081689 | 298.5625 | 0.0046036 | 0 | 0 | 0.0092072 | 298.8018 | 0.0051228 | 0 | 0 | 0.010246 | 298.8816 | 0.0052958 | 0 | 0 | 0.010592 | 299.121 | 0.005815 | 0 | 0 | 0.01163 | 299.3603 | 0.0063342 | 0 | 0 | 0.012668 | 299.5199 | 0.0066803 | 0 | 0 | 0.013361 | 299.7593 | 0.0071995 | 0 | 0 | 0.014399 | 299.9188 | 0.0075456 | 0 | 0 | 0.015091 | 300.0784 | 0.0078917 | 0 | 0 | 0.015783
2017-12-13 12:00 | 272.3752 | 0.81184 |  | 286.0116 | 0 | 0 | 0 | 0 | 294.0489 | 0 | 0 | 0 | 0 | 300.6248 | 0.0090768 | 0 | 0 | 0.018154 | 300.8683 | 0.009605 | 0 | 0 | 0.01921 | 301.0307 | 0.0099572 | 0 | 0 | 0.019914 | 301.2742 | 0.010485 | 0 | 0 | 0.020971 | 301.5178 | 0.011014 | 0 | 0 | 0.022027 | 301.7613 | 0.011542 | 0 | 0 | 0.023084 | 302.0861 | 0.012246 | 0 | 0 | 0.024493 | 302.3296 | 0.012775 | 0 | 0 | 0.025549 | 302.492 | 0.013127 | 0 | 0 | 0.026254 | 302.7356 | 0.013655 | 0 | 0 | 0.02731 | 302.8979 | 0.014007 | 0 | 0 | 0.028014 | 303.1415 | 0.014536 | 0 | 0 | 0.029071 | 303.385 | 0.015064 | 0 | 0 | 0.030128 | 303.5474 | 0.015416 | 0 | 0 | 0.030832 | 303.7909 | 0.015944 | 0 | 0 | 0.031888 | 304.0345 | 0.016472 | 0 | 0 | 0.032945 | 304.1157 | 0.016649 | 0 | 0 | 0.033297 | 304.3592 | 0.017177 | 0 | 0 | 0.034354 | 304.6028 | 0.017705 | 0 | 0 | 0.03541 | 304.7652 | 0.018057 | 0 | 0 | 0.036115 | 305.0087 | 0.018586 | 0 | 0 | 0.037171 | 305.1711 | 0.018938 | 0 | 0 | 0.037875 | 305.3334 | 0.01929 | 0 | 0 | 0.03858
2017-12-13 13:00 | 274.2304 | 0.81737 |  | 287.9597 | 0 | 0 | 0 | 0 | 296.0516 | 0 | 0 | 0 | 0 | 302.6723 | 0.013518 | 0 | 0 | 0.027036 | 302.9175 | 0.01405 | 0 | 0 | 0.0281 | 303.081 | 0.014404 | 0 | 0 | 0.028809 | 303.3262 | 0.014936 | 0 | 0 | 0.029872 | 303.5714 | 0.015468 | 0 | 0 | 0.030936 | 303.8166 | 0.016 | 0 | 0 | 0.032 | 304.1436 | 0.016709 | 0 | 0 | 0.033418 | 304.3888 | 0.017241 | 0 | 0 | 0.034482 | 304.5523 | 0.017596 | 0 | 0 | 0.035191 | 304.7975 | 0.018127 | 0 | 0 | 0.036255 | 304.961 | 0.018482 | 0 | 0 | 0.036964 | 305.2062 | 0.019014 | 0 | 0 | 0.038028 | 305.4514 | 0.019546 | 0 | 0 | 0.039091 | 305.6149 | 0.0199 | 0 | 0 | 0.039801 | 305.8601 | 0.020432 | 0 | 0 | 0.040864 | 306.1053 | 0.020964 | 0 | 0 | 0.041928 | 306.187 | 0.021141 | 0 | 0 | 0.042283 | 306.4322 | 0.021673 | 0 | 0 | 0.043346 | 306.6774 | 0.022205 | 0 | 0 | 0.04441 | 306.8409 | 0.02256 | 0 | 0 | 0.045119 | 307.0861 | 0.023091 | 0 | 0 | 0.046183 | 307.2496 | 0.023446 | 0 | 0 | 0.046892 | 307.4131 | 0.023801 | 0 | 0 | 0.047601
2017-12-13 14:00 | 273.071 | 0.81391 |  | 286.7422 | 0 | 0 | 0 | 0 | 294.7999 | 0 | 0 | 0 | 0 | 301.3926 | 0.010742 | 0 | 0 | 0.021485 | 301.6368 | 0.011272 | 0 | 0 | 0.022544 | 301.7996 | 0.011625 | 0 | 0 | 0.02325 | 302.0438 | 0.012155 | 0 | 0 | 0.024309 | 302.2879 | 0.012684 | 0 | 0 | 0.025368 | 302.5321 | 0.013214 | 0 | 0 | 0.026428 | 302.8577 | 0.01392 | 0 | 0 | 0.02784 | 303.1019 | 0.01445 | 0 | 0 | 0.028899 | 303.2646 | 0.014803 | 0 | 0 | 0.029605 | 303.5088 | 0.015332 | 0 | 0 | 0.030665 | 303.6716 | 0.015685 | 0 | 0 | 0.031371 | 303.9158 | 0.016215 | 0 | 0 | 0.03243 | 304.16 | 0.016745 | 0 | 0 | 0.033489 | 304.3227 | 0.017098 | 0 | 0 | 0.034195 | 304.5669 | 0.017627 | 0 | 0 | 0.035255 | 304.8111 | 0.018157 | 0 | 0 | 0.036314 | 304.8925 | 0.018333 | 0 | 0 | 0.036667 | 305.1366 | 0.018863 | 0 | 0 | 0.037726 | 305.3808 | 0.019393 | 0 | 0 | 0.038785 | 305.5436 | 0.019746 | 0 | 0 | 0.039491 | 305.7878 | 0.020275 | 0 | 0 | 0.040551 | 305.9506 | 0.020628 | 0 | 0 | 0.041257 | 306.1133 | 0.020981 | 0 | 0 | 0.041963
2017-12-13 15:00 | 271.4428 | 0.80906 |  | 285.0325 | 0 | 0 | 0 | 0 | 293.0422 | 0 | 0 | 0 | 0 | 299.5956 | 0.0068445 | 0 | 0 | 0.013689 | 299.8383 | 0.007371 | 0 | 0 | 0.014742 | 300.0001 | 0.007722 | 0 | 0 | 0.015444 | 300.2429 | 0.0082484 | 0 | 0 | 0.016497 | 300.4856 | 0.0087749 | 0 | 0 | 0.01755 | 300.7283 | 0.0093013 | 0 | 0 | 0.018603 | 301.0519 | 0.010003 | 0 | 0 | 0.020007 | 301.2946 | 0.01053 | 0 | 0 | 0.021059 | 301.4565 | 0.010881 | 0 | 0 | 0.021761 | 301.6992 | 0.011407 | 0 | 0 | 0.022814 | 301.861 | 0.011758 | 0 | 0 | 0.023516 | 302.1037 | 0.012285 | 0 | 0 | 0.024569 | 302.3464 | 0.012811 | 0 | 0 | 0.025622 | 302.5082 | 0.013162 | 0 | 0 | 0.026324 | 302.751 | 0.013688 | 0 | 0 | 0.027377 | 302.9937 | 0.014215 | 0 | 0 | 0.02843 | 303.0746 | 0.01439 | 0 | 0 | 0.028781 | 303.3173 | 0.014917 | 0 | 0 | 0.029834 | 303.56 | 0.015443 | 0 | 0 | 0.030887 | 303.7218 | 0.015794 | 0 | 0 | 0.031589 | 303.9646 | 0.016321 | 0 | 0 | 0.032642 | 304.1264 | 0.016672 | 0 | 0 | 0.033343 | 304.2882 | 0.017023 | 0 | 0 | 0.034045
2017-12-13 16:00 | 274.6372 | 0.81858 |  | 288.3868 | 0 | 0 | 0 | 0 | 296.4908 | 0.0001102 | 0 | 0 | 0.00022041 | 303.1213 | 0.014492 | 0 | 0 | 0.028984 | 303.3669 | 0.015024 | 0 | 0 | 0.030049 | 303.5306 | 0.01538 | 0 | 0 | 0.030759 | 303.7762 | 0.015912 | 0 | 0 | 0.031824 | 304.0218 | 0.016445 | 0 | 0 | 0.03289 | 304.2673 | 0.016978 | 0 | 0 | 0.033955 | 304.5948 | 0.017688 | 0 | 0 | 0.035375 | 304.8404 | 0.01822 | 0 | 0 | 0.036441 | 305.0041 | 0.018575 | 0 | 0 | 0.037151 | 305.2496 | 0.019108 | 0 | 0 | 0.038216 | 305.4134 | 0.019463 | 0 | 0 | 0.038926 | 305.6589 | 0.019996 | 0 | 0 | 0.039992 | 305.9045 | 0.020529 | 0 | 0 | 0.041057 | 306.0682 | 0.020884 | 0 | 0 | 0.041767 | 306.3138 | 0.021416 | 0 | 0 | 0.042833 | 306.5594 | 0.021949 | 0 | 0 | 0.043898 | 306.6412 | 0.022126 | 0 | 0 | 0.044253 | 306.8868 | 0.022659 | 0 | 0 | 0.045318 | 307.1324 | 0.023192 | 0 | 0 | 0.046384 | 307.2961 | 0.023547 | 0 | 0 | 0.047094 | 307.5417 | 0.02408 | 0 | 0 | 0.048159 | 307.7054 | 0.024435 | 0 | 0 | 0.048869 | 307.8691 | 0.02479 | 0 | 0 | 0.049579
2017-12-13 17:00 | 288.9769 | 0.86132 |  | 303.4445 | 0.015193 | 0 | 0 | 0.030385 | 311.9716 | 0.033688 | 0 | 0 | 0.067376 | 318.9483 | 0.048821 | 0 | 0 | 0.097641 | 319.2067 | 0.049381 | 0 | 0 | 0.098762 | 319.379 | 0.049755 | 0 | 0 | 0.099509 | 319.6374 | 0.050315 | 0 | 0 | 0.10063 | 319.8958 | 0.050876 | 0 | 0 | 0.10175 | 320.1542 | 0.051436 | 0 | 0 | 0.10287 | 320.4987 | 0.052183 | 0 | 0 | 0.10437 | 320.7571 | 0.052744 | 0 | 0 | 0.10549 | 320.9294 | 0.053117 | 0 | 0 | 0.10623 | 321.1878 | 0.053678 | 0 | 0 | 0.10736 | 321.36 | 0.054052 | 0 | 0 | 0.1081 | 321.6184 | 0.054612 | 0 | 0 | 0.10922 | 321.8768 | 0.055172 | 0 | 0 | 0.11034 | 322.0491 | 0.055546 | 0 | 0 | 0.11109 | 322.3075 | 0.056107 | 0 | 0 | 0.11221 | 322.5659 | 0.056667 | 0 | 0 | 0.11333 | 322.652 | 0.056854 | 0 | 0 | 0.11371 | 322.9104 | 0.057414 | 0 | 0 | 0.11483 | 323.1688 | 0.057975 | 0 | 0 | 0.11595 | 323.3411 | 0.058348 | 0 | 0 | 0.1167 | 323.5995 | 0.058909 | 0 | 0 | 0.11782 | 323.7717 | 0.059283 | 0 | 0 | 0.11857 | 323.944 | 0.059656 | 0 | 0 | 0.11931
2017-12-13 18:00 | 286.1925 | 0.85302 |  | 300.5206 | 0.0088508 | 0 | 0 | 0.017702 | 308.9656 | 0.027168 | 0 | 0 | 0.054336 | 315.8751 | 0.042155 | 0 | 0 | 0.084309 | 316.131 | 0.04271 | 0 | 0 | 0.085419 | 316.3016 | 0.04308 | 0 | 0 | 0.086159 | 316.5575 | 0.043635 | 0 | 0 | 0.08727 | 316.8134 | 0.04419 | 0 | 0 | 0.08838 | 317.0693 | 0.044745 | 0 | 0 | 0.08949 | 317.4105 | 0.045485 | 0 | 0 | 0.09097 | 317.6664 | 0.04604 | 0 | 0 | 0.09208 | 317.837 | 0.04641 | 0 | 0 | 0.09282 | 318.0929 | 0.046965 | 0 | 0 | 0.09393 | 318.2635 | 0.047335 | 0 | 0 | 0.09467 | 318.5194 | 0.04789 | 0 | 0 | 0.095781 | 318.7753 | 0.048445 | 0 | 0 | 0.096891 | 318.9459 | 0.048815 | 0 | 0 | 0.097631 | 319.2018 | 0.04937 | 0 | 0 | 0.098741 | 319.4578 | 0.049926 | 0 | 0 | 0.099851 | 319.5431 | 0.050111 | 0 | 0 | 0.10022 | 319.799 | 0.050666 | 0 | 0 | 0.10133 | 320.0549 | 0.051221 | 0 | 0 | 0.10244 | 320.2255 | 0.051591 | 0 | 0 | 0.10318 | 320.4814 | 0.052146 | 0 | 0 | 0.10429 | 320.652 | 0.052516 | 0 | 0 | 0.10503 | 320.8226 | 0.052886 | 0 | 0 | 0.10577
2017-12-13 19:00 | 288.1278 | 0.85879 |  | 302.5528 | 0.013259 | 0 | 0 | 0.026518 | 311.0549 | 0.0317 | 0 | 0 | 0.063399 | 318.0111 | 0.046788 | 0 | 0 | 0.093576 | 318.2688 | 0.047347 | 0 | 0 | 0.094693 | 318.4405 | 0.047719 | 0 | 0 | 0.095438 | 318.6982 | 0.048278 | 0 | 0 | 0.096556 | 318.9558 | 0.048837 | 0 | 0 | 0.097674 | 319.2134 | 0.049396 | 0 | 0 | 0.098791 | 319.557 | 0.050141 | 0 | 0 | 0.10028 | 319.8146 | 0.050699 | 0 | 0 | 0.1014 | 319.9863 | 0.051072 | 0 | 0 | 0.10214 | 320.244 | 0.051631 | 0 | 0 | 0.10326 | 320.4157 | 0.052003 | 0 | 0 | 0.10401 | 320.6734 | 0.052562 | 0 | 0 | 0.10512 | 320.931 | 0.053121 | 0 | 0 | 0.10624 | 321.1028 | 0.053494 | 0 | 0 | 0.10699 | 321.3604 | 0.054052 | 0 | 0 | 0.1081 | 321.6181 | 0.054611 | 0 | 0 | 0.10922 | 321.7039 | 0.054797 | 0 | 0 | 0.10959 | 321.9616 | 0.055356 | 0 | 0 | 0.11071 | 322.2192 | 0.055915 | 0 | 0 | 0.11183 | 322.391 | 0.056288 | 0 | 0 | 0.11258 | 322.6486 | 0.056846 | 0 | 0 | 0.11369 | 322.8204 | 0.057219 | 0 | 0 | 0.11444 | 322.9921 | 0.057592 | 0 | 0 | 0.11518
2017-12-13 20:00 | 280.7255 | 0.83673 |  | 294.78 | 0 | 0 | 0 | 0 | 303.0636 | 0.014367 | 0 | 0 | 0.028733 | 309.8411 | 0.029067 | 0 | 0 | 0.058134 | 310.0921 | 0.029611 | 0 | 0 | 0.059223 | 310.2595 | 0.029974 | 0 | 0 | 0.059949 | 310.5105 | 0.030519 | 0 | 0 | 0.061038 | 310.7615 | 0.031063 | 0 | 0 | 0.062127 | 311.0125 | 0.031608 | 0 | 0 | 0.063216 | 311.3472 | 0.032334 | 0 | 0 | 0.064668 | 311.5982 | 0.032878 | 0 | 0 | 0.065756 | 311.7656 | 0.033241 | 0 | 0 | 0.066482 | 312.0166 | 0.033786 | 0 | 0 | 0.067571 | 312.184 | 0.034149 | 0 | 0 | 0.068297 | 312.435 | 0.034693 | 0 | 0 | 0.069386 | 312.686 | 0.035238 | 0 | 0 | 0.070475 | 312.8533 | 0.035601 | 0 | 0 | 0.071201 | 313.1044 | 0.036145 | 0 | 0 | 0.07229 | 313.3554 | 0.036689 | 0 | 0 | 0.073379 | 313.439 | 0.036871 | 0 | 0 | 0.073742 | 313.6901 | 0.037415 | 0 | 0 | 0.074831 | 313.9411 | 0.03796 | 0 | 0 | 0.07592 | 314.1084 | 0.038323 | 0 | 0 | 0.076646 | 314.3595 | 0.038867 | 0 | 0 | 0.077735 | 314.5268 | 0.03923 | 0 | 0 | 0.078461 | 314.6941 | 0.039593 | 0 | 0 | 0.079186
2017-12-13 21:00 | 254.2516 | 0.75782 |  | 266.9807 | 0 | 0 | 0 | 0 | 274.4831 | 0 | 0 | 0 | 0 | 280.6215 | 0 | 0 | 0 | 0 | 280.8488 | 0 | 0 | 0 | 0 | 281.0004 | 0 | 0 | 0 | 0 | 281.2277 | 0 | 0 | 0 | 0 | 281.4551 | 0 | 0 | 0 | 0 | 281.6824 | 0 | 0 | 0 | 0 | 281.9855 | 0 | 0 | 0 | 0 | 282.2129 | 0 | 0 | 0 | 0 | 282.3644 | 0 | 0 | 0 | 0 | 282.5918 | 0 | 0 | 0 | 0 | 282.7434 | 0 | 0 | 0 | 0 | 282.9707 | 0 | 0 | 0 | 0 | 283.198 | 0 | 0 | 0 | 0 | 283.3496 | 0 | 0 | 0 | 0 | 283.577 | 0 | 0 | 0 | 0 | 283.8043 | 0 | 0 | 0 | 0 | 283.8801 | 0 | 0 | 0 | 0 | 284.1074 | 0 | 0 | 0 | 0 | 284.3348 | 0 | 0 | 0 | 0 | 284.4863 | 0 | 0 | 0 | 0 | 284.7137 | 0 | 0 | 0 | 0 | 284.8653 | 0 | 0 | 0 | 0 | 285.0168 | 0 | 0 | 0 | 0
2017-12-13 22:00 | 270.0103 | 0.80479 |  | 283.5283 | 0 | 0 | 0 | 0 | 291.4957 | 0 | 0 | 0 | 0 | 298.0146 | 0.0034152 | 0 | 0 | 0.0068304 | 298.256 | 0.0039389 | 0 | 0 | 0.0078778 | 298.4169 | 0.004288 | 0 | 0 | 0.008576 | 298.6584 | 0.0048117 | 0 | 0 | 0.0096234 | 298.8998 | 0.0053354 | 0 | 0 | 0.010671 | 299.1413 | 0.005859 | 0 | 0 | 0.011718 | 299.4632 | 0.0065573 | 0 | 0 | 0.013115 | 299.7046 | 0.0070809 | 0 | 0 | 0.014162 | 299.8656 | 0.0074301 | 0 | 0 | 0.01486 | 300.107 | 0.0079537 | 0 | 0 | 0.015907 | 300.268 | 0.0083029 | 0 | 0 | 0.016606 | 300.5094 | 0.0088265 | 0 | 0 | 0.017653 | 300.7508 | 0.0093502 | 0 | 0 | 0.0187 | 300.9118 | 0.0096993 | 0 | 0 | 0.019399 | 301.1532 | 0.010223 | 0 | 0 | 0.020446 | 301.3947 | 0.010747 | 0 | 0 | 0.021493 | 301.4752 | 0.010921 | 0 | 0 | 0.021843 | 301.7166 | 0.011445 | 0 | 0 | 0.02289 | 301.958 | 0.011969 | 0 | 0 | 0.023937 | 302.119 | 0.012318 | 0 | 0 | 0.024635 | 302.3604 | 0.012841 | 0 | 0 | 0.025683 | 302.5214 | 0.013191 | 0 | 0 | 0.026381 | 302.6823 | 0.01354 | 0 | 0 | 0.027079
2017-12-13 23:00 | 282.0586 | 0.8407 |  | 296.1798 | 0 | 0 | 0 | 0 | 304.5028 | 0.017488 | 0 | 0 | 0.034976 | 311.3125 | 0.032258 | 0 | 0 | 0.064517 | 311.5647 | 0.032805 | 0 | 0 | 0.065611 | 311.7329 | 0.03317 | 0 | 0 | 0.06634 | 311.9851 | 0.033717 | 0 | 0 | 0.067434 | 312.2373 | 0.034264 | 0 | 0 | 0.068529 | 312.4895 | 0.034811 | 0 | 0 | 0.069623 | 312.8258 | 0.035541 | 0 | 0 | 0.071081 | 313.078 | 0.036088 | 0 | 0 | 0.072176 | 313.2461 | 0.036452 | 0 | 0 | 0.072905 | 313.4983 | 0.037 | 0 | 0 | 0.073999 | 313.6665 | 0.037364 | 0 | 0 | 0.074728 | 313.9187 | 0.037911 | 0 | 0 | 0.075823 | 314.1709 | 0.038458 | 0 | 0 | 0.076917 | 314.339 | 0.038823 | 0 | 0 | 0.077646 | 314.5912 | 0.03937 | 0 | 0 | 0.07874 | 314.8435 | 0.039917 | 0 | 0 | 0.079834 | 314.9275 | 0.040099 | 0 | 0 | 0.080199 | 315.1797 | 0.040646 | 0 | 0 | 0.081293 | 315.4319 | 0.041194 | 0 | 0 | 0.082387 | 315.6001 | 0.041558 | 0 | 0 | 0.083116 | 315.8523 | 0.042105 | 0 | 0 | 0.084211 | 316.0204 | 0.04247 | 0 | 0 | 0.08494 | 316.1886 | 0.042835 | 0 | 0 | 0.085669
2017-12-14 | 277.2957 | 0.82651 |  | 291.1785 | 0 | 0 | 0 | 0 | 299.3609 | 0.0063354 | 0 | 0 | 0.012671 | 306.0556 | 0.020856 | 0 | 0 | 0.041712 | 306.3035 | 0.021394 | 0 | 0 | 0.042788 | 306.4688 | 0.021753 | 0 | 0 | 0.043505 | 306.7168 | 0.02229 | 0 | 0 | 0.044581 | 306.9647 | 0.022828 | 0 | 0 | 0.045656 | 307.2127 | 0.023366 | 0 | 0 | 0.046732 | 307.5433 | 0.024083 | 0 | 0 | 0.048166 | 307.7913 | 0.024621 | 0 | 0 | 0.049242 | 307.9566 | 0.024979 | 0 | 0 | 0.049959 | 308.2045 | 0.025517 | 0 | 0 | 0.051034 | 308.3698 | 0.025876 | 0 | 0 | 0.051751 | 308.6178 | 0.026414 | 0 | 0 | 0.052827 | 308.8657 | 0.026951 | 0 | 0 | 0.053903 | 309.031 | 0.02731 | 0 | 0 | 0.05462 | 309.279 | 0.027848 | 0 | 0 | 0.055695 | 309.5269 | 0.028386 | 0 | 0 | 0.056771 | 309.6096 | 0.028565 | 0 | 0 | 0.05713 | 309.8575 | 0.029103 | 0 | 0 | 0.058205 | 310.1055 | 0.02964 | 0 | 0 | 0.059281 | 310.2708 | 0.029999 | 0 | 0 | 0.059998 | 310.5187 | 0.030537 | 0 | 0 | 0.061074 | 310.684 | 0.030895 | 0 | 0 | 0.061791 | 310.8493 | 0.031254 | 0 | 0 | 0.062508
2017-12-14 01:00 | 278.2607 | 0.82938 |  | 292.1918 | 0 | 0 | 0 | 0 | 300.4027 | 0.008595 | 0 | 0 | 0.01719 | 307.1207 | 0.023166 | 0 | 0 | 0.046333 | 307.3695 | 0.023706 | 0 | 0 | 0.047412 | 307.5354 | 0.024066 | 0 | 0 | 0.048132 | 307.7842 | 0.024606 | 0 | 0 | 0.049211 | 308.033 | 0.025145 | 0 | 0 | 0.05029 | 308.2818 | 0.025685 | 0 | 0 | 0.05137 | 308.6136 | 0.026404 | 0 | 0 | 0.052809 | 308.8624 | 0.026944 | 0 | 0 | 0.053888 | 309.0283 | 0.027304 | 0 | 0 | 0.054608 | 309.2771 | 0.027844 | 0 | 0 | 0.055687 | 309.443 | 0.028203 | 0 | 0 | 0.056407 | 309.6918 | 0.028743 | 0 | 0 | 0.057486 | 309.9406 | 0.029283 | 0 | 0 | 0.058566 | 310.1065 | 0.029643 | 0 | 0 | 0.059285 | 310.3553 | 0.030182 | 0 | 0 | 0.060364 | 310.6041 | 0.030722 | 0 | 0 | 0.061444 | 310.687 | 0.030902 | 0 | 0 | 0.061804 | 310.9358 | 0.031441 | 0 | 0 | 0.062883 | 311.1847 | 0.031981 | 0 | 0 | 0.063962 | 311.3505 | 0.032341 | 0 | 0 | 0.064682 | 311.5994 | 0.032881 | 0 | 0 | 0.065761 | 311.7652 | 0.03324 | 0 | 0 | 0.066481 | 311.9311 | 0.0336 | 0 | 0 | 0.0672
2017-12-14 02:00 | 282.1908 | 0.8411 |  | 296.3186 | 0 | 0 | 0 | 0 | 304.6454 | 0.017798 | 0 | 0 | 0.035595 | 311.4583 | 0.032575 | 0 | 0 | 0.06515 | 311.7107 | 0.033122 | 0 | 0 | 0.066244 | 311.8789 | 0.033487 | 0 | 0 | 0.066974 | 312.1312 | 0.034034 | 0 | 0 | 0.068068 | 312.3835 | 0.034582 | 0 | 0 | 0.069163 | 312.6359 | 0.035129 | 0 | 0 | 0.070258 | 312.9723 | 0.035859 | 0 | 0 | 0.071717 | 313.2246 | 0.036406 | 0 | 0 | 0.072812 | 313.3929 | 0.036771 | 0 | 0 | 0.073541 | 313.6452 | 0.037318 | 0 | 0 | 0.074636 | 313.8134 | 0.037683 | 0 | 0 | 0.075366 | 314.0657 | 0.03823 | 0 | 0 | 0.07646 | 314.3181 | 0.038778 | 0 | 0 | 0.077555 | 314.4863 | 0.039142 | 0 | 0 | 0.078285 | 314.7386 | 0.03969 | 0 | 0 | 0.079379 | 314.9909 | 0.040237 | 0 | 0 | 0.080474 | 315.075 | 0.040419 | 0 | 0 | 0.080839 | 315.3274 | 0.040967 | 0 | 0 | 0.081933 | 315.5797 | 0.041514 | 0 | 0 | 0.083028 | 315.7479 | 0.041879 | 0 | 0 | 0.083758 | 316.0003 | 0.042426 | 0 | 0 | 0.084852 | 316.1685 | 0.042791 | 0 | 0 | 0.085582 | 316.3367 | 0.043156 | 0 | 0 | 0.086312
2017-12-14 03:00 | 279.1165 | 0.83193 |  | 293.0904 | 0 | 0 | 0 | 0 | 301.3266 | 0.010599 | 0 | 0 | 0.021198 | 308.0652 | 0.025215 | 0 | 0 | 0.05043 | 308.3148 | 0.025756 | 0 | 0 | 0.051513 | 308.4812 | 0.026117 | 0 | 0 | 0.052235 | 308.7308 | 0.026659 | 0 | 0 | 0.053317 | 308.9804 | 0.0272 | 0 | 0 | 0.0544 | 309.2299 | 0.027741 | 0 | 0 | 0.055483 | 309.5627 | 0.028463 | 0 | 0 | 0.056926 | 309.8123 | 0.029004 | 0 | 0 | 0.058009 | 309.9787 | 0.029365 | 0 | 0 | 0.058731 | 310.2283 | 0.029907 | 0 | 0 | 0.059813 | 310.3946 | 0.030268 | 0 | 0 | 0.060535 | 310.6442 | 0.030809 | 0 | 0 | 0.061618 | 310.8938 | 0.03135 | 0 | 0 | 0.062701 | 311.0602 | 0.031711 | 0 | 0 | 0.063422 | 311.3098 | 0.032253 | 0 | 0 | 0.064505 | 311.5593 | 0.032794 | 0 | 0 | 0.065588 | 311.6425 | 0.032974 | 0 | 0 | 0.065949 | 311.8921 | 0.033516 | 0 | 0 | 0.067031 | 312.1417 | 0.034057 | 0 | 0 | 0.068114 | 312.3081 | 0.034418 | 0 | 0 | 0.068836 | 312.5577 | 0.034959 | 0 | 0 | 0.069918 | 312.7241 | 0.03532 | 0 | 0 | 0.07064 | 312.8904 | 0.035681 | 0 | 0 | 0.071362
2017-12-14 04:00 | 281.5569 | 0.83921 |  | 295.653 | 0 | 0 | 0 | 0 | 303.9611 | 0.016313 | 0 | 0 | 0.032627 | 310.7587 | 0.031057 | 0 | 0 | 0.062115 | 311.0105 | 0.031603 | 0 | 0 | 0.063207 | 311.1783 | 0.031967 | 0 | 0 | 0.063935 | 311.4301 | 0.032513 | 0 | 0 | 0.065027 | 311.6818 | 0.03306 | 0 | 0 | 0.066119 | 311.9336 | 0.033606 | 0 | 0 | 0.067211 | 312.2693 | 0.034334 | 0 | 0 | 0.068667 | 312.5211 | 0.03488 | 0 | 0 | 0.06976 | 312.6889 | 0.035244 | 0 | 0 | 0.070488 | 312.9407 | 0.03579 | 0 | 0 | 0.07158 | 313.1085 | 0.036154 | 0 | 0 | 0.072308 | 313.3603 | 0.0367 | 0 | 0 | 0.0734 | 313.612 | 0.037246 | 0 | 0 | 0.074492 | 313.7799 | 0.03761 | 0 | 0 | 0.07522 | 314.0316 | 0.038156 | 0 | 0 | 0.076312 | 314.2834 | 0.038702 | 0 | 0 | 0.077405 | 314.3673 | 0.038884 | 0 | 0 | 0.077769 | 314.6191 | 0.03943 | 0 | 0 | 0.078861 | 314.8708 | 0.039976 | 0 | 0 | 0.079953 | 315.0387 | 0.040341 | 0 | 0 | 0.080681 | 315.2904 | 0.040887 | 0 | 0 | 0.081773 | 315.4583 | 0.041251 | 0 | 0 | 0.082501 | 315.6261 | 0.041615 | 0 | 0 | 0.083229
2017-12-14 05:00 | 279.1857 | 0.83214 |  | 293.1631 | 0 | 0 | 0 | 0 | 301.4013 | 0.010761 | 0 | 0 | 0.021522 | 308.1416 | 0.025381 | 0 | 0 | 0.050762 | 308.3913 | 0.025922 | 0 | 0 | 0.051845 | 308.5577 | 0.026283 | 0 | 0 | 0.052567 | 308.8073 | 0.026825 | 0 | 0 | 0.05365 | 309.057 | 0.027366 | 0 | 0 | 0.054732 | 309.3066 | 0.027908 | 0 | 0 | 0.055815 | 309.6395 | 0.02863 | 0 | 0 | 0.057259 | 309.8891 | 0.029171 | 0 | 0 | 0.058342 | 310.0556 | 0.029532 | 0 | 0 | 0.059064 | 310.3052 | 0.030074 | 0 | 0 | 0.060147 | 310.4716 | 0.030435 | 0 | 0 | 0.060869 | 310.7213 | 0.030976 | 0 | 0 | 0.061952 | 310.9709 | 0.031518 | 0 | 0 | 0.063035 | 311.1373 | 0.031879 | 0 | 0 | 0.063757 | 311.387 | 0.03242 | 0 | 0 | 0.06484 | 311.6366 | 0.032961 | 0 | 0 | 0.065923 | 311.7198 | 0.033142 | 0 | 0 | 0.066284 | 311.9695 | 0.033683 | 0 | 0 | 0.067367 | 312.2191 | 0.034225 | 0 | 0 | 0.06845 | 312.3855 | 0.034586 | 0 | 0 | 0.069172 | 312.6352 | 0.035127 | 0 | 0 | 0.070255 | 312.8016 | 0.035488 | 0 | 0 | 0.070977 | 312.968 | 0.035849 | 0 | 0 | 0.071699
2017-12-14 06:00 | 285.251 | 0.85022 |  | 299.5321 | 0.0067067 | 0 | 0 | 0.013413 | 307.9492 | 0.024964 | 0 | 0 | 0.049927 | 314.836 | 0.039901 | 0 | 0 | 0.079802 | 315.0911 | 0.040454 | 0 | 0 | 0.080908 | 315.2611 | 0.040823 | 0 | 0 | 0.081646 | 315.5162 | 0.041376 | 0 | 0 | 0.082752 | 315.7712 | 0.041929 | 0 | 0 | 0.083859 | 316.0263 | 0.042483 | 0 | 0 | 0.084965 | 316.3664 | 0.04322 | 0 | 0 | 0.086441 | 316.6215 | 0.043774 | 0 | 0 | 0.087547 | 316.7915 | 0.044142 | 0 | 0 | 0.088285 | 317.0466 | 0.044696 | 0 | 0 | 0.089391 | 317.2166 | 0.045064 | 0 | 0 | 0.090129 | 317.4717 | 0.045618 | 0 | 0 | 0.091235 | 317.7267 | 0.046171 | 0 | 0 | 0.092342 | 317.8968 | 0.04654 | 0 | 0 | 0.09308 | 318.1519 | 0.047093 | 0 | 0 | 0.094186 | 318.4069 | 0.047646 | 0 | 0 | 0.095292 | 318.4919 | 0.047831 | 0 | 0 | 0.095661 | 318.747 | 0.048384 | 0 | 0 | 0.096768 | 319.0021 | 0.048937 | 0 | 0 | 0.097874 | 319.1721 | 0.049306 | 0 | 0 | 0.098612 | 319.4272 | 0.049859 | 0 | 0 | 0.099718 | 319.5972 | 0.050228 | 0 | 0 | 0.10046 | 319.7673 | 0.050597 | 0 | 0 | 0.10119
2017-12-14 07:00 | 279.6136 | 0.83342 |  | 293.6124 | 0 | 0 | 0 | 0 | 301.8632 | 0.011763 | 0 | 0 | 0.023526 | 308.6139 | 0.026405 | 0 | 0 | 0.05281 | 308.8639 | 0.026948 | 0 | 0 | 0.053895 | 309.0306 | 0.027309 | 0 | 0 | 0.054618 | 309.2806 | 0.027851 | 0 | 0 | 0.055703 | 309.5307 | 0.028394 | 0 | 0 | 0.056787 | 309.7807 | 0.028936 | 0 | 0 | 0.057872 | 310.1141 | 0.029659 | 0 | 0 | 0.059318 | 310.3641 | 0.030201 | 0 | 0 | 0.060403 | 310.5308 | 0.030563 | 0 | 0 | 0.061126 | 310.7808 | 0.031105 | 0 | 0 | 0.06221 | 310.9475 | 0.031467 | 0 | 0 | 0.062933 | 311.1975 | 0.032009 | 0 | 0 | 0.064018 | 311.4475 | 0.032551 | 0 | 0 | 0.065103 | 311.6142 | 0.032913 | 0 | 0 | 0.065826 | 311.8642 | 0.033455 | 0 | 0 | 0.06691 | 312.1143 | 0.033997 | 0 | 0 | 0.067995 | 312.1976 | 0.034178 | 0 | 0 | 0.068356 | 312.4476 | 0.034721 | 0 | 0 | 0.069441 | 312.6976 | 0.035263 | 0 | 0 | 0.070526 | 312.8643 | 0.035624 | 0 | 0 | 0.071249 | 313.1144 | 0.036167 | 0 | 0 | 0.072333 | 313.281 | 0.036528 | 0 | 0 | 0.073056 | 313.4477 | 0.03689 | 0 | 0 | 0.073779
2017-12-14 08:00 | 283.2828 | 0.84435 |  | 297.4653 | 0.0022239 | 0 | 0 | 0.0044477 | 305.8244 | 0.020355 | 0 | 0 | 0.040709 | 312.6636 | 0.035189 | 0 | 0 | 0.070378 | 312.9169 | 0.035738 | 0 | 0 | 0.071477 | 313.0858 | 0.036105 | 0 | 0 | 0.07221 | 313.3391 | 0.036654 | 0 | 0 | 0.073308 | 313.5924 | 0.037204 | 0 | 0 | 0.074407 | 313.8457 | 0.037753 | 0 | 0 | 0.075506 | 314.1835 | 0.038486 | 0 | 0 | 0.076971 | 314.4368 | 0.039035 | 0 | 0 | 0.07807 | 314.6056 | 0.039401 | 0 | 0 | 0.078803 | 314.8589 | 0.039951 | 0 | 0 | 0.079901 | 315.0278 | 0.040317 | 0 | 0 | 0.080634 | 315.2811 | 0.040866 | 0 | 0 | 0.081733 | 315.5344 | 0.041416 | 0 | 0 | 0.082832 | 315.7033 | 0.041782 | 0 | 0 | 0.083564 | 315.9566 | 0.042332 | 0 | 0 | 0.084663 | 316.2099 | 0.042881 | 0 | 0 | 0.085762 | 316.2943 | 0.043064 | 0 | 0 | 0.086128 | 316.5477 | 0.043613 | 0 | 0 | 0.087227 | 316.801 | 0.044163 | 0 | 0 | 0.088326 | 316.9698 | 0.044529 | 0 | 0 | 0.089058 | 317.2231 | 0.045079 | 0 | 0 | 0.090157 | 317.392 | 0.045445 | 0 | 0 | 0.09089 | 317.5609 | 0.045811 | 0 | 0 | 0.091622
2017-12-14 09:00 | 285.0481 | 0.84961 |  | 299.319 | 0.0062444 | 0 | 0 | 0.012489 | 307.7301 | 0.024488 | 0 | 0 | 0.048977 | 314.612 | 0.039415 | 0 | 0 | 0.07883 | 314.8669 | 0.039968 | 0 | 0 | 0.079936 | 315.0368 | 0.040336 | 0 | 0 | 0.080673 | 315.2917 | 0.040889 | 0 | 0 | 0.081779 | 315.5466 | 0.041442 | 0 | 0 | 0.082884 | 315.8015 | 0.041995 | 0 | 0 | 0.08399 | 316.1413 | 0.042732 | 0 | 0 | 0.085464 | 316.3962 | 0.043285 | 0 | 0 | 0.08657 | 316.5661 | 0.043654 | 0 | 0 | 0.087307 | 316.821 | 0.044206 | 0 | 0 | 0.088413 | 316.9909 | 0.044575 | 0 | 0 | 0.08915 | 317.2458 | 0.045128 | 0 | 0 | 0.090256 | 317.5007 | 0.045681 | 0 | 0 | 0.091361 | 317.6706 | 0.046049 | 0 | 0 | 0.092098 | 317.9255 | 0.046602 | 0 | 0 | 0.093204 | 318.1804 | 0.047155 | 0 | 0 | 0.09431 | 318.2653 | 0.047339 | 0 | 0 | 0.094678 | 318.5202 | 0.047892 | 0 | 0 | 0.095784 | 318.7751 | 0.048445 | 0 | 0 | 0.09689 | 318.945 | 0.048813 | 0 | 0 | 0.097627 | 319.1999 | 0.049366 | 0 | 0 | 0.098733 | 319.3698 | 0.049735 | 0 | 0 | 0.09947 | 319.5398 | 0.050103 | 0 | 0 | 0.10021
2017-12-14 10:00 | 295.1711 | 0.87979 |  | 309.9488 | 0.029301 | 0 | 0 | 0.058601 | 318.6587 | 0.048192 | 0 | 0 | 0.096385 | 325.7849 | 0.063649 | 0 | 0 | 0.1273 | 326.0489 | 0.064222 | 0 | 0 | 0.12844 | 326.2248 | 0.064603 | 0 | 0 | 0.12921 | 326.4887 | 0.065176 | 0 | 0 | 0.13035 | 326.7527 | 0.065748 | 0 | 0 | 0.1315 | 327.0166 | 0.066321 | 0 | 0 | 0.13264 | 327.3685 | 0.067084 | 0 | 0 | 0.13417 | 327.6325 | 0.067656 | 0 | 0 | 0.13531 | 327.8084 | 0.068038 | 0 | 0 | 0.13608 | 328.0724 | 0.068611 | 0 | 0 | 0.13722 | 328.2483 | 0.068992 | 0 | 0 | 0.13798 | 328.5123 | 0.069565 | 0 | 0 | 0.13913 | 328.7762 | 0.070137 | 0 | 0 | 0.14027 | 328.9522 | 0.070519 | 0 | 0 | 0.14104 | 329.2161 | 0.071091 | 0 | 0 | 0.14218 | 329.48 | 0.071664 | 0 | 0 | 0.14333 | 329.568 | 0.071855 | 0 | 0 | 0.14371 | 329.8319 | 0.072427 | 0 | 0 | 0.14485 | 330.0959 | 0.073 | 0 | 0 | 0.146 | 330.2718 | 0.073381 | 0 | 0 | 0.14676 | 330.5358 | 0.073954 | 0 | 0 | 0.14791 | 330.7117 | 0.074335 | 0 | 0 | 0.14867 | 330.8877 | 0.074717 | 0 | 0 | 0.14943
2017-12-14 11:00 | 295.1328 | 0.87967 |  | 309.9085 | 0.029213 | 0 | 0 | 0.058426 | 318.6173 | 0.048103 | 0 | 0 | 0.096205 | 325.7426 | 0.063557 | 0 | 0 | 0.12711 | 326.0065 | 0.06413 | 0 | 0 | 0.12826 | 326.1825 | 0.064511 | 0 | 0 | 0.12902 | 326.4464 | 0.065084 | 0 | 0 | 0.13017 | 326.7103 | 0.065656 | 0 | 0 | 0.13131 | 326.9742 | 0.066229 | 0 | 0 | 0.13246 | 327.326 | 0.066992 | 0 | 0 | 0.13398 | 327.5899 | 0.067564 | 0 | 0 | 0.13513 | 327.7659 | 0.067946 | 0 | 0 | 0.13589 | 328.0298 | 0.068518 | 0 | 0 | 0.13704 | 328.2057 | 0.0689 | 0 | 0 | 0.1378 | 328.4696 | 0.069472 | 0 | 0 | 0.13894 | 328.7335 | 0.070045 | 0 | 0 | 0.14009 | 328.9094 | 0.070426 | 0 | 0 | 0.14085 | 329.1733 | 0.070999 | 0 | 0 | 0.142 | 329.4372 | 0.071571 | 0 | 0 | 0.14314 | 329.5252 | 0.071762 | 0 | 0 | 0.14352 | 329.7891 | 0.072334 | 0 | 0 | 0.14467 | 330.053 | 0.072907 | 0 | 0 | 0.14581 | 330.229 | 0.073288 | 0 | 0 | 0.14658 | 330.4929 | 0.073861 | 0 | 0 | 0.14772 | 330.6688 | 0.074242 | 0 | 0 | 0.14848 | 330.8447 | 0.074624 | 0 | 0 | 0.14925
2017-12-14 12:00 | 297.0601 | 0.88542 |  | 311.9323 | 0.033603 | 0 | 0 | 0.067206 | 320.6979 | 0.052615 | 0 | 0 | 0.10523 | 327.8698 | 0.068171 | 0 | 0 | 0.13634 | 328.1354 | 0.068747 | 0 | 0 | 0.13749 | 328.3125 | 0.069131 | 0 | 0 | 0.13826 | 328.5781 | 0.069708 | 0 | 0 | 0.13942 | 328.8438 | 0.070284 | 0 | 0 | 0.14057 | 329.1094 | 0.07086 | 0 | 0 | 0.14172 | 329.4636 | 0.071628 | 0 | 0 | 0.14326 | 329.7292 | 0.072204 | 0 | 0 | 0.14441 | 329.9063 | 0.072588 | 0 | 0 | 0.14518 | 330.1719 | 0.073164 | 0 | 0 | 0.14633 | 330.349 | 0.073549 | 0 | 0 | 0.1471 | 330.6146 | 0.074125 | 0 | 0 | 0.14825 | 330.8802 | 0.074701 | 0 | 0 | 0.1494 | 331.0573 | 0.075085 | 0 | 0 | 0.15017 | 331.3229 | 0.075661 | 0 | 0 | 0.15132 | 331.5886 | 0.076237 | 0 | 0 | 0.15247 | 331.6771 | 0.076429 | 0 | 0 | 0.15286 | 331.9427 | 0.077005 | 0 | 0 | 0.15401 | 332.2083 | 0.077582 | 0 | 0 | 0.15516 | 332.3854 | 0.077966 | 0 | 0 | 0.15593 | 332.6511 | 0.078542 | 0 | 0 | 0.15708 | 332.8281 | 0.078926 | 0 | 0 | 0.15785 | 333.0052 | 0.07931 | 0 | 0 | 0.15862
2017-12-14 13:00 | 293.7842 | 0.87565 |  | 308.4924 | 0.026142 | 0 | 0 | 0.052284 | 317.1614 | 0.044945 | 0 | 0 | 0.089889 | 324.2542 | 0.060329 | 0 | 0 | 0.12066 | 324.5169 | 0.060899 | 0 | 0 | 0.1218 | 324.692 | 0.061279 | 0 | 0 | 0.12256 | 324.9547 | 0.061848 | 0 | 0 | 0.1237 | 325.2174 | 0.062418 | 0 | 0 | 0.12484 | 325.4801 | 0.062988 | 0 | 0 | 0.12598 | 325.8304 | 0.063748 | 0 | 0 | 0.1275 | 326.0931 | 0.064317 | 0 | 0 | 0.12863 | 326.2682 | 0.064697 | 0 | 0 | 0.12939 | 326.5309 | 0.065267 | 0 | 0 | 0.13053 | 326.706 | 0.065647 | 0 | 0 | 0.13129 | 326.9687 | 0.066217 | 0 | 0 | 0.13243 | 327.2314 | 0.066787 | 0 | 0 | 0.13357 | 327.4065 | 0.067166 | 0 | 0 | 0.13433 | 327.6692 | 0.067736 | 0 | 0 | 0.13547 | 327.9319 | 0.068306 | 0 | 0 | 0.13661 | 328.0195 | 0.068496 | 0 | 0 | 0.13699 | 328.2822 | 0.069066 | 0 | 0 | 0.13813 | 328.5449 | 0.069636 | 0 | 0 | 0.13927 | 328.72 | 0.070015 | 0 | 0 | 0.14003 | 328.9827 | 0.070585 | 0 | 0 | 0.14117 | 329.1578 | 0.070965 | 0 | 0 | 0.14193 | 329.333 | 0.071345 | 0 | 0 | 0.14269
2017-12-14 14:00 | 289.2591 | 0.86217 |  | 303.7408 | 0.015835 | 0 | 0 | 0.031671 | 312.2762 | 0.034349 | 0 | 0 | 0.068698 | 319.2598 | 0.049496 | 0 | 0 | 0.098992 | 319.5184 | 0.050057 | 0 | 0 | 0.10011 | 319.6908 | 0.050431 | 0 | 0 | 0.10086 | 319.9495 | 0.050992 | 0 | 0 | 0.10198 | 320.2081 | 0.051553 | 0 | 0 | 0.10311 | 320.4668 | 0.052114 | 0 | 0 | 0.10423 | 320.8117 | 0.052862 | 0 | 0 | 0.10572 | 321.0703 | 0.053423 | 0 | 0 | 0.10685 | 321.2427 | 0.053797 | 0 | 0 | 0.10759 | 321.5014 | 0.054358 | 0 | 0 | 0.10872 | 321.6738 | 0.054732 | 0 | 0 | 0.10946 | 321.9325 | 0.055293 | 0 | 0 | 0.11059 | 322.1911 | 0.055854 | 0 | 0 | 0.11171 | 322.3636 | 0.056228 | 0 | 0 | 0.11246 | 322.6222 | 0.056789 | 0 | 0 | 0.11358 | 322.8809 | 0.05735 | 0 | 0 | 0.1147 | 322.9671 | 0.057537 | 0 | 0 | 0.11507 | 323.2257 | 0.058098 | 0 | 0 | 0.1162 | 323.4844 | 0.058659 | 0 | 0 | 0.11732 | 323.6568 | 0.059033 | 0 | 0 | 0.11807 | 323.9155 | 0.059594 | 0 | 0 | 0.11919 | 324.0879 | 0.059968 | 0 | 0 | 0.11994 | 324.2603 | 0.060342 | 0 | 0 | 0.12068
2017-12-14 15:00 | 285.1065 | 0.84979 |  | 299.3802 | 0.0063774 | 0 | 0 | 0.012755 | 307.7931 | 0.024625 | 0 | 0 | 0.04925 | 314.6764 | 0.039555 | 0 | 0 | 0.07911 | 314.9313 | 0.040108 | 0 | 0 | 0.080215 | 315.1013 | 0.040476 | 0 | 0 | 0.080953 | 315.3562 | 0.041029 | 0 | 0 | 0.082059 | 315.6112 | 0.041582 | 0 | 0 | 0.083165 | 315.8661 | 0.042135 | 0 | 0 | 0.08427 | 316.206 | 0.042873 | 0 | 0 | 0.085745 | 316.461 | 0.043425 | 0 | 0 | 0.086851 | 316.6309 | 0.043794 | 0 | 0 | 0.087588 | 316.8859 | 0.044347 | 0 | 0 | 0.088694 | 317.0558 | 0.044716 | 0 | 0 | 0.089431 | 317.3108 | 0.045269 | 0 | 0 | 0.090537 | 317.5657 | 0.045822 | 0 | 0 | 0.091643 | 317.7356 | 0.04619 | 0 | 0 | 0.092381 | 317.9906 | 0.046743 | 0 | 0 | 0.093486 | 318.2455 | 0.047296 | 0 | 0 | 0.094592 | 318.3305 | 0.04748 | 0 | 0 | 0.094961 | 318.5854 | 0.048033 | 0 | 0 | 0.096067 | 318.8404 | 0.048586 | 0 | 0 | 0.097173 | 319.0103 | 0.048955 | 0 | 0 | 0.09791 | 319.2653 | 0.049508 | 0 | 0 | 0.099016 | 319.4352 | 0.049877 | 0 | 0 | 0.099753 | 319.6052 | 0.050245 | 0 | 0 | 0.10049
2017-12-14 16:00 | 287.8984 | 0.85811 |  | 302.3119 | 0.012736 | 0 | 0 | 0.025472 | 310.8072 | 0.031162 | 0 | 0 | 0.062325 | 317.7579 | 0.046239 | 0 | 0 | 0.092477 | 318.0153 | 0.046797 | 0 | 0 | 0.093594 | 318.1869 | 0.047169 | 0 | 0 | 0.094338 | 318.4444 | 0.047727 | 0 | 0 | 0.095455 | 318.7018 | 0.048286 | 0 | 0 | 0.096572 | 318.9592 | 0.048844 | 0 | 0 | 0.097688 | 319.3025 | 0.049589 | 0 | 0 | 0.099177 | 319.5599 | 0.050147 | 0 | 0 | 0.10029 | 319.7315 | 0.050519 | 0 | 0 | 0.10104 | 319.989 | 0.051078 | 0 | 0 | 0.10216 | 320.1606 | 0.05145 | 0 | 0 | 0.1029 | 320.418 | 0.052008 | 0 | 0 | 0.10402 | 320.6755 | 0.052567 | 0 | 0 | 0.10513 | 320.8471 | 0.052939 | 0 | 0 | 0.10588 | 321.1045 | 0.053497 | 0 | 0 | 0.10699 | 321.3619 | 0.054056 | 0 | 0 | 0.10811 | 321.4478 | 0.054242 | 0 | 0 | 0.10848 | 321.7052 | 0.0548 | 0 | 0 | 0.1096 | 321.9626 | 0.055359 | 0 | 0 | 0.11072 | 322.1342 | 0.055731 | 0 | 0 | 0.11146 | 322.3917 | 0.056289 | 0 | 0 | 0.11258 | 322.5633 | 0.056661 | 0 | 0 | 0.11332 | 322.7349 | 0.057034 | 0 | 0 | 0.11407
2017-12-14 17:00 | 300.1264 | 0.89456 |  | 315.1521 | 0.040587 | 0 | 0 | 0.081173 | 324.0082 | 0.059795 | 0 | 0 | 0.11959 | 331.2541 | 0.075512 | 0 | 0 | 0.15102 | 331.5225 | 0.076094 | 0 | 0 | 0.15219 | 331.7014 | 0.076482 | 0 | 0 | 0.15296 | 331.9698 | 0.077064 | 0 | 0 | 0.15413 | 332.2381 | 0.077646 | 0 | 0 | 0.15529 | 332.5065 | 0.078228 | 0 | 0 | 0.15646 | 332.8643 | 0.079004 | 0 | 0 | 0.15801 | 333.1327 | 0.079586 | 0 | 0 | 0.15917 | 333.3116 | 0.079975 | 0 | 0 | 0.15995 | 333.58 | 0.080557 | 0 | 0 | 0.16111 | 333.7589 | 0.080945 | 0 | 0 | 0.16189 | 334.0273 | 0.081527 | 0 | 0 | 0.16305 | 334.2956 | 0.082109 | 0 | 0 | 0.16422 | 334.4745 | 0.082497 | 0 | 0 | 0.16499 | 334.7429 | 0.083079 | 0 | 0 | 0.16616 | 335.0113 | 0.083661 | 0 | 0 | 0.16732 | 335.1007 | 0.083855 | 0 | 0 | 0.16771 | 335.3691 | 0.084437 | 0 | 0 | 0.16887 | 335.6375 | 0.085019 | 0 | 0 | 0.17004 | 335.8164 | 0.085407 | 0 | 0 | 0.17081 | 336.0847 | 0.085989 | 0 | 0 | 0.17198 | 336.2636 | 0.086377 | 0 | 0 | 0.17275 | 336.4426 | 0.086766 | 0 | 0 | 0.17353
2017-12-14 18:00 | 288.8618 | 0.86098 |  | 303.3236 | 0.014931 | 0 | 0 | 0.029861 | 311.8473 | 0.033419 | 0 | 0 | 0.066837 | 318.8213 | 0.048545 | 0 | 0 | 0.09709 | 319.0796 | 0.049105 | 0 | 0 | 0.09821 | 319.2518 | 0.049479 | 0 | 0 | 0.098957 | 319.5101 | 0.050039 | 0 | 0 | 0.10008 | 319.7684 | 0.050599 | 0 | 0 | 0.1012 | 320.0267 | 0.051159 | 0 | 0 | 0.10232 | 320.371 | 0.051906 | 0 | 0 | 0.10381 | 320.6293 | 0.052467 | 0 | 0 | 0.10493 | 320.8015 | 0.05284 | 0 | 0 | 0.10568 | 321.0598 | 0.0534 | 0 | 0 | 0.1068 | 321.232 | 0.053774 | 0 | 0 | 0.10755 | 321.4903 | 0.054334 | 0 | 0 | 0.10867 | 321.7486 | 0.054894 | 0 | 0 | 0.10979 | 321.9208 | 0.055268 | 0 | 0 | 0.11054 | 322.1791 | 0.055828 | 0 | 0 | 0.11166 | 322.4374 | 0.056388 | 0 | 0 | 0.11278 | 322.5235 | 0.056575 | 0 | 0 | 0.11315 | 322.7818 | 0.057135 | 0 | 0 | 0.11427 | 323.0401 | 0.057696 | 0 | 0 | 0.11539 | 323.2123 | 0.058069 | 0 | 0 | 0.11614 | 323.4706 | 0.058629 | 0 | 0 | 0.11726 | 323.6428 | 0.059003 | 0 | 0 | 0.11801 | 323.815 | 0.059376 | 0 | 0 | 0.11875
2017-12-14 19:00 | 288.6446 | 0.86033 |  | 303.0955 | 0.014436 | 0 | 0 | 0.028871 | 311.6128 | 0.03291 | 0 | 0 | 0.065819 | 318.5815 | 0.048025 | 0 | 0 | 0.09605 | 318.8396 | 0.048585 | 0 | 0 | 0.097169 | 319.0116 | 0.048958 | 0 | 0 | 0.097916 | 319.2697 | 0.049518 | 0 | 0 | 0.099035 | 319.5278 | 0.050078 | 0 | 0 | 0.10016 | 319.7859 | 0.050637 | 0 | 0 | 0.10127 | 320.1301 | 0.051384 | 0 | 0 | 0.10277 | 320.3882 | 0.051944 | 0 | 0 | 0.10389 | 320.5602 | 0.052317 | 0 | 0 | 0.10463 | 320.8183 | 0.052877 | 0 | 0 | 0.10575 | 320.9904 | 0.05325 | 0 | 0 | 0.1065 | 321.2485 | 0.05381 | 0 | 0 | 0.10762 | 321.5066 | 0.054369 | 0 | 0 | 0.10874 | 321.6787 | 0.054743 | 0 | 0 | 0.10949 | 321.9368 | 0.055303 | 0 | 0 | 0.11061 | 322.1949 | 0.055862 | 0 | 0 | 0.11172 | 322.2809 | 0.056049 | 0 | 0 | 0.1121 | 322.539 | 0.056609 | 0 | 0 | 0.11322 | 322.7971 | 0.057169 | 0 | 0 | 0.11434 | 322.9692 | 0.057542 | 0 | 0 | 0.11508 | 323.2273 | 0.058102 | 0 | 0 | 0.1162 | 323.3993 | 0.058475 | 0 | 0 | 0.11695 | 323.5714 | 0.058848 | 0 | 0 | 0.1177
2017-12-14 20:00 | 286.009 | 0.85248 |  | 300.328 | 0.008433 | 0 | 0 | 0.016866 | 308.7675 | 0.026738 | 0 | 0 | 0.053477 | 315.6726 | 0.041715 | 0 | 0 | 0.083431 | 315.9283 | 0.04227 | 0 | 0 | 0.08454 | 316.0988 | 0.04264 | 0 | 0 | 0.08528 | 316.3546 | 0.043195 | 0 | 0 | 0.086389 | 316.6103 | 0.043749 | 0 | 0 | 0.087499 | 316.866 | 0.044304 | 0 | 0 | 0.088608 | 317.207 | 0.045044 | 0 | 0 | 0.090087 | 317.4628 | 0.045598 | 0 | 0 | 0.091197 | 317.6333 | 0.045968 | 0 | 0 | 0.091936 | 317.889 | 0.046523 | 0 | 0 | 0.093046 | 318.0595 | 0.046893 | 0 | 0 | 0.093785 | 318.3153 | 0.047447 | 0 | 0 | 0.094895 | 318.571 | 0.048002 | 0 | 0 | 0.096004 | 318.7415 | 0.048372 | 0 | 0 | 0.096744 | 318.9972 | 0.048927 | 0 | 0 | 0.097853 | 319.253 | 0.049481 | 0 | 0 | 0.098963 | 319.3382 | 0.049666 | 0 | 0 | 0.099333 | 319.594 | 0.050221 | 0 | 0 | 0.10044 | 319.8497 | 0.050776 | 0 | 0 | 0.10155 | 320.0202 | 0.051145 | 0 | 0 | 0.10229 | 320.276 | 0.0517 | 0 | 0 | 0.1034 | 320.4465 | 0.05207 | 0 | 0 | 0.10414 | 320.6169 | 0.05244 | 0 | 0 | 0.10488
2017-12-14 21:00 | 288.4213 | 0.85967 |  | 302.861 | 0.013927 | 0 | 0 | 0.027854 | 311.3717 | 0.032387 | 0 | 0 | 0.064774 | 318.335 | 0.04749 | 0 | 0 | 0.094981 | 318.5929 | 0.04805 | 0 | 0 | 0.096099 | 318.7649 | 0.048423 | 0 | 0 | 0.096845 | 319.0228 | 0.048982 | 0 | 0 | 0.097964 | 319.2807 | 0.049541 | 0 | 0 | 0.099083 | 319.5386 | 0.050101 | 0 | 0 | 0.1002 | 319.8824 | 0.050847 | 0 | 0 | 0.10169 | 320.1403 | 0.051406 | 0 | 0 | 0.10281 | 320.3123 | 0.051779 | 0 | 0 | 0.10356 | 320.5702 | 0.052338 | 0 | 0 | 0.10468 | 320.7421 | 0.052711 | 0 | 0 | 0.10542 | 321 | 0.053271 | 0 | 0 | 0.10654 | 321.2579 | 0.05383 | 0 | 0 | 0.10766 | 321.4298 | 0.054203 | 0 | 0 | 0.10841 | 321.6877 | 0.054762 | 0 | 0 | 0.10952 | 321.9456 | 0.055322 | 0 | 0 | 0.11064 | 322.0316 | 0.055508 | 0 | 0 | 0.11102 | 322.2895 | 0.056068 | 0 | 0 | 0.11214 | 322.5474 | 0.056627 | 0 | 0 | 0.11325 | 322.7193 | 0.057 | 0 | 0 | 0.114 | 322.9772 | 0.057559 | 0 | 0 | 0.11512 | 323.1492 | 0.057932 | 0 | 0 | 0.11586 | 323.3211 | 0.058305 | 0 | 0 | 0.11661
2017-12-14 22:00 | 288.7217 | 0.86056 |  | 303.1765 | 0.014611 | 0 | 0 | 0.029223 | 311.696 | 0.03309 | 0 | 0 | 0.066181 | 318.6666 | 0.04821 | 0 | 0 | 0.096419 | 318.9248 | 0.048769 | 0 | 0 | 0.097539 | 319.0969 | 0.049143 | 0 | 0 | 0.098286 | 319.3551 | 0.049703 | 0 | 0 | 0.099406 | 319.6132 | 0.050263 | 0 | 0 | 0.10053 | 319.8714 | 0.050823 | 0 | 0 | 0.10165 | 320.2156 | 0.051569 | 0 | 0 | 0.10314 | 320.4738 | 0.052129 | 0 | 0 | 0.10426 | 320.6459 | 0.052503 | 0 | 0 | 0.10501 | 320.9041 | 0.053063 | 0 | 0 | 0.10613 | 321.0762 | 0.053436 | 0 | 0 | 0.10687 | 321.3344 | 0.053996 | 0 | 0 | 0.10799 | 321.5925 | 0.054556 | 0 | 0 | 0.10911 | 321.7646 | 0.054929 | 0 | 0 | 0.10986 | 322.0228 | 0.055489 | 0 | 0 | 0.11098 | 322.281 | 0.056049 | 0 | 0 | 0.1121 | 322.367 | 0.056236 | 0 | 0 | 0.11247 | 322.6252 | 0.056796 | 0 | 0 | 0.11359 | 322.8834 | 0.057356 | 0 | 0 | 0.11471 | 323.0555 | 0.057729 | 0 | 0 | 0.11546 | 323.3136 | 0.058289 | 0 | 0 | 0.11658 | 323.4858 | 0.058662 | 0 | 0 | 0.11732 | 323.6579 | 0.059036 | 0 | 0 | 0.11807
2017-12-14 23:00 | 289.0443 | 0.86152 |  | 303.5152 | 0.015346 | 0 | 0 | 0.030692 | 312.0443 | 0.033846 | 0 | 0 | 0.067691 | 319.0226 | 0.048982 | 0 | 0 | 0.097963 | 319.2811 | 0.049542 | 0 | 0 | 0.099085 | 319.4534 | 0.049916 | 0 | 0 | 0.099832 | 319.7119 | 0.050477 | 0 | 0 | 0.10095 | 319.9703 | 0.051037 | 0 | 0 | 0.10207 | 320.2288 | 0.051598 | 0 | 0 | 0.1032 | 320.5734 | 0.052345 | 0 | 0 | 0.10469 | 320.8318 | 0.052906 | 0 | 0 | 0.10581 | 321.0041 | 0.05328 | 0 | 0 | 0.10656 | 321.2626 | 0.05384 | 0 | 0 | 0.10768 | 321.4349 | 0.054214 | 0 | 0 | 0.10843 | 321.6934 | 0.054775 | 0 | 0 | 0.10955 | 321.9518 | 0.055335 | 0 | 0 | 0.11067 | 322.1241 | 0.055709 | 0 | 0 | 0.11142 | 322.3826 | 0.056269 | 0 | 0 | 0.11254 | 322.641 | 0.05683 | 0 | 0 | 0.11366 | 322.7272 | 0.057017 | 0 | 0 | 0.11403 | 322.9856 | 0.057578 | 0 | 0 | 0.11516 | 323.2441 | 0.058138 | 0 | 0 | 0.11628 | 323.4164 | 0.058512 | 0 | 0 | 0.11702 | 323.6749 | 0.059072 | 0 | 0 | 0.11814 | 323.8472 | 0.059446 | 0 | 0 | 0.11889 | 324.0195 | 0.05982 | 0 | 0 | 0.11964
2017-12-15 | 290.4723 | 0.86578 |  | 305.0148 | 0.018599 | 0 | 0 | 0.037197 | 313.586 | 0.03719 | 0 | 0 | 0.074379 | 320.5988 | 0.0524 | 0 | 0 | 0.1048 | 320.8586 | 0.052964 | 0 | 0 | 0.10593 | 321.0317 | 0.053339 | 0 | 0 | 0.10668 | 321.2915 | 0.053903 | 0 | 0 | 0.10781 | 321.5512 | 0.054466 | 0 | 0 | 0.10893 | 321.8109 | 0.05503 | 0 | 0 | 0.11006 | 322.1572 | 0.055781 | 0 | 0 | 0.11156 | 322.417 | 0.056344 | 0 | 0 | 0.11269 | 322.5901 | 0.05672 | 0 | 0 | 0.11344 | 322.8499 | 0.057283 | 0 | 0 | 0.11457 | 323.023 | 0.057659 | 0 | 0 | 0.11532 | 323.2827 | 0.058222 | 0 | 0 | 0.11644 | 323.5425 | 0.058785 | 0 | 0 | 0.11757 | 323.7156 | 0.059161 | 0 | 0 | 0.11832 | 323.9754 | 0.059724 | 0 | 0 | 0.11945 | 324.2351 | 0.060288 | 0 | 0 | 0.12058 | 324.3217 | 0.060475 | 0 | 0 | 0.12095 | 324.5814 | 0.061039 | 0 | 0 | 0.12208 | 324.8412 | 0.061602 | 0 | 0 | 0.1232 | 325.0143 | 0.061978 | 0 | 0 | 0.12396 | 325.274 | 0.062541 | 0 | 0 | 0.12508 | 325.4472 | 0.062917 | 0 | 0 | 0.12583 | 325.6204 | 0.063292 | 0 | 0 | 0.12658
2017-12-15 01:00 | 286.956 | 0.8553 |  | 301.3224 | 0.01059 | 0 | 0 | 0.02118 | 309.7899 | 0.028956 | 0 | 0 | 0.057912 | 316.7178 | 0.043983 | 0 | 0 | 0.087965 | 316.9744 | 0.044539 | 0 | 0 | 0.089078 | 317.1455 | 0.04491 | 0 | 0 | 0.08982 | 317.402 | 0.045467 | 0 | 0 | 0.090933 | 317.6586 | 0.046023 | 0 | 0 | 0.092046 | 317.9152 | 0.04658 | 0 | 0 | 0.09316 | 318.2573 | 0.047322 | 0 | 0 | 0.094644 | 318.5139 | 0.047878 | 0 | 0 | 0.095757 | 318.685 | 0.048249 | 0 | 0 | 0.096499 | 318.9416 | 0.048806 | 0 | 0 | 0.097612 | 319.1126 | 0.049177 | 0 | 0 | 0.098354 | 319.3692 | 0.049734 | 0 | 0 | 0.099467 | 319.6258 | 0.05029 | 0 | 0 | 0.10058 | 319.7969 | 0.050661 | 0 | 0 | 0.10132 | 320.0535 | 0.051218 | 0 | 0 | 0.10244 | 320.3101 | 0.051774 | 0 | 0 | 0.10355 | 320.3956 | 0.05196 | 0 | 0 | 0.10392 | 320.6522 | 0.052516 | 0 | 0 | 0.10503 | 320.9088 | 0.053073 | 0 | 0 | 0.10615 | 321.0798 | 0.053444 | 0 | 0 | 0.10689 | 321.3364 | 0.054 | 0 | 0 | 0.108 | 321.5075 | 0.054371 | 0 | 0 | 0.10874 | 321.6785 | 0.054742 | 0 | 0 | 0.10948
2017-12-15 02:00 | 291.4264 | 0.86862 |  | 306.0166 | 0.020772 | 0 | 0 | 0.041543 | 314.6159 | 0.039424 | 0 | 0 | 0.078847 | 321.6518 | 0.054684 | 0 | 0 | 0.10937 | 321.9124 | 0.05525 | 0 | 0 | 0.1105 | 322.0861 | 0.055626 | 0 | 0 | 0.11125 | 322.3467 | 0.056192 | 0 | 0 | 0.11238 | 322.6073 | 0.056757 | 0 | 0 | 0.11351 | 322.8679 | 0.057322 | 0 | 0 | 0.11464 | 323.2153 | 0.058076 | 0 | 0 | 0.11615 | 323.4759 | 0.058641 | 0 | 0 | 0.11728 | 323.6496 | 0.059018 | 0 | 0 | 0.11804 | 323.9102 | 0.059583 | 0 | 0 | 0.11917 | 324.084 | 0.05996 | 0 | 0 | 0.11992 | 324.3445 | 0.060525 | 0 | 0 | 0.12105 | 324.6051 | 0.06109 | 0 | 0 | 0.12218 | 324.7789 | 0.061467 | 0 | 0 | 0.12293 | 325.0394 | 0.062032 | 0 | 0 | 0.12406 | 325.3 | 0.062597 | 0 | 0 | 0.12519 | 325.3869 | 0.062786 | 0 | 0 | 0.12557 | 325.6475 | 0.063351 | 0 | 0 | 0.1267 | 325.9081 | 0.063916 | 0 | 0 | 0.12783 | 326.0818 | 0.064293 | 0 | 0 | 0.12859 | 326.3424 | 0.064858 | 0 | 0 | 0.12972 | 326.5161 | 0.065235 | 0 | 0 | 0.13047 | 326.6898 | 0.065612 | 0 | 0 | 0.13122
2017-12-15 03:00 | 291.2652 | 0.86814 |  | 305.8473 | 0.020404 | 0 | 0 | 0.040809 | 314.4419 | 0.039046 | 0 | 0 | 0.078092 | 321.4739 | 0.054298 | 0 | 0 | 0.1086 | 321.7343 | 0.054863 | 0 | 0 | 0.10973 | 321.908 | 0.05524 | 0 | 0 | 0.11048 | 322.1684 | 0.055805 | 0 | 0 | 0.11161 | 322.4288 | 0.05637 | 0 | 0 | 0.11274 | 322.6893 | 0.056935 | 0 | 0 | 0.11387 | 323.0365 | 0.057688 | 0 | 0 | 0.11538 | 323.297 | 0.058253 | 0 | 0 | 0.11651 | 323.4706 | 0.058629 | 0 | 0 | 0.11726 | 323.7311 | 0.059194 | 0 | 0 | 0.11839 | 323.9047 | 0.059571 | 0 | 0 | 0.11914 | 324.1651 | 0.060136 | 0 | 0 | 0.12027 | 324.4256 | 0.060701 | 0 | 0 | 0.1214 | 324.5992 | 0.061077 | 0 | 0 | 0.12215 | 324.8596 | 0.061642 | 0 | 0 | 0.12328 | 325.1201 | 0.062207 | 0 | 0 | 0.12441 | 325.2069 | 0.062395 | 0 | 0 | 0.12479 | 325.4674 | 0.06296 | 0 | 0 | 0.12592 | 325.7278 | 0.063525 | 0 | 0 | 0.12705 | 325.9014 | 0.063902 | 0 | 0 | 0.1278 | 326.1619 | 0.064467 | 0 | 0 | 0.12893 | 326.3355 | 0.064843 | 0 | 0 | 0.12969 | 326.5091 | 0.06522 | 0 | 0 | 0.13044
2017-12-15 04:00 | 288.5206 | 0.85996 |  | 302.9653 | 0.014153 | 0 | 0 | 0.028307 | 311.479 | 0.03262 | 0 | 0 | 0.065239 | 318.4447 | 0.047728 | 0 | 0 | 0.095456 | 318.7027 | 0.048288 | 0 | 0 | 0.096575 | 318.8747 | 0.048661 | 0 | 0 | 0.097322 | 319.1327 | 0.04922 | 0 | 0 | 0.098441 | 319.3906 | 0.04978 | 0 | 0 | 0.09956 | 319.6486 | 0.05034 | 0 | 0 | 0.10068 | 319.9926 | 0.051086 | 0 | 0 | 0.10217 | 320.2506 | 0.051645 | 0 | 0 | 0.10329 | 320.4226 | 0.052018 | 0 | 0 | 0.10404 | 320.6806 | 0.052578 | 0 | 0 | 0.10516 | 320.8526 | 0.052951 | 0 | 0 | 0.1059 | 321.1106 | 0.05351 | 0 | 0 | 0.10702 | 321.3686 | 0.05407 | 0 | 0 | 0.10814 | 321.5406 | 0.054443 | 0 | 0 | 0.10889 | 321.7985 | 0.055003 | 0 | 0 | 0.11001 | 322.0565 | 0.055562 | 0 | 0 | 0.11112 | 322.1425 | 0.055749 | 0 | 0 | 0.1115 | 322.4005 | 0.056308 | 0 | 0 | 0.11262 | 322.6585 | 0.056868 | 0 | 0 | 0.11374 | 322.8305 | 0.057241 | 0 | 0 | 0.11448 | 323.0885 | 0.057801 | 0 | 0 | 0.1156 | 323.2605 | 0.058174 | 0 | 0 | 0.11635 | 323.4325 | 0.058547 | 0 | 0 | 0.11709
2017-12-15 05:00 | 293.9212 | 0.87606 |  | 308.6363 | 0.026454 | 0 | 0 | 0.052907 | 317.3093 | 0.045265 | 0 | 0 | 0.090531 | 324.4054 | 0.060657 | 0 | 0 | 0.12131 | 324.6682 | 0.061227 | 0 | 0 | 0.12245 | 324.8434 | 0.061607 | 0 | 0 | 0.12321 | 325.1062 | 0.062177 | 0 | 0 | 0.12435 | 325.369 | 0.062747 | 0 | 0 | 0.12549 | 325.6319 | 0.063317 | 0 | 0 | 0.12663 | 325.9823 | 0.064077 | 0 | 0 | 0.12815 | 326.2451 | 0.064647 | 0 | 0 | 0.12929 | 326.4203 | 0.065027 | 0 | 0 | 0.13005 | 326.6831 | 0.065597 | 0 | 0 | 0.13119 | 326.8583 | 0.065977 | 0 | 0 | 0.13195 | 327.1212 | 0.066547 | 0 | 0 | 0.13309 | 327.384 | 0.067118 | 0 | 0 | 0.13424 | 327.5592 | 0.067498 | 0 | 0 | 0.135 | 327.822 | 0.068068 | 0 | 0 | 0.13614 | 328.0848 | 0.068638 | 0 | 0 | 0.13728 | 328.1724 | 0.068828 | 0 | 0 | 0.13766 | 328.4353 | 0.069398 | 0 | 0 | 0.1388 | 328.6981 | 0.069968 | 0 | 0 | 0.13994 | 328.8733 | 0.070348 | 0 | 0 | 0.1407 | 329.1361 | 0.070918 | 0 | 0 | 0.14184 | 329.3113 | 0.071298 | 0 | 0 | 0.1426 | 329.4865 | 0.071678 | 0 | 0 | 0.14336
2017-12-15 06:00 | 280.5817 | 0.8363 |  | 294.629 | 0 | 0 | 0 | 0 | 302.9083 | 0.01403 | 0 | 0 | 0.02806 | 309.6824 | 0.028723 | 0 | 0 | 0.057445 | 309.9333 | 0.029267 | 0 | 0 | 0.058534 | 310.1005 | 0.02963 | 0 | 0 | 0.059259 | 310.3514 | 0.030174 | 0 | 0 | 0.060348 | 310.6023 | 0.030718 | 0 | 0 | 0.061436 | 310.8532 | 0.031262 | 0 | 0 | 0.062524 | 311.1877 | 0.031988 | 0 | 0 | 0.063976 | 311.4386 | 0.032532 | 0 | 0 | 0.065064 | 311.6059 | 0.032895 | 0 | 0 | 0.06579 | 311.8568 | 0.033439 | 0 | 0 | 0.066878 | 312.024 | 0.033802 | 0 | 0 | 0.067603 | 312.2749 | 0.034346 | 0 | 0 | 0.068692 | 312.5258 | 0.03489 | 0 | 0 | 0.06978 | 312.6931 | 0.035253 | 0 | 0 | 0.070506 | 312.944 | 0.035797 | 0 | 0 | 0.071594 | 313.1948 | 0.036341 | 0 | 0 | 0.072683 | 313.2785 | 0.036523 | 0 | 0 | 0.073045 | 313.5294 | 0.037067 | 0 | 0 | 0.074134 | 313.7803 | 0.037611 | 0 | 0 | 0.075222 | 313.9475 | 0.037974 | 0 | 0 | 0.075948 | 314.1984 | 0.038518 | 0 | 0 | 0.077036 | 314.3657 | 0.038881 | 0 | 0 | 0.077762 | 314.5329 | 0.039244 | 0 | 0 | 0.078487
2017-12-15 07:00 | 287.3222 | 0.85639 |  | 301.7069 | 0.011424 | 0 | 0 | 0.022848 | 310.1852 | 0.029813 | 0 | 0 | 0.059627 | 317.1219 | 0.044859 | 0 | 0 | 0.089718 | 317.3789 | 0.045416 | 0 | 0 | 0.090833 | 317.5501 | 0.045788 | 0 | 0 | 0.091576 | 317.8071 | 0.046345 | 0 | 0 | 0.09269 | 318.064 | 0.046902 | 0 | 0 | 0.093805 | 318.3209 | 0.04746 | 0 | 0 | 0.094919 | 318.6634 | 0.048203 | 0 | 0 | 0.096405 | 318.9204 | 0.04876 | 0 | 0 | 0.09752 | 319.0916 | 0.049131 | 0 | 0 | 0.098263 | 319.3486 | 0.049689 | 0 | 0 | 0.099377 | 319.5198 | 0.05006 | 0 | 0 | 0.10012 | 319.7768 | 0.050617 | 0 | 0 | 0.10123 | 320.0337 | 0.051175 | 0 | 0 | 0.10235 | 320.205 | 0.051546 | 0 | 0 | 0.10309 | 320.4619 | 0.052103 | 0 | 0 | 0.10421 | 320.7188 | 0.052661 | 0 | 0 | 0.10532 | 320.8044 | 0.052846 | 0 | 0 | 0.10569 | 321.0613 | 0.053404 | 0 | 0 | 0.10681 | 321.3183 | 0.053961 | 0 | 0 | 0.10792 | 321.4895 | 0.054332 | 0 | 0 | 0.10866 | 321.7465 | 0.05489 | 0 | 0 | 0.10978 | 321.9177 | 0.055261 | 0 | 0 | 0.11052 | 322.089 | 0.055633 | 0 | 0 | 0.11127
2017-12-15 08:00 | 284.2695 | 0.84729 |  | 298.5014 | 0.0044711 | 0 | 0 | 0.0089422 | 306.8896 | 0.022665 | 0 | 0 | 0.04533 | 313.7526 | 0.037551 | 0 | 0 | 0.075102 | 314.0068 | 0.038102 | 0 | 0 | 0.076205 | 314.1763 | 0.03847 | 0 | 0 | 0.07694 | 314.4305 | 0.039021 | 0 | 0 | 0.078043 | 314.6847 | 0.039573 | 0 | 0 | 0.079145 | 314.9389 | 0.040124 | 0 | 0 | 0.080248 | 315.2778 | 0.040859 | 0 | 0 | 0.081718 | 315.532 | 0.04141 | 0 | 0 | 0.082821 | 315.7014 | 0.041778 | 0 | 0 | 0.083556 | 315.9556 | 0.042329 | 0 | 0 | 0.084659 | 316.1251 | 0.042697 | 0 | 0 | 0.085394 | 316.3793 | 0.043248 | 0 | 0 | 0.086496 | 316.6334 | 0.0438 | 0 | 0 | 0.087599 | 316.8029 | 0.044167 | 0 | 0 | 0.088334 | 317.0571 | 0.044718 | 0 | 0 | 0.089437 | 317.3113 | 0.04527 | 0 | 0 | 0.09054 | 317.396 | 0.045454 | 0 | 0 | 0.090907 | 317.6502 | 0.046005 | 0 | 0 | 0.09201 | 317.9044 | 0.046556 | 0 | 0 | 0.093112 | 318.0738 | 0.046924 | 0 | 0 | 0.093848 | 318.328 | 0.047475 | 0 | 0 | 0.09495 | 318.4975 | 0.047843 | 0 | 0 | 0.095685 | 318.6669 | 0.04821 | 0 | 0 | 0.09642
2017-12-15 09:00 | 283.5376 | 0.84511 |  | 297.7328 | 0.0028041 | 0 | 0 | 0.0056083 | 306.0994 | 0.020951 | 0 | 0 | 0.041903 | 312.9448 | 0.035799 | 0 | 0 | 0.071598 | 313.1984 | 0.036349 | 0 | 0 | 0.072698 | 313.3674 | 0.036716 | 0 | 0 | 0.073431 | 313.6209 | 0.037265 | 0 | 0 | 0.074531 | 313.8745 | 0.037815 | 0 | 0 | 0.075631 | 314.128 | 0.038365 | 0 | 0 | 0.076731 | 314.466 | 0.039098 | 0 | 0 | 0.078197 | 314.7196 | 0.039648 | 0 | 0 | 0.079297 | 314.8886 | 0.040015 | 0 | 0 | 0.08003 | 315.1421 | 0.040565 | 0 | 0 | 0.08113 | 315.3112 | 0.040932 | 0 | 0 | 0.081863 | 315.5647 | 0.041481 | 0 | 0 | 0.082963 | 315.8182 | 0.042031 | 0 | 0 | 0.084063 | 315.9872 | 0.042398 | 0 | 0 | 0.084796 | 316.2408 | 0.042948 | 0 | 0 | 0.085896 | 316.4943 | 0.043498 | 0 | 0 | 0.086996 | 316.5788 | 0.043681 | 0 | 0 | 0.087362 | 316.8324 | 0.044231 | 0 | 0 | 0.088462 | 317.0859 | 0.044781 | 0 | 0 | 0.089562 | 317.2549 | 0.045148 | 0 | 0 | 0.090295 | 317.5084 | 0.045697 | 0 | 0 | 0.091395 | 317.6775 | 0.046064 | 0 | 0 | 0.092128 | 317.8465 | 0.046431 | 0 | 0 | 0.092861
2017-12-15 10:00 | 275.6421 | 0.82158 |  | 289.442 | 0 | 0 | 0 | 0 | 297.5757 | 0.0024632 | 0 | 0 | 0.0049265 | 304.2304 | 0.016897 | 0 | 0 | 0.033795 | 304.4769 | 0.017432 | 0 | 0 | 0.034864 | 304.6412 | 0.017788 | 0 | 0 | 0.035577 | 304.8877 | 0.018323 | 0 | 0 | 0.036646 | 305.1342 | 0.018858 | 0 | 0 | 0.037715 | 305.3806 | 0.019392 | 0 | 0 | 0.038785 | 305.7093 | 0.020105 | 0 | 0 | 0.04021 | 305.9558 | 0.02064 | 0 | 0 | 0.041279 | 306.1201 | 0.020996 | 0 | 0 | 0.041992 | 306.3665 | 0.021531 | 0 | 0 | 0.043061 | 306.5309 | 0.021887 | 0 | 0 | 0.043774 | 306.7773 | 0.022422 | 0 | 0 | 0.044843 | 307.0238 | 0.022956 | 0 | 0 | 0.045913 | 307.1881 | 0.023313 | 0 | 0 | 0.046625 | 307.4346 | 0.023847 | 0 | 0 | 0.047695 | 307.6811 | 0.024382 | 0 | 0 | 0.048764 | 307.7632 | 0.02456 | 0 | 0 | 0.04912 | 308.0097 | 0.025095 | 0 | 0 | 0.050189 | 308.2562 | 0.025629 | 0 | 0 | 0.051259 | 308.4205 | 0.025986 | 0 | 0 | 0.051971 | 308.667 | 0.02652 | 0 | 0 | 0.053041 | 308.8313 | 0.026877 | 0 | 0 | 0.053753 | 308.9956 | 0.027233 | 0 | 0 | 0.054466
2017-12-15 11:00 | 278.5794 | 0.83033 |  | 292.5264 | 0 | 0 | 0 | 0 | 300.7467 | 0.0093412 | 0 | 0 | 0.018682 | 307.4724 | 0.023929 | 0 | 0 | 0.047859 | 307.7215 | 0.02447 | 0 | 0 | 0.048939 | 307.8876 | 0.02483 | 0 | 0 | 0.04966 | 308.1367 | 0.02537 | 0 | 0 | 0.05074 | 308.3858 | 0.02591 | 0 | 0 | 0.051821 | 308.6349 | 0.026451 | 0 | 0 | 0.052901 | 308.967 | 0.027171 | 0 | 0 | 0.054342 | 309.2161 | 0.027711 | 0 | 0 | 0.055423 | 309.3822 | 0.028072 | 0 | 0 | 0.056143 | 309.6313 | 0.028612 | 0 | 0 | 0.057224 | 309.7973 | 0.028972 | 0 | 0 | 0.057944 | 310.0464 | 0.029512 | 0 | 0 | 0.059025 | 310.2955 | 0.030053 | 0 | 0 | 0.060105 | 310.4616 | 0.030413 | 0 | 0 | 0.060826 | 310.7107 | 0.030953 | 0 | 0 | 0.061906 | 310.9598 | 0.031493 | 0 | 0 | 0.062987 | 311.0428 | 0.031674 | 0 | 0 | 0.063347 | 311.2919 | 0.032214 | 0 | 0 | 0.064428 | 311.541 | 0.032754 | 0 | 0 | 0.065508 | 311.7071 | 0.033114 | 0 | 0 | 0.066229 | 311.9562 | 0.033655 | 0 | 0 | 0.067309 | 312.1223 | 0.034015 | 0 | 0 | 0.06803 | 312.2883 | 0.034375 | 0 | 0 | 0.06875
2017-12-15 12:00 | 289.0342 | 0.86149 |  | 303.5046 | 0.015323 | 0 | 0 | 0.030646 | 312.0334 | 0.033822 | 0 | 0 | 0.067644 | 319.0115 | 0.048958 | 0 | 0 | 0.097915 | 319.2699 | 0.049518 | 0 | 0 | 0.099036 | 319.4422 | 0.049892 | 0 | 0 | 0.099784 | 319.7007 | 0.050452 | 0 | 0 | 0.1009 | 319.9591 | 0.051013 | 0 | 0 | 0.10203 | 320.2176 | 0.051574 | 0 | 0 | 0.10315 | 320.5622 | 0.052321 | 0 | 0 | 0.10464 | 320.8206 | 0.052882 | 0 | 0 | 0.10576 | 320.9929 | 0.053255 | 0 | 0 | 0.10651 | 321.2514 | 0.053816 | 0 | 0 | 0.10763 | 321.4237 | 0.05419 | 0 | 0 | 0.10838 | 321.6821 | 0.05475 | 0 | 0 | 0.1095 | 321.9406 | 0.055311 | 0 | 0 | 0.11062 | 322.1129 | 0.055684 | 0 | 0 | 0.11137 | 322.3713 | 0.056245 | 0 | 0 | 0.11249 | 322.6298 | 0.056806 | 0 | 0 | 0.11361 | 322.7159 | 0.056992 | 0 | 0 | 0.11398 | 322.9744 | 0.057553 | 0 | 0 | 0.11511 | 323.2328 | 0.058114 | 0 | 0 | 0.11623 | 323.4051 | 0.058487 | 0 | 0 | 0.11697 | 323.6636 | 0.059048 | 0 | 0 | 0.1181 | 323.8359 | 0.059422 | 0 | 0 | 0.11884 | 324.0082 | 0.059795 | 0 | 0 | 0.11959
2017-12-15 13:00 | 280.4079 | 0.83578 |  | 294.4465 | 0 | 0 | 0 | 0 | 302.7207 | 0.013623 | 0 | 0 | 0.027246 | 309.4906 | 0.028307 | 0 | 0 | 0.056613 | 309.7413 | 0.028851 | 0 | 0 | 0.057701 | 309.9084 | 0.029213 | 0 | 0 | 0.058426 | 310.1592 | 0.029757 | 0 | 0 | 0.059514 | 310.4099 | 0.030301 | 0 | 0 | 0.060602 | 310.6607 | 0.030845 | 0 | 0 | 0.061689 | 310.995 | 0.03157 | 0 | 0 | 0.063139 | 311.2457 | 0.032114 | 0 | 0 | 0.064227 | 311.4129 | 0.032476 | 0 | 0 | 0.064952 | 311.6636 | 0.03302 | 0 | 0 | 0.06604 | 311.8308 | 0.033383 | 0 | 0 | 0.066765 | 312.0815 | 0.033926 | 0 | 0 | 0.067853 | 312.3322 | 0.03447 | 0 | 0 | 0.06894 | 312.4994 | 0.034833 | 0 | 0 | 0.069666 | 312.7501 | 0.035377 | 0 | 0 | 0.070753 | 313.0008 | 0.03592 | 0 | 0 | 0.071841 | 313.0844 | 0.036102 | 0 | 0 | 0.072204 | 313.3352 | 0.036646 | 0 | 0 | 0.073291 | 313.5859 | 0.037189 | 0 | 0 | 0.074379 | 313.7531 | 0.037552 | 0 | 0 | 0.075104 | 314.0038 | 0.038096 | 0 | 0 | 0.076192 | 314.1709 | 0.038458 | 0 | 0 | 0.076917 | 314.3381 | 0.038821 | 0 | 0 | 0.077642
2017-12-15 14:00 | 278.3851 | 0.82975 |  | 292.3223 | 0 | 0 | 0 | 0 | 300.5369 | 0.0088862 | 0 | 0 | 0.017772 | 307.2579 | 0.023464 | 0 | 0 | 0.046928 | 307.5068 | 0.024004 | 0 | 0 | 0.048008 | 307.6728 | 0.024364 | 0 | 0 | 0.048728 | 307.9217 | 0.024904 | 0 | 0 | 0.049808 | 308.1706 | 0.025444 | 0 | 0 | 0.050888 | 308.4196 | 0.025984 | 0 | 0 | 0.051967 | 308.7515 | 0.026704 | 0 | 0 | 0.053407 | 309.0004 | 0.027244 | 0 | 0 | 0.054487 | 309.1663 | 0.027603 | 0 | 0 | 0.055207 | 309.4153 | 0.028143 | 0 | 0 | 0.056287 | 309.5812 | 0.028503 | 0 | 0 | 0.057007 | 309.8302 | 0.029043 | 0 | 0 | 0.058086 | 310.0791 | 0.029583 | 0 | 0 | 0.059166 | 310.245 | 0.029943 | 0 | 0 | 0.059886 | 310.494 | 0.030483 | 0 | 0 | 0.060966 | 310.7429 | 0.031023 | 0 | 0 | 0.062046 | 310.8259 | 0.031203 | 0 | 0 | 0.062406 | 311.0748 | 0.031743 | 0 | 0 | 0.063486 | 311.3237 | 0.032283 | 0 | 0 | 0.064566 | 311.4897 | 0.032643 | 0 | 0 | 0.065285 | 311.7386 | 0.033183 | 0 | 0 | 0.066365 | 311.9045 | 0.033543 | 0 | 0 | 0.067085 | 312.0705 | 0.033903 | 0 | 0 | 0.067805
2017-12-15 15:00 | 279.1915 | 0.83216 |  | 293.1691 | 0 | 0 | 0 | 0 | 301.4075 | 0.010774 | 0 | 0 | 0.021549 | 308.148 | 0.025395 | 0 | 0 | 0.050789 | 308.3976 | 0.025936 | 0 | 0 | 0.051872 | 308.564 | 0.026297 | 0 | 0 | 0.052594 | 308.8137 | 0.026839 | 0 | 0 | 0.053677 | 309.0633 | 0.02738 | 0 | 0 | 0.05476 | 309.313 | 0.027922 | 0 | 0 | 0.055843 | 309.6458 | 0.028643 | 0 | 0 | 0.057287 | 309.8955 | 0.029185 | 0 | 0 | 0.05837 | 310.0619 | 0.029546 | 0 | 0 | 0.059092 | 310.3116 | 0.030087 | 0 | 0 | 0.060175 | 310.478 | 0.030448 | 0 | 0 | 0.060897 | 310.7277 | 0.03099 | 0 | 0 | 0.06198 | 310.9773 | 0.031531 | 0 | 0 | 0.063063 | 311.1437 | 0.031892 | 0 | 0 | 0.063785 | 311.3934 | 0.032434 | 0 | 0 | 0.064868 | 311.643 | 0.032975 | 0 | 0 | 0.065951 | 311.7262 | 0.033156 | 0 | 0 | 0.066312 | 311.9759 | 0.033697 | 0 | 0 | 0.067395 | 312.2255 | 0.034239 | 0 | 0 | 0.068478 | 312.392 | 0.0346 | 0 | 0 | 0.0692 | 312.6416 | 0.035141 | 0 | 0 | 0.070283 | 312.808 | 0.035502 | 0 | 0 | 0.071005 | 312.9745 | 0.035863 | 0 | 0 | 0.071727
2017-12-15 16:00 | 287.1026 | 0.85574 |  | 301.4763 | 0.010924 | 0 | 0 | 0.021847 | 309.9481 | 0.029299 | 0 | 0 | 0.058598 | 316.8795 | 0.044333 | 0 | 0 | 0.088667 | 317.1363 | 0.04489 | 0 | 0 | 0.08978 | 317.3074 | 0.045261 | 0 | 0 | 0.090523 | 317.5641 | 0.045818 | 0 | 0 | 0.091636 | 317.8209 | 0.046375 | 0 | 0 | 0.09275 | 318.0776 | 0.046932 | 0 | 0 | 0.093864 | 318.4199 | 0.047674 | 0 | 0 | 0.095349 | 318.6766 | 0.048231 | 0 | 0 | 0.096462 | 318.8477 | 0.048602 | 0 | 0 | 0.097205 | 319.1045 | 0.049159 | 0 | 0 | 0.098318 | 319.2756 | 0.04953 | 0 | 0 | 0.099061 | 319.5323 | 0.050087 | 0 | 0 | 0.10017 | 319.7891 | 0.050644 | 0 | 0 | 0.10129 | 319.9602 | 0.051015 | 0 | 0 | 0.10203 | 320.2169 | 0.051572 | 0 | 0 | 0.10314 | 320.4736 | 0.052129 | 0 | 0 | 0.10426 | 320.5592 | 0.052315 | 0 | 0 | 0.10463 | 320.8159 | 0.052871 | 0 | 0 | 0.10574 | 321.0727 | 0.053428 | 0 | 0 | 0.10686 | 321.2438 | 0.053799 | 0 | 0 | 0.1076 | 321.5005 | 0.054356 | 0 | 0 | 0.10871 | 321.6717 | 0.054728 | 0 | 0 | 0.10946 | 321.8428 | 0.055099 | 0 | 0 | 0.1102
2017-12-15 17:00 | 287.8897 | 0.85808 |  | 302.3028 | 0.012716 | 0 | 0 | 0.025433 | 310.7978 | 0.031142 | 0 | 0 | 0.062284 | 317.7483 | 0.046218 | 0 | 0 | 0.092435 | 318.0057 | 0.046776 | 0 | 0 | 0.093552 | 318.1774 | 0.047148 | 0 | 0 | 0.094297 | 318.4348 | 0.047707 | 0 | 0 | 0.095413 | 318.6922 | 0.048265 | 0 | 0 | 0.09653 | 318.9496 | 0.048823 | 0 | 0 | 0.097647 | 319.2929 | 0.049568 | 0 | 0 | 0.099136 | 319.5503 | 0.050126 | 0 | 0 | 0.10025 | 319.7219 | 0.050498 | 0 | 0 | 0.101 | 319.9793 | 0.051057 | 0 | 0 | 0.10211 | 320.1509 | 0.051429 | 0 | 0 | 0.10286 | 320.4084 | 0.051987 | 0 | 0 | 0.10397 | 320.6658 | 0.052546 | 0 | 0 | 0.10509 | 320.8374 | 0.052918 | 0 | 0 | 0.10584 | 321.0948 | 0.053476 | 0 | 0 | 0.10695 | 321.3523 | 0.054035 | 0 | 0 | 0.10807 | 321.4381 | 0.054221 | 0 | 0 | 0.10844 | 321.6955 | 0.054779 | 0 | 0 | 0.10956 | 321.9529 | 0.055338 | 0 | 0 | 0.11068 | 322.1245 | 0.05571 | 0 | 0 | 0.11142 | 322.382 | 0.056268 | 0 | 0 | 0.11254 | 322.5536 | 0.05664 | 0 | 0 | 0.11328 | 322.7252 | 0.057013 | 0 | 0 | 0.11403
2017-12-15 18:00 | 289.6303 | 0.86327 |  | 304.1305 | 0.016681 | 0 | 0 | 0.033361 | 312.6769 | 0.035218 | 0 | 0 | 0.070436 | 319.6694 | 0.050385 | 0 | 0 | 0.10077 | 319.9284 | 0.050946 | 0 | 0 | 0.10189 | 320.101 | 0.051321 | 0 | 0 | 0.10264 | 320.36 | 0.051883 | 0 | 0 | 0.10377 | 320.619 | 0.052444 | 0 | 0 | 0.10489 | 320.878 | 0.053006 | 0 | 0 | 0.10601 | 321.2233 | 0.053755 | 0 | 0 | 0.10751 | 321.4823 | 0.054317 | 0 | 0 | 0.10863 | 321.6549 | 0.054691 | 0 | 0 | 0.10938 | 321.9139 | 0.055253 | 0 | 0 | 0.11051 | 322.0866 | 0.055627 | 0 | 0 | 0.11125 | 322.3455 | 0.056189 | 0 | 0 | 0.11238 | 322.6045 | 0.056751 | 0 | 0 | 0.1135 | 322.7772 | 0.057125 | 0 | 0 | 0.11425 | 323.0362 | 0.057687 | 0 | 0 | 0.11537 | 323.2951 | 0.058249 | 0 | 0 | 0.1165 | 323.3815 | 0.058436 | 0 | 0 | 0.11687 | 323.6404 | 0.058998 | 0 | 0 | 0.118 | 323.8994 | 0.05956 | 0 | 0 | 0.11912 | 324.0721 | 0.059934 | 0 | 0 | 0.11987 | 324.3311 | 0.060496 | 0 | 0 | 0.12099 | 324.5037 | 0.06087 | 0 | 0 | 0.12174 | 324.6764 | 0.061245 | 0 | 0 | 0.12249
2017-12-15 19:00 | 288.8466 | 0.86094 |  | 303.3076 | 0.014896 | 0 | 0 | 0.029792 | 311.8308 | 0.033383 | 0 | 0 | 0.066765 | 318.8044 | 0.048508 | 0 | 0 | 0.097017 | 319.0627 | 0.049069 | 0 | 0 | 0.098137 | 319.2349 | 0.049442 | 0 | 0 | 0.098884 | 319.4932 | 0.050002 | 0 | 0 | 0.1 | 319.7514 | 0.050563 | 0 | 0 | 0.10113 | 320.0097 | 0.051123 | 0 | 0 | 0.10225 | 320.3541 | 0.05187 | 0 | 0 | 0.10374 | 320.6124 | 0.05243 | 0 | 0 | 0.10486 | 320.7846 | 0.052803 | 0 | 0 | 0.10561 | 321.0429 | 0.053364 | 0 | 0 | 0.10673 | 321.215 | 0.053737 | 0 | 0 | 0.10747 | 321.4733 | 0.054297 | 0 | 0 | 0.10859 | 321.7316 | 0.054857 | 0 | 0 | 0.10971 | 321.9038 | 0.055231 | 0 | 0 | 0.11046 | 322.1621 | 0.055791 | 0 | 0 | 0.11158 | 322.4203 | 0.056351 | 0 | 0 | 0.1127 | 322.5064 | 0.056538 | 0 | 0 | 0.11308 | 322.7647 | 0.057098 | 0 | 0 | 0.1142 | 323.023 | 0.057659 | 0 | 0 | 0.11532 | 323.1952 | 0.058032 | 0 | 0 | 0.11606 | 323.4535 | 0.058592 | 0 | 0 | 0.11718 | 323.6257 | 0.058966 | 0 | 0 | 0.11793 | 323.7978 | 0.059339 | 0 | 0 | 0.11868
2017-12-15 20:00 | 274.9342 | 0.81947 |  | 288.6987 | 0 | 0 | 0 | 0 | 296.8114 | 0.00080565 | 0 | 0 | 0.0016113 | 303.4491 | 0.015203 | 0 | 0 | 0.030406 | 303.695 | 0.015736 | 0 | 0 | 0.031472 | 303.8589 | 0.016092 | 0 | 0 | 0.032183 | 304.1047 | 0.016625 | 0 | 0 | 0.033249 | 304.3505 | 0.017158 | 0 | 0 | 0.034316 | 304.5964 | 0.017691 | 0 | 0 | 0.035382 | 304.9242 | 0.018402 | 0 | 0 | 0.036804 | 305.17 | 0.018935 | 0 | 0 | 0.037871 | 305.3339 | 0.019291 | 0 | 0 | 0.038582 | 305.5797 | 0.019824 | 0 | 0 | 0.039648 | 305.7436 | 0.02018 | 0 | 0 | 0.040359 | 305.9895 | 0.020713 | 0 | 0 | 0.041426 | 306.2353 | 0.021246 | 0 | 0 | 0.042492 | 306.3992 | 0.021602 | 0 | 0 | 0.043203 | 306.6451 | 0.022135 | 0 | 0 | 0.04427 | 306.8909 | 0.022668 | 0 | 0 | 0.045336 | 306.9728 | 0.022846 | 0 | 0 | 0.045691 | 307.2187 | 0.023379 | 0 | 0 | 0.046758 | 307.4645 | 0.023912 | 0 | 0 | 0.047824 | 307.6284 | 0.024268 | 0 | 0 | 0.048535 | 307.8743 | 0.024801 | 0 | 0 | 0.049602 | 308.0382 | 0.025156 | 0 | 0 | 0.050313 | 308.202 | 0.025512 | 0 | 0 | 0.051024
2017-12-15 21:00 | 286.8776 | 0.85507 |  | 301.2401 | 0.010411 | 0 | 0 | 0.020823 | 309.7052 | 0.028772 | 0 | 0 | 0.057545 | 316.6313 | 0.043795 | 0 | 0 | 0.08759 | 316.8878 | 0.044351 | 0 | 0 | 0.088702 | 317.0588 | 0.044722 | 0 | 0 | 0.089444 | 317.3153 | 0.045279 | 0 | 0 | 0.090557 | 317.5718 | 0.045835 | 0 | 0 | 0.09167 | 317.8284 | 0.046391 | 0 | 0 | 0.092783 | 318.1704 | 0.047133 | 0 | 0 | 0.094266 | 318.4269 | 0.04769 | 0 | 0 | 0.095379 | 318.5979 | 0.048061 | 0 | 0 | 0.096121 | 318.8544 | 0.048617 | 0 | 0 | 0.097234 | 319.0254 | 0.048988 | 0 | 0 | 0.097976 | 319.282 | 0.049544 | 0 | 0 | 0.099088 | 319.5385 | 0.050101 | 0 | 0 | 0.1002 | 319.7095 | 0.050472 | 0 | 0 | 0.10094 | 319.966 | 0.051028 | 0 | 0 | 0.10206 | 320.2225 | 0.051584 | 0 | 0 | 0.10317 | 320.308 | 0.05177 | 0 | 0 | 0.10354 | 320.5646 | 0.052326 | 0 | 0 | 0.10465 | 320.8211 | 0.052883 | 0 | 0 | 0.10577 | 320.9921 | 0.053254 | 0 | 0 | 0.10651 | 321.2486 | 0.05381 | 0 | 0 | 0.10762 | 321.4196 | 0.054181 | 0 | 0 | 0.10836 | 321.5906 | 0.054552 | 0 | 0 | 0.1091
2017-12-15 22:00 | 271.6438 | 0.80966 |  | 285.2435 | 0 | 0 | 0 | 0 | 293.2592 | 0 | 0 | 0 | 0 | 299.8174 | 0.0073257 | 0 | 0 | 0.014651 | 300.0603 | 0.0078525 | 0 | 0 | 0.015705 | 300.2223 | 0.0082037 | 0 | 0 | 0.016407 | 300.4652 | 0.0087306 | 0 | 0 | 0.017461 | 300.7081 | 0.0092574 | 0 | 0 | 0.018515 | 300.951 | 0.0097843 | 0 | 0 | 0.019569 | 301.2748 | 0.010487 | 0 | 0 | 0.020973 | 301.5177 | 0.011014 | 0 | 0 | 0.022027 | 301.6797 | 0.011365 | 0 | 0 | 0.02273 | 301.9226 | 0.011892 | 0 | 0 | 0.023783 | 302.0845 | 0.012243 | 0 | 0 | 0.024486 | 302.3274 | 0.01277 | 0 | 0 | 0.025539 | 302.5703 | 0.013297 | 0 | 0 | 0.026593 | 302.7322 | 0.013648 | 0 | 0 | 0.027296 | 302.9751 | 0.014175 | 0 | 0 | 0.028349 | 303.218 | 0.014702 | 0 | 0 | 0.029403 | 303.299 | 0.014877 | 0 | 0 | 0.029754 | 303.5419 | 0.015404 | 0 | 0 | 0.030808 | 303.7848 | 0.015931 | 0 | 0 | 0.031862 | 303.9467 | 0.016282 | 0 | 0 | 0.032564 | 304.1896 | 0.016809 | 0 | 0 | 0.033618 | 304.3515 | 0.01716 | 0 | 0 | 0.03432 | 304.5135 | 0.017511 | 0 | 0 | 0.035023
2017-12-15 23:00 | 279.592 | 0.83335 |  | 293.5897 | 0 | 0 | 0 | 0 | 301.8399 | 0.011712 | 0 | 0 | 0.023425 | 308.5901 | 0.026353 | 0 | 0 | 0.052707 | 308.8401 | 0.026896 | 0 | 0 | 0.053792 | 309.0067 | 0.027257 | 0 | 0 | 0.054515 | 309.2567 | 0.0278 | 0 | 0 | 0.055599 | 309.5068 | 0.028342 | 0 | 0 | 0.056684 | 309.7568 | 0.028884 | 0 | 0 | 0.057768 | 310.0901 | 0.029607 | 0 | 0 | 0.059214 | 310.3401 | 0.030149 | 0 | 0 | 0.060299 | 310.5068 | 0.030511 | 0 | 0 | 0.061022 | 310.7568 | 0.031053 | 0 | 0 | 0.062106 | 310.9235 | 0.031415 | 0 | 0 | 0.062829 | 311.1735 | 0.031957 | 0 | 0 | 0.063914 | 311.4235 | 0.032499 | 0 | 0 | 0.064998 | 311.5901 | 0.032861 | 0 | 0 | 0.065721 | 311.8401 | 0.033403 | 0 | 0 | 0.066806 | 312.0901 | 0.033945 | 0 | 0 | 0.06789 | 312.1735 | 0.034126 | 0 | 0 | 0.068252 | 312.4235 | 0.034668 | 0 | 0 | 0.069336 | 312.6735 | 0.03521 | 0 | 0 | 0.070421 | 312.8402 | 0.035572 | 0 | 0 | 0.071144 | 313.0902 | 0.036114 | 0 | 0 | 0.072228 | 313.2568 | 0.036476 | 0 | 0 | 0.072951 | 313.4235 | 0.036837 | 0 | 0 | 0.073674
2017-12-16 | 291.9385 | 0.87015 |  | 306.5543 | 0.021938 | 0 | 0 | 0.043876 | 315.1688 | 0.040623 | 0 | 0 | 0.081245 | 322.217 | 0.05591 | 0 | 0 | 0.11182 | 322.4781 | 0.056477 | 0 | 0 | 0.11295 | 322.6521 | 0.056854 | 0 | 0 | 0.11371 | 322.9131 | 0.05742 | 0 | 0 | 0.11484 | 323.1742 | 0.057986 | 0 | 0 | 0.11597 | 323.4352 | 0.058553 | 0 | 0 | 0.11711 | 323.7833 | 0.059308 | 0 | 0 | 0.11862 | 324.0443 | 0.059874 | 0 | 0 | 0.11975 | 324.2184 | 0.060251 | 0 | 0 | 0.1205 | 324.4794 | 0.060817 | 0 | 0 | 0.12163 | 324.6534 | 0.061195 | 0 | 0 | 0.12239 | 324.9145 | 0.061761 | 0 | 0 | 0.12352 | 325.1755 | 0.062327 | 0 | 0 | 0.12465 | 325.3496 | 0.062705 | 0 | 0 | 0.12541 | 325.6106 | 0.063271 | 0 | 0 | 0.12654 | 325.8716 | 0.063837 | 0 | 0 | 0.12767 | 325.9587 | 0.064026 | 0 | 0 | 0.12805 | 326.2197 | 0.064592 | 0 | 0 | 0.12918 | 326.4808 | 0.065158 | 0 | 0 | 0.13032 | 326.6548 | 0.065536 | 0 | 0 | 0.13107 | 326.9158 | 0.066102 | 0 | 0 | 0.1322 | 327.0899 | 0.06648 | 0 | 0 | 0.13296 | 327.2639 | 0.066857 | 0 | 0 | 0.13371
2017-12-16 01:00 | 286.8819 | 0.85508 |  | 301.2446 | 0.010421 | 0 | 0 | 0.020842 | 309.7099 | 0.028782 | 0 | 0 | 0.057565 | 316.636 | 0.043805 | 0 | 0 | 0.08761 | 316.8926 | 0.044362 | 0 | 0 | 0.088723 | 317.0636 | 0.044733 | 0 | 0 | 0.089465 | 317.3201 | 0.045289 | 0 | 0 | 0.090578 | 317.5766 | 0.045845 | 0 | 0 | 0.091691 | 317.8331 | 0.046402 | 0 | 0 | 0.092803 | 318.1752 | 0.047144 | 0 | 0 | 0.094287 | 318.4317 | 0.0477 | 0 | 0 | 0.0954 | 318.6027 | 0.048071 | 0 | 0 | 0.096142 | 318.8592 | 0.048627 | 0 | 0 | 0.097255 | 319.0303 | 0.048998 | 0 | 0 | 0.097997 | 319.2868 | 0.049555 | 0 | 0 | 0.099109 | 319.5433 | 0.050111 | 0 | 0 | 0.10022 | 319.7143 | 0.050482 | 0 | 0 | 0.10096 | 319.9708 | 0.051038 | 0 | 0 | 0.10208 | 320.2274 | 0.051595 | 0 | 0 | 0.10319 | 320.3129 | 0.05178 | 0 | 0 | 0.10356 | 320.5694 | 0.052337 | 0 | 0 | 0.10467 | 320.8259 | 0.052893 | 0 | 0 | 0.10579 | 320.9969 | 0.053264 | 0 | 0 | 0.10653 | 321.2535 | 0.05382 | 0 | 0 | 0.10764 | 321.4245 | 0.054191 | 0 | 0 | 0.10838 | 321.5955 | 0.054562 | 0 | 0 | 0.10912
2017-12-16 02:00 | 298.8536 | 0.89076 |  | 313.8156 | 0.037688 | 0 | 0 | 0.075375 | 322.6342 | 0.056815 | 0 | 0 | 0.11363 | 329.8493 | 0.072465 | 0 | 0 | 0.14493 | 330.1166 | 0.073044 | 0 | 0 | 0.14609 | 330.2947 | 0.073431 | 0 | 0 | 0.14686 | 330.5619 | 0.07401 | 0 | 0 | 0.14802 | 330.8292 | 0.07459 | 0 | 0 | 0.14918 | 331.0964 | 0.07517 | 0 | 0 | 0.15034 | 331.4527 | 0.075943 | 0 | 0 | 0.15189 | 331.7199 | 0.076522 | 0 | 0 | 0.15304 | 331.8981 | 0.076909 | 0 | 0 | 0.15382 | 332.1653 | 0.077488 | 0 | 0 | 0.15498 | 332.3435 | 0.077875 | 0 | 0 | 0.15575 | 332.6107 | 0.078454 | 0 | 0 | 0.15691 | 332.8779 | 0.079034 | 0 | 0 | 0.15807 | 333.0561 | 0.07942 | 0 | 0 | 0.15884 | 333.3233 | 0.08 | 0 | 0 | 0.16 | 333.5905 | 0.08058 | 0 | 0 | 0.16116 | 333.6796 | 0.080773 | 0 | 0 | 0.16155 | 333.9468 | 0.081352 | 0 | 0 | 0.1627 | 334.2141 | 0.081932 | 0 | 0 | 0.16386 | 334.3922 | 0.082318 | 0 | 0 | 0.16464 | 334.6594 | 0.082898 | 0 | 0 | 0.1658 | 334.8376 | 0.083284 | 0 | 0 | 0.16657 | 335.0158 | 0.083671 | 0 | 0 | 0.16734
2017-12-16 03:00 | 303.1867 | 0.90368 |  | 318.3657 | 0.047557 | 0 | 0 | 0.095114 | 327.3121 | 0.066962 | 0 | 0 | 0.13392 | 334.6319 | 0.082838 | 0 | 0 | 0.16568 | 334.903 | 0.083426 | 0 | 0 | 0.16685 | 335.0837 | 0.083818 | 0 | 0 | 0.16764 | 335.3548 | 0.084406 | 0 | 0 | 0.16881 | 335.6259 | 0.084994 | 0 | 0 | 0.16999 | 335.897 | 0.085582 | 0 | 0 | 0.17116 | 336.2585 | 0.086366 | 0 | 0 | 0.17273 | 336.5296 | 0.086954 | 0 | 0 | 0.17391 | 336.7103 | 0.087346 | 0 | 0 | 0.17469 | 336.9814 | 0.087934 | 0 | 0 | 0.17587 | 337.1622 | 0.088326 | 0 | 0 | 0.17665 | 337.4333 | 0.088914 | 0 | 0 | 0.17783 | 337.7044 | 0.089502 | 0 | 0 | 0.179 | 337.8851 | 0.089894 | 0 | 0 | 0.17979 | 338.1562 | 0.090482 | 0 | 0 | 0.18096 | 338.4273 | 0.09107 | 0 | 0 | 0.18214 | 338.5177 | 0.091267 | 0 | 0 | 0.18253 | 338.7888 | 0.091855 | 0 | 0 | 0.18371 | 339.0599 | 0.092443 | 0 | 0 | 0.18489 | 339.2406 | 0.092835 | 0 | 0 | 0.18567 | 339.5117 | 0.093423 | 0 | 0 | 0.18685 | 339.6925 | 0.093815 | 0 | 0 | 0.18763 | 339.8732 | 0.094207 | 0 | 0 | 0.18841
2017-12-16 04:00 | 293.6996 | 0.8754 |  | 308.4035 | 0.025949 | 0 | 0 | 0.051898 | 317.07 | 0.044746 | 0 | 0 | 0.089493 | 324.1607 | 0.060126 | 0 | 0 | 0.12025 | 324.4234 | 0.060696 | 0 | 0 | 0.12139 | 324.5984 | 0.061076 | 0 | 0 | 0.12215 | 324.8611 | 0.061645 | 0 | 0 | 0.12329 | 325.1237 | 0.062215 | 0 | 0 | 0.12443 | 325.3863 | 0.062785 | 0 | 0 | 0.12557 | 325.7365 | 0.063544 | 0 | 0 | 0.12709 | 325.9991 | 0.064114 | 0 | 0 | 0.12823 | 326.1742 | 0.064493 | 0 | 0 | 0.12899 | 326.4368 | 0.065063 | 0 | 0 | 0.13013 | 326.6119 | 0.065443 | 0 | 0 | 0.13089 | 326.8745 | 0.066012 | 0 | 0 | 0.13202 | 327.1371 | 0.066582 | 0 | 0 | 0.13316 | 327.3122 | 0.066962 | 0 | 0 | 0.13392 | 327.5748 | 0.067531 | 0 | 0 | 0.13506 | 327.8374 | 0.068101 | 0 | 0 | 0.1362 | 327.925 | 0.068291 | 0 | 0 | 0.13658 | 328.1876 | 0.068861 | 0 | 0 | 0.13772 | 328.4502 | 0.06943 | 0 | 0 | 0.13886 | 328.6253 | 0.06981 | 0 | 0 | 0.13962 | 328.8879 | 0.07038 | 0 | 0 | 0.14076 | 329.063 | 0.070759 | 0 | 0 | 0.14152 | 329.2381 | 0.071139 | 0 | 0 | 0.14228
2017-12-16 05:00 | 310.3661 | 0.92508 |  | 325.9045 | 0.063909 | 0 | 0 | 0.12782 | 335.0628 | 0.083773 | 0 | 0 | 0.16755 | 342.5559 | 0.10003 | 0 | 0 | 0.20005 | 342.8334 | 0.10063 | 0 | 0 | 0.20125 | 343.0185 | 0.10103 | 0 | 0 | 0.20206 | 343.296 | 0.10163 | 0 | 0 | 0.20326 | 343.5735 | 0.10223 | 0 | 0 | 0.20447 | 343.851 | 0.10283 | 0 | 0 | 0.20567 | 344.2211 | 0.10364 | 0 | 0 | 0.20727 | 344.4986 | 0.10424 | 0 | 0 | 0.20848 | 344.6836 | 0.10464 | 0 | 0 | 0.20928 | 344.9611 | 0.10524 | 0 | 0 | 0.21048 | 345.1461 | 0.10564 | 0 | 0 | 0.21129 | 345.4237 | 0.10625 | 0 | 0 | 0.21249 | 345.7012 | 0.10685 | 0 | 0 | 0.2137 | 345.8862 | 0.10725 | 0 | 0 | 0.2145 | 346.1637 | 0.10785 | 0 | 0 | 0.2157 | 346.4412 | 0.10845 | 0 | 0 | 0.21691 | 346.5337 | 0.10865 | 0 | 0 | 0.21731 | 346.8113 | 0.10926 | 0 | 0 | 0.21851 | 347.0888 | 0.10986 | 0 | 0 | 0.21971 | 347.2738 | 0.11026 | 0 | 0 | 0.22052 | 347.5513 | 0.11086 | 0 | 0 | 0.22172 | 347.7363 | 0.11126 | 0 | 0 | 0.22252 | 347.9214 | 0.11166 | 0 | 0 | 0.22333
2017-12-16 06:00 | 311.7235 | 0.92912 |  | 327.3299 | 0.067 | 0 | 0 | 0.134 | 336.5282 | 0.086951 | 0 | 0 | 0.1739 | 344.0541 | 0.10327 | 0 | 0 | 0.20655 | 344.3328 | 0.10388 | 0 | 0 | 0.20776 | 344.5186 | 0.10428 | 0 | 0 | 0.20857 | 344.7974 | 0.10489 | 0 | 0 | 0.20977 | 345.0761 | 0.10549 | 0 | 0 | 0.21098 | 345.3549 | 0.1061 | 0 | 0 | 0.21219 | 345.7265 | 0.1069 | 0 | 0 | 0.2138 | 346.0052 | 0.10751 | 0 | 0 | 0.21501 | 346.1911 | 0.10791 | 0 | 0 | 0.21582 | 346.4698 | 0.10851 | 0 | 0 | 0.21703 | 346.6556 | 0.10892 | 0 | 0 | 0.21784 | 346.9344 | 0.10952 | 0 | 0 | 0.21904 | 347.2131 | 0.11013 | 0 | 0 | 0.22025 | 347.3989 | 0.11053 | 0 | 0 | 0.22106 | 347.6777 | 0.11113 | 0 | 0 | 0.22227 | 347.9564 | 0.11174 | 0 | 0 | 0.22348 | 348.0493 | 0.11194 | 0 | 0 | 0.22388 | 348.328 | 0.11255 | 0 | 0 | 0.22509 | 348.6068 | 0.11315 | 0 | 0 | 0.2263 | 348.7926 | 0.11355 | 0 | 0 | 0.22711 | 349.0713 | 0.11416 | 0 | 0 | 0.22831 | 349.2572 | 0.11456 | 0 | 0 | 0.22912 | 349.443 | 0.11496 | 0 | 0 | 0.22993
2017-12-16 07:00 | 316.4152 | 0.94311 |  | 332.2565 | 0.077686 | 0 | 0 | 0.15537 | 341.5932 | 0.097937 | 0 | 0 | 0.19587 | 349.2324 | 0.11451 | 0 | 0 | 0.22901 | 349.5153 | 0.11512 | 0 | 0 | 0.23024 | 349.7039 | 0.11553 | 0 | 0 | 0.23106 | 349.9869 | 0.11614 | 0 | 0 | 0.23229 | 350.2698 | 0.11676 | 0 | 0 | 0.23351 | 350.5527 | 0.11737 | 0 | 0 | 0.23474 | 350.93 | 0.11819 | 0 | 0 | 0.23638 | 351.2129 | 0.1188 | 0 | 0 | 0.2376 | 351.4015 | 0.11921 | 0 | 0 | 0.23842 | 351.6845 | 0.11983 | 0 | 0 | 0.23965 | 351.8731 | 0.12023 | 0 | 0 | 0.24047 | 352.156 | 0.12085 | 0 | 0 | 0.2417 | 352.439 | 0.12146 | 0 | 0 | 0.24292 | 352.6276 | 0.12187 | 0 | 0 | 0.24374 | 352.9105 | 0.12248 | 0 | 0 | 0.24497 | 353.1934 | 0.1231 | 0 | 0 | 0.2462 | 353.2877 | 0.1233 | 0 | 0 | 0.24661 | 353.5707 | 0.12392 | 0 | 0 | 0.24783 | 353.8536 | 0.12453 | 0 | 0 | 0.24906 | 354.0422 | 0.12494 | 0 | 0 | 0.24988 | 354.3252 | 0.12555 | 0 | 0 | 0.25111 | 354.5138 | 0.12596 | 0 | 0 | 0.25192 | 354.7024 | 0.12637 | 0 | 0 | 0.25274
2017-12-16 08:00 | 310.7739 | 0.92629 |  | 326.3327 | 0.064837 | 0 | 0 | 0.12967 | 335.503 | 0.084728 | 0 | 0 | 0.16946 | 343.006 | 0.101 | 0 | 0 | 0.202 | 343.2839 | 0.1016 | 0 | 0 | 0.20321 | 343.4691 | 0.10201 | 0 | 0 | 0.20401 | 343.747 | 0.10261 | 0 | 0 | 0.20522 | 344.0249 | 0.10321 | 0 | 0 | 0.20642 | 344.3028 | 0.10381 | 0 | 0 | 0.20763 | 344.6733 | 0.10462 | 0 | 0 | 0.20924 | 344.9512 | 0.10522 | 0 | 0 | 0.21044 | 345.1365 | 0.10562 | 0 | 0 | 0.21125 | 345.4143 | 0.10623 | 0 | 0 | 0.21245 | 345.5996 | 0.10663 | 0 | 0 | 0.21325 | 345.8775 | 0.10723 | 0 | 0 | 0.21446 | 346.1554 | 0.10783 | 0 | 0 | 0.21567 | 346.3406 | 0.10823 | 0 | 0 | 0.21647 | 346.6185 | 0.10884 | 0 | 0 | 0.21767 | 346.8964 | 0.10944 | 0 | 0 | 0.21888 | 346.989 | 0.10964 | 0 | 0 | 0.21928 | 347.2669 | 0.11024 | 0 | 0 | 0.22049 | 347.5448 | 0.11085 | 0 | 0 | 0.22169 | 347.7301 | 0.11125 | 0 | 0 | 0.2225 | 348.008 | 0.11185 | 0 | 0 | 0.2237 | 348.1932 | 0.11225 | 0 | 0 | 0.22451 | 348.3785 | 0.11265 | 0 | 0 | 0.22531
2017-12-16 09:00 | 316.267 | 0.94266 |  | 332.1009 | 0.077348 | 0 | 0 | 0.1547 | 341.4332 | 0.09759 | 0 | 0 | 0.19518 | 349.0688 | 0.11415 | 0 | 0 | 0.2283 | 349.3516 | 0.11477 | 0 | 0 | 0.22953 | 349.5402 | 0.11517 | 0 | 0 | 0.23035 | 349.823 | 0.11579 | 0 | 0 | 0.23158 | 350.1058 | 0.1164 | 0 | 0 | 0.2328 | 350.3886 | 0.11701 | 0 | 0 | 0.23403 | 350.7656 | 0.11783 | 0 | 0 | 0.23566 | 351.0484 | 0.11845 | 0 | 0 | 0.23689 | 351.237 | 0.11885 | 0 | 0 | 0.23771 | 351.5198 | 0.11947 | 0 | 0 | 0.23894 | 351.7083 | 0.11988 | 0 | 0 | 0.23975 | 351.9911 | 0.12049 | 0 | 0 | 0.24098 | 352.2739 | 0.1211 | 0 | 0 | 0.24221 | 352.4624 | 0.12151 | 0 | 0 | 0.24303 | 352.7452 | 0.12213 | 0 | 0 | 0.24425 | 353.028 | 0.12274 | 0 | 0 | 0.24548 | 353.1223 | 0.12294 | 0 | 0 | 0.24589 | 353.4051 | 0.12356 | 0 | 0 | 0.24711 | 353.6879 | 0.12417 | 0 | 0 | 0.24834 | 353.8764 | 0.12458 | 0 | 0 | 0.24916 | 354.1592 | 0.12519 | 0 | 0 | 0.25039 | 354.3478 | 0.1256 | 0 | 0 | 0.2512 | 354.5363 | 0.12601 | 0 | 0 | 0.25202
2017-12-16 10:00 | 324.0313 | 0.96581 |  | 340.2538 | 0.095032 | 0 | 0 | 0.19006 | 349.8153 | 0.11577 | 0 | 0 | 0.23154 | 357.6384 | 0.13274 | 0 | 0 | 0.26548 | 357.9281 | 0.13337 | 0 | 0 | 0.26674 | 358.1213 | 0.13379 | 0 | 0 | 0.26757 | 358.411 | 0.13442 | 0 | 0 | 0.26883 | 358.7007 | 0.13504 | 0 | 0 | 0.27009 | 358.9905 | 0.13567 | 0 | 0 | 0.27134 | 359.3768 | 0.13651 | 0 | 0 | 0.27302 | 359.6666 | 0.13714 | 0 | 0 | 0.27428 | 359.8597 | 0.13756 | 0 | 0 | 0.27511 | 360.1495 | 0.13819 | 0 | 0 | 0.27637 | 360.3426 | 0.1386 | 0 | 0 | 0.27721 | 360.6324 | 0.13923 | 0 | 0 | 0.27847 | 360.9221 | 0.13986 | 0 | 0 | 0.27972 | 361.1153 | 0.14028 | 0 | 0 | 0.28056 | 361.405 | 0.14091 | 0 | 0 | 0.28182 | 361.6948 | 0.14154 | 0 | 0 | 0.28308 | 361.7913 | 0.14175 | 0 | 0 | 0.28349 | 362.0811 | 0.14238 | 0 | 0 | 0.28475 | 362.3708 | 0.143 | 0 | 0 | 0.28601 | 362.564 | 0.14342 | 0 | 0 | 0.28685 | 362.8537 | 0.14405 | 0 | 0 | 0.2881 | 363.0469 | 0.14447 | 0 | 0 | 0.28894 | 363.24 | 0.14489 | 0 | 0 | 0.28978
2017-12-16 11:00 | 324.1573 | 0.96618 |  | 340.3861 | 0.095319 | 0 | 0 | 0.19064 | 349.9513 | 0.11607 | 0 | 0 | 0.23213 | 357.7774 | 0.13304 | 0 | 0 | 0.26608 | 358.0672 | 0.13367 | 0 | 0 | 0.26734 | 358.2605 | 0.13409 | 0 | 0 | 0.26818 | 358.5503 | 0.13472 | 0 | 0 | 0.26943 | 358.8402 | 0.13535 | 0 | 0 | 0.27069 | 359.1301 | 0.13597 | 0 | 0 | 0.27195 | 359.5165 | 0.13681 | 0 | 0 | 0.27363 | 359.8064 | 0.13744 | 0 | 0 | 0.27488 | 359.9996 | 0.13786 | 0 | 0 | 0.27572 | 360.2895 | 0.13849 | 0 | 0 | 0.27698 | 360.4827 | 0.13891 | 0 | 0 | 0.27782 | 360.7726 | 0.13954 | 0 | 0 | 0.27907 | 361.0624 | 0.14017 | 0 | 0 | 0.28033 | 361.2557 | 0.14059 | 0 | 0 | 0.28117 | 361.5455 | 0.14121 | 0 | 0 | 0.28243 | 361.8354 | 0.14184 | 0 | 0 | 0.28369 | 361.932 | 0.14205 | 0 | 0 | 0.2841 | 362.2218 | 0.14268 | 0 | 0 | 0.28536 | 362.5117 | 0.14331 | 0 | 0 | 0.28662 | 362.7049 | 0.14373 | 0 | 0 | 0.28746 | 362.9948 | 0.14436 | 0 | 0 | 0.28871 | 363.188 | 0.14478 | 0 | 0 | 0.28955 | 363.3813 | 0.1452 | 0 | 0 | 0.29039
2017-12-16 12:00 | 320.7349 | 0.95598 |  | 336.7924 | 0.087524 | 0 | 0 | 0.17505 | 346.2566 | 0.10805 | 0 | 0 | 0.2161 | 354.0001 | 0.12485 | 0 | 0 | 0.2497 | 354.2869 | 0.12547 | 0 | 0 | 0.25094 | 354.4781 | 0.12588 | 0 | 0 | 0.25177 | 354.7649 | 0.12651 | 0 | 0 | 0.25301 | 355.0517 | 0.12713 | 0 | 0 | 0.25426 | 355.3384 | 0.12775 | 0 | 0 | 0.2555 | 355.7208 | 0.12858 | 0 | 0 | 0.25716 | 356.0076 | 0.1292 | 0 | 0 | 0.2584 | 356.1988 | 0.12962 | 0 | 0 | 0.25923 | 356.4856 | 0.13024 | 0 | 0 | 0.26048 | 356.6768 | 0.13065 | 0 | 0 | 0.26131 | 356.9636 | 0.13128 | 0 | 0 | 0.26255 | 357.2504 | 0.1319 | 0 | 0 | 0.2638 | 357.4416 | 0.13231 | 0 | 0 | 0.26462 | 357.7284 | 0.13293 | 0 | 0 | 0.26587 | 358.0152 | 0.13356 | 0 | 0 | 0.26711 | 358.1108 | 0.13376 | 0 | 0 | 0.26753 | 358.3976 | 0.13439 | 0 | 0 | 0.26877 | 358.6844 | 0.13501 | 0 | 0 | 0.27002 | 358.8756 | 0.13542 | 0 | 0 | 0.27085 | 359.1624 | 0.13604 | 0 | 0 | 0.27209 | 359.3536 | 0.13646 | 0 | 0 | 0.27292 | 359.5448 | 0.13687 | 0 | 0 | 0.27375
2017-12-16 13:00 | 312.973 | 0.93285 |  | 328.6419 | 0.069846 | 0 | 0 | 0.13969 | 337.8771 | 0.089877 | 0 | 0 | 0.17975 | 345.4332 | 0.10627 | 0 | 0 | 0.21253 | 345.713 | 0.10687 | 0 | 0 | 0.21375 | 345.8996 | 0.10728 | 0 | 0 | 0.21456 | 346.1794 | 0.10788 | 0 | 0 | 0.21577 | 346.4593 | 0.10849 | 0 | 0 | 0.21698 | 346.7391 | 0.1091 | 0 | 0 | 0.2182 | 347.1123 | 0.10991 | 0 | 0 | 0.21982 | 347.3921 | 0.11052 | 0 | 0 | 0.22103 | 347.5787 | 0.11092 | 0 | 0 | 0.22184 | 347.8586 | 0.11153 | 0 | 0 | 0.22305 | 348.0451 | 0.11193 | 0 | 0 | 0.22386 | 348.325 | 0.11254 | 0 | 0 | 0.22508 | 348.6048 | 0.11315 | 0 | 0 | 0.22629 | 348.7914 | 0.11355 | 0 | 0 | 0.2271 | 349.0713 | 0.11416 | 0 | 0 | 0.22831 | 349.3511 | 0.11476 | 0 | 0 | 0.22953 | 349.4444 | 0.11497 | 0 | 0 | 0.22993 | 349.7243 | 0.11557 | 0 | 0 | 0.23115 | 350.0041 | 0.11618 | 0 | 0 | 0.23236 | 350.1907 | 0.11659 | 0 | 0 | 0.23317 | 350.4705 | 0.11719 | 0 | 0 | 0.23438 | 350.6571 | 0.1176 | 0 | 0 | 0.23519 | 350.8437 | 0.118 | 0 | 0 | 0.236
2017-12-16 14:00 | 316.1907 | 0.94244 |  | 332.0207 | 0.077175 | 0 | 0 | 0.15435 | 341.3508 | 0.097412 | 0 | 0 | 0.19482 | 348.9846 | 0.11397 | 0 | 0 | 0.22794 | 349.2673 | 0.11458 | 0 | 0 | 0.22916 | 349.4558 | 0.11499 | 0 | 0 | 0.22998 | 349.7385 | 0.1156 | 0 | 0 | 0.23121 | 350.0213 | 0.11622 | 0 | 0 | 0.23244 | 350.304 | 0.11683 | 0 | 0 | 0.23366 | 350.681 | 0.11765 | 0 | 0 | 0.2353 | 350.9637 | 0.11826 | 0 | 0 | 0.23652 | 351.1522 | 0.11867 | 0 | 0 | 0.23734 | 351.4349 | 0.11928 | 0 | 0 | 0.23857 | 351.6234 | 0.11969 | 0 | 0 | 0.23939 | 351.9061 | 0.12031 | 0 | 0 | 0.24061 | 352.1889 | 0.12092 | 0 | 0 | 0.24184 | 352.3774 | 0.12133 | 0 | 0 | 0.24266 | 352.6601 | 0.12194 | 0 | 0 | 0.24388 | 352.9428 | 0.12255 | 0 | 0 | 0.24511 | 353.0371 | 0.12276 | 0 | 0 | 0.24552 | 353.3198 | 0.12337 | 0 | 0 | 0.24674 | 353.6025 | 0.12399 | 0 | 0 | 0.24797 | 353.791 | 0.12439 | 0 | 0 | 0.24879 | 354.0737 | 0.12501 | 0 | 0 | 0.25002 | 354.2622 | 0.12542 | 0 | 0 | 0.25083 | 354.4507 | 0.12583 | 0 | 0 | 0.25165
2017-12-16 15:00 | 313.6341 | 0.93482 |  | 329.3361 | 0.071352 | 0 | 0 | 0.1427 | 338.5908 | 0.091425 | 0 | 0 | 0.18285 | 346.1628 | 0.10785 | 0 | 0 | 0.2157 | 346.4432 | 0.10846 | 0 | 0 | 0.21691 | 346.6302 | 0.10886 | 0 | 0 | 0.21773 | 346.9107 | 0.10947 | 0 | 0 | 0.21894 | 347.1911 | 0.11008 | 0 | 0 | 0.22016 | 347.4715 | 0.11069 | 0 | 0 | 0.22137 | 347.8455 | 0.1115 | 0 | 0 | 0.223 | 348.1259 | 0.11211 | 0 | 0 | 0.22421 | 348.3129 | 0.11251 | 0 | 0 | 0.22502 | 348.5933 | 0.11312 | 0 | 0 | 0.22624 | 348.7803 | 0.11353 | 0 | 0 | 0.22705 | 349.0607 | 0.11413 | 0 | 0 | 0.22827 | 349.3412 | 0.11474 | 0 | 0 | 0.22949 | 349.5281 | 0.11515 | 0 | 0 | 0.2303 | 349.8086 | 0.11576 | 0 | 0 | 0.23151 | 350.089 | 0.11636 | 0 | 0 | 0.23273 | 350.1825 | 0.11657 | 0 | 0 | 0.23314 | 350.463 | 0.11718 | 0 | 0 | 0.23435 | 350.7434 | 0.11778 | 0 | 0 | 0.23557 | 350.9304 | 0.11819 | 0 | 0 | 0.23638 | 351.2108 | 0.1188 | 0 | 0 | 0.2376 | 351.3978 | 0.1192 | 0 | 0 | 0.23841 | 351.5847 | 0.11961 | 0 | 0 | 0.23922
2017-12-16 16:00 | 310.572 | 0.92569 |  | 326.1207 | 0.064377 | 0 | 0 | 0.12875 | 335.285 | 0.084255 | 0 | 0 | 0.16851 | 342.7831 | 0.10052 | 0 | 0 | 0.20104 | 343.0608 | 0.10112 | 0 | 0 | 0.20224 | 343.246 | 0.10152 | 0 | 0 | 0.20304 | 343.5237 | 0.10212 | 0 | 0 | 0.20425 | 343.8014 | 0.10273 | 0 | 0 | 0.20545 | 344.0791 | 0.10333 | 0 | 0 | 0.20666 | 344.4494 | 0.10413 | 0 | 0 | 0.20826 | 344.7271 | 0.10473 | 0 | 0 | 0.20947 | 344.9122 | 0.10514 | 0 | 0 | 0.21027 | 345.1899 | 0.10574 | 0 | 0 | 0.21148 | 345.3751 | 0.10614 | 0 | 0 | 0.21228 | 345.6528 | 0.10674 | 0 | 0 | 0.21348 | 345.9305 | 0.10734 | 0 | 0 | 0.21469 | 346.1156 | 0.10775 | 0 | 0 | 0.21549 | 346.3933 | 0.10835 | 0 | 0 | 0.2167 | 346.671 | 0.10895 | 0 | 0 | 0.2179 | 346.7636 | 0.10915 | 0 | 0 | 0.2183 | 347.0413 | 0.10975 | 0 | 0 | 0.21951 | 347.319 | 0.11036 | 0 | 0 | 0.22071 | 347.5041 | 0.11076 | 0 | 0 | 0.22152 | 347.7818 | 0.11136 | 0 | 0 | 0.22272 | 347.967 | 0.11176 | 0 | 0 | 0.22352 | 348.1521 | 0.11216 | 0 | 0 | 0.22433
2017-12-16 17:00 | 310.9606 | 0.92685 |  | 326.5288 | 0.065263 | 0 | 0 | 0.13053 | 335.7046 | 0.085165 | 0 | 0 | 0.17033 | 343.2121 | 0.10145 | 0 | 0 | 0.2029 | 343.4901 | 0.10205 | 0 | 0 | 0.2041 | 343.6755 | 0.10245 | 0 | 0 | 0.20491 | 343.9535 | 0.10306 | 0 | 0 | 0.20611 | 344.2316 | 0.10366 | 0 | 0 | 0.20732 | 344.5096 | 0.10426 | 0 | 0 | 0.20853 | 344.8804 | 0.10507 | 0 | 0 | 0.21013 | 345.1584 | 0.10567 | 0 | 0 | 0.21134 | 345.3438 | 0.10607 | 0 | 0 | 0.21214 | 345.6219 | 0.10668 | 0 | 0 | 0.21335 | 345.8072 | 0.10708 | 0 | 0 | 0.21416 | 346.0853 | 0.10768 | 0 | 0 | 0.21536 | 346.3633 | 0.10828 | 0 | 0 | 0.21657 | 346.5487 | 0.10869 | 0 | 0 | 0.21737 | 346.8268 | 0.10929 | 0 | 0 | 0.21858 | 347.1048 | 0.10989 | 0 | 0 | 0.21978 | 347.1975 | 0.11009 | 0 | 0 | 0.22019 | 347.4756 | 0.1107 | 0 | 0 | 0.22139 | 347.7536 | 0.1113 | 0 | 0 | 0.2226 | 347.939 | 0.1117 | 0 | 0 | 0.2234 | 348.217 | 0.1123 | 0 | 0 | 0.22461 | 348.4024 | 0.11271 | 0 | 0 | 0.22541 | 348.5878 | 0.11311 | 0 | 0 | 0.22622
2017-12-16 18:00 | 319.5653 | 0.9525 |  | 335.5642 | 0.08486 | 0 | 0 | 0.16972 | 344.9939 | 0.10531 | 0 | 0 | 0.21063 | 352.7092 | 0.12205 | 0 | 0 | 0.2441 | 352.9949 | 0.12267 | 0 | 0 | 0.24534 | 353.1854 | 0.12308 | 0 | 0 | 0.24616 | 353.4712 | 0.1237 | 0 | 0 | 0.2474 | 353.7569 | 0.12432 | 0 | 0 | 0.24864 | 354.0426 | 0.12494 | 0 | 0 | 0.24988 | 354.4236 | 0.12577 | 0 | 0 | 0.25153 | 354.7094 | 0.12639 | 0 | 0 | 0.25277 | 354.8999 | 0.1268 | 0 | 0 | 0.2536 | 355.1856 | 0.12742 | 0 | 0 | 0.25484 | 355.3761 | 0.12783 | 0 | 0 | 0.25566 | 355.6619 | 0.12845 | 0 | 0 | 0.2569 | 355.9476 | 0.12907 | 0 | 0 | 0.25814 | 356.1381 | 0.12949 | 0 | 0 | 0.25897 | 356.4239 | 0.13011 | 0 | 0 | 0.26021 | 356.7096 | 0.13072 | 0 | 0 | 0.26145 | 356.8049 | 0.13093 | 0 | 0 | 0.26186 | 357.0906 | 0.13155 | 0 | 0 | 0.2631 | 357.3764 | 0.13217 | 0 | 0 | 0.26434 | 357.5669 | 0.13258 | 0 | 0 | 0.26517 | 357.8526 | 0.1332 | 0 | 0 | 0.26641 | 358.0431 | 0.13362 | 0 | 0 | 0.26723 | 358.2336 | 0.13403 | 0 | 0 | 0.26806
2017-12-16 19:00 | 315.6083 | 0.9407 |  | 331.4091 | 0.075848 | 0 | 0 | 0.1517 | 340.7221 | 0.096048 | 0 | 0 | 0.1921 | 348.3417 | 0.11257 | 0 | 0 | 0.22515 | 348.6239 | 0.11319 | 0 | 0 | 0.22637 | 348.8121 | 0.1136 | 0 | 0 | 0.22719 | 349.0943 | 0.11421 | 0 | 0 | 0.22841 | 349.3765 | 0.11482 | 0 | 0 | 0.22964 | 349.6587 | 0.11543 | 0 | 0 | 0.23086 | 350.035 | 0.11625 | 0 | 0 | 0.2325 | 350.3172 | 0.11686 | 0 | 0 | 0.23372 | 350.5053 | 0.11727 | 0 | 0 | 0.23454 | 350.7876 | 0.11788 | 0 | 0 | 0.23576 | 350.9757 | 0.11829 | 0 | 0 | 0.23658 | 351.2579 | 0.1189 | 0 | 0 | 0.2378 | 351.5401 | 0.11951 | 0 | 0 | 0.23902 | 351.7283 | 0.11992 | 0 | 0 | 0.23984 | 352.0105 | 0.12053 | 0 | 0 | 0.24106 | 352.2927 | 0.12114 | 0 | 0 | 0.24229 | 352.3868 | 0.12135 | 0 | 0 | 0.2427 | 352.669 | 0.12196 | 0 | 0 | 0.24392 | 352.9512 | 0.12257 | 0 | 0 | 0.24515 | 353.1393 | 0.12298 | 0 | 0 | 0.24596 | 353.4215 | 0.12359 | 0 | 0 | 0.24719 | 353.6097 | 0.124 | 0 | 0 | 0.248 | 353.7978 | 0.12441 | 0 | 0 | 0.24882
2017-12-16 20:00 | 313.2295 | 0.93361 |  | 328.9112 | 0.07043 | 0 | 0 | 0.14086 | 338.154 | 0.090478 | 0 | 0 | 0.18096 | 345.7162 | 0.10688 | 0 | 0 | 0.21376 | 345.9963 | 0.10749 | 0 | 0 | 0.21498 | 346.183 | 0.10789 | 0 | 0 | 0.21579 | 346.4631 | 0.1085 | 0 | 0 | 0.217 | 346.7432 | 0.10911 | 0 | 0 | 0.21822 | 347.0233 | 0.10972 | 0 | 0 | 0.21943 | 347.3967 | 0.11053 | 0 | 0 | 0.22105 | 347.6768 | 0.11113 | 0 | 0 | 0.22227 | 347.8635 | 0.11154 | 0 | 0 | 0.22308 | 348.1436 | 0.11215 | 0 | 0 | 0.22429 | 348.3304 | 0.11255 | 0 | 0 | 0.2251 | 348.6104 | 0.11316 | 0 | 0 | 0.22632 | 348.8905 | 0.11377 | 0 | 0 | 0.22753 | 349.0772 | 0.11417 | 0 | 0 | 0.22834 | 349.3573 | 0.11478 | 0 | 0 | 0.22956 | 349.6374 | 0.11539 | 0 | 0 | 0.23077 | 349.7308 | 0.11559 | 0 | 0 | 0.23118 | 350.0109 | 0.1162 | 0 | 0 | 0.23239 | 350.2909 | 0.1168 | 0 | 0 | 0.23361 | 350.4777 | 0.11721 | 0 | 0 | 0.23442 | 350.7577 | 0.11782 | 0 | 0 | 0.23563 | 350.9445 | 0.11822 | 0 | 0 | 0.23644 | 351.1312 | 0.11863 | 0 | 0 | 0.23725
2017-12-16 21:00 | 314.3363 | 0.93691 |  | 330.0735 | 0.072951 | 0 | 0 | 0.1459 | 339.3489 | 0.093069 | 0 | 0 | 0.18614 | 346.9378 | 0.10953 | 0 | 0 | 0.21906 | 347.2189 | 0.11014 | 0 | 0 | 0.22028 | 347.4063 | 0.11055 | 0 | 0 | 0.22109 | 347.6874 | 0.11116 | 0 | 0 | 0.22231 | 347.9684 | 0.11177 | 0 | 0 | 0.22353 | 348.2495 | 0.11237 | 0 | 0 | 0.22475 | 348.6243 | 0.11319 | 0 | 0 | 0.22638 | 348.9054 | 0.1138 | 0 | 0 | 0.22759 | 349.0927 | 0.1142 | 0 | 0 | 0.22841 | 349.3738 | 0.11481 | 0 | 0 | 0.22963 | 349.5612 | 0.11522 | 0 | 0 | 0.23044 | 349.8423 | 0.11583 | 0 | 0 | 0.23166 | 350.1233 | 0.11644 | 0 | 0 | 0.23288 | 350.3107 | 0.11685 | 0 | 0 | 0.23369 | 350.5918 | 0.11746 | 0 | 0 | 0.23491 | 350.8729 | 0.11806 | 0 | 0 | 0.23613 | 350.9666 | 0.11827 | 0 | 0 | 0.23654 | 351.2476 | 0.11888 | 0 | 0 | 0.23776 | 351.5287 | 0.11949 | 0 | 0 | 0.23897 | 351.7161 | 0.11989 | 0 | 0 | 0.23979 | 351.9972 | 0.1205 | 0 | 0 | 0.24101 | 352.1845 | 0.12091 | 0 | 0 | 0.24182 | 352.3719 | 0.12132 | 0 | 0 | 0.24263
2017-12-16 22:00 | 320.2957 | 0.95467 |  | 336.3312 | 0.086524 | 0 | 0 | 0.17305 | 345.7825 | 0.10702 | 0 | 0 | 0.21405 | 353.5153 | 0.1238 | 0 | 0 | 0.24759 | 353.8017 | 0.12442 | 0 | 0 | 0.24884 | 353.9927 | 0.12483 | 0 | 0 | 0.24966 | 354.2791 | 0.12545 | 0 | 0 | 0.25091 | 354.5655 | 0.12607 | 0 | 0 | 0.25215 | 354.8519 | 0.1267 | 0 | 0 | 0.25339 | 355.2338 | 0.12752 | 0 | 0 | 0.25505 | 355.5202 | 0.12814 | 0 | 0 | 0.25629 | 355.7111 | 0.12856 | 0 | 0 | 0.25712 | 355.9975 | 0.12918 | 0 | 0 | 0.25836 | 356.1884 | 0.12959 | 0 | 0 | 0.25919 | 356.4748 | 0.13022 | 0 | 0 | 0.26043 | 356.7612 | 0.13084 | 0 | 0 | 0.26167 | 356.9522 | 0.13125 | 0 | 0 | 0.2625 | 357.2386 | 0.13187 | 0 | 0 | 0.26374 | 357.525 | 0.13249 | 0 | 0 | 0.26499 | 357.6204 | 0.1327 | 0 | 0 | 0.2654 | 357.9068 | 0.13332 | 0 | 0 | 0.26664 | 358.1932 | 0.13394 | 0 | 0 | 0.26789 | 358.3842 | 0.13436 | 0 | 0 | 0.26871 | 358.6706 | 0.13498 | 0 | 0 | 0.26996 | 358.8615 | 0.13539 | 0 | 0 | 0.27078 | 359.0524 | 0.13581 | 0 | 0 | 0.27161
2017-12-16 23:00 | 323.9251 | 0.96549 |  | 340.1423 | 0.09479 | 0 | 0 | 0.18958 | 349.7006 | 0.11552 | 0 | 0 | 0.23104 | 357.5211 | 0.13248 | 0 | 0 | 0.26497 | 357.8108 | 0.13311 | 0 | 0 | 0.26623 | 358.0039 | 0.13353 | 0 | 0 | 0.26706 | 358.2935 | 0.13416 | 0 | 0 | 0.26832 | 358.5832 | 0.13479 | 0 | 0 | 0.26958 | 358.8728 | 0.13542 | 0 | 0 | 0.27083 | 359.259 | 0.13625 | 0 | 0 | 0.27251 | 359.5486 | 0.13688 | 0 | 0 | 0.27377 | 359.7417 | 0.1373 | 0 | 0 | 0.2746 | 360.0314 | 0.13793 | 0 | 0 | 0.27586 | 360.2245 | 0.13835 | 0 | 0 | 0.2767 | 360.5141 | 0.13898 | 0 | 0 | 0.27795 | 360.8038 | 0.13961 | 0 | 0 | 0.27921 | 360.9969 | 0.14002 | 0 | 0 | 0.28005 | 361.2865 | 0.14065 | 0 | 0 | 0.2813 | 361.5762 | 0.14128 | 0 | 0 | 0.28256 | 361.6727 | 0.14149 | 0 | 0 | 0.28298 | 361.9624 | 0.14212 | 0 | 0 | 0.28424 | 362.252 | 0.14275 | 0 | 0 | 0.28549 | 362.4451 | 0.14317 | 0 | 0 | 0.28633 | 362.7348 | 0.14379 | 0 | 0 | 0.28759 | 362.9279 | 0.14421 | 0 | 0 | 0.28842 | 363.121 | 0.14463 | 0 | 0 | 0.28926
2017-12-17 | 319.4914 | 0.95228 |  | 335.4867 | 0.084692 | 0 | 0 | 0.16938 | 344.9142 | 0.10514 | 0 | 0 | 0.21028 | 352.6276 | 0.12187 | 0 | 0 | 0.24374 | 352.9133 | 0.12249 | 0 | 0 | 0.24498 | 353.1038 | 0.1229 | 0 | 0 | 0.24581 | 353.3895 | 0.12352 | 0 | 0 | 0.24705 | 353.6751 | 0.12414 | 0 | 0 | 0.24829 | 353.9608 | 0.12476 | 0 | 0 | 0.24953 | 354.3417 | 0.12559 | 0 | 0 | 0.25118 | 354.6274 | 0.12621 | 0 | 0 | 0.25242 | 354.8179 | 0.12662 | 0 | 0 | 0.25324 | 355.1036 | 0.12724 | 0 | 0 | 0.25448 | 355.294 | 0.12765 | 0 | 0 | 0.25531 | 355.5797 | 0.12827 | 0 | 0 | 0.25655 | 355.8654 | 0.12889 | 0 | 0 | 0.25779 | 356.0558 | 0.12931 | 0 | 0 | 0.25861 | 356.3415 | 0.12993 | 0 | 0 | 0.25985 | 356.6272 | 0.13055 | 0 | 0 | 0.26109 | 356.7224 | 0.13075 | 0 | 0 | 0.26151 | 357.0081 | 0.13137 | 0 | 0 | 0.26274 | 357.2938 | 0.13199 | 0 | 0 | 0.26398 | 357.4842 | 0.1324 | 0 | 0 | 0.26481 | 357.7699 | 0.13302 | 0 | 0 | 0.26605 | 357.9604 | 0.13344 | 0 | 0 | 0.26688 | 358.1508 | 0.13385 | 0 | 0 | 0.2677
2017-12-17 01:00 | 318.2097 | 0.94846 |  | 334.1408 | 0.081773 | 0 | 0 | 0.16355 | 343.5305 | 0.10214 | 0 | 0 | 0.20428 | 351.213 | 0.1188 | 0 | 0 | 0.23761 | 351.4975 | 0.11942 | 0 | 0 | 0.23884 | 351.6872 | 0.11983 | 0 | 0 | 0.23966 | 351.9717 | 0.12045 | 0 | 0 | 0.2409 | 352.2563 | 0.12107 | 0 | 0 | 0.24213 | 352.5408 | 0.12168 | 0 | 0 | 0.24337 | 352.9202 | 0.12251 | 0 | 0 | 0.24501 | 353.2047 | 0.12312 | 0 | 0 | 0.24625 | 353.3944 | 0.12353 | 0 | 0 | 0.24707 | 353.6789 | 0.12415 | 0 | 0 | 0.2483 | 353.8686 | 0.12456 | 0 | 0 | 0.24913 | 354.1532 | 0.12518 | 0 | 0 | 0.25036 | 354.4377 | 0.1258 | 0 | 0 | 0.25159 | 354.6274 | 0.12621 | 0 | 0 | 0.25242 | 354.9119 | 0.12683 | 0 | 0 | 0.25365 | 355.1965 | 0.12744 | 0 | 0 | 0.25489 | 355.2913 | 0.12765 | 0 | 0 | 0.2553 | 355.5759 | 0.12827 | 0 | 0 | 0.25653 | 355.8604 | 0.12888 | 0 | 0 | 0.25777 | 356.0501 | 0.12929 | 0 | 0 | 0.25859 | 356.3346 | 0.12991 | 0 | 0 | 0.25982 | 356.5243 | 0.13032 | 0 | 0 | 0.26065 | 356.714 | 0.13073 | 0 | 0 | 0.26147
2017-12-17 02:00 | 310.1122 | 0.92432 |  | 325.6379 | 0.06333 | 0 | 0 | 0.12666 | 334.7886 | 0.083178 | 0 | 0 | 0.16636 | 342.2756 | 0.099417 | 0 | 0 | 0.19883 | 342.5529 | 0.10002 | 0 | 0 | 0.20004 | 342.7378 | 0.10042 | 0 | 0 | 0.20084 | 343.0151 | 0.10102 | 0 | 0 | 0.20204 | 343.2924 | 0.10162 | 0 | 0 | 0.20325 | 343.5697 | 0.10222 | 0 | 0 | 0.20445 | 343.9394 | 0.10303 | 0 | 0 | 0.20605 | 344.2167 | 0.10363 | 0 | 0 | 0.20726 | 344.4016 | 0.10403 | 0 | 0 | 0.20806 | 344.6789 | 0.10463 | 0 | 0 | 0.20926 | 344.8637 | 0.10503 | 0 | 0 | 0.21006 | 345.141 | 0.10563 | 0 | 0 | 0.21126 | 345.4183 | 0.10623 | 0 | 0 | 0.21247 | 345.6032 | 0.10663 | 0 | 0 | 0.21327 | 345.8805 | 0.10724 | 0 | 0 | 0.21447 | 346.1578 | 0.10784 | 0 | 0 | 0.21568 | 346.2502 | 0.10804 | 0 | 0 | 0.21608 | 346.5275 | 0.10864 | 0 | 0 | 0.21728 | 346.8048 | 0.10924 | 0 | 0 | 0.21848 | 346.9897 | 0.10964 | 0 | 0 | 0.21928 | 347.2669 | 0.11024 | 0 | 0 | 0.22049 | 347.4518 | 0.11064 | 0 | 0 | 0.22129 | 347.6367 | 0.11105 | 0 | 0 | 0.22209
2017-12-17 03:00 | 304.5446 | 0.90772 |  | 319.7915 | 0.050649 | 0 | 0 | 0.1013 | 328.778 | 0.070141 | 0 | 0 | 0.14028 | 336.1306 | 0.086089 | 0 | 0 | 0.17218 | 336.4029 | 0.086679 | 0 | 0 | 0.17336 | 336.5844 | 0.087073 | 0 | 0 | 0.17415 | 336.8567 | 0.087664 | 0 | 0 | 0.17533 | 337.1291 | 0.088255 | 0 | 0 | 0.17651 | 337.4014 | 0.088845 | 0 | 0 | 0.17769 | 337.7645 | 0.089633 | 0 | 0 | 0.17927 | 338.0368 | 0.090223 | 0 | 0 | 0.18045 | 338.2183 | 0.090617 | 0 | 0 | 0.18123 | 338.4906 | 0.091208 | 0 | 0 | 0.18242 | 338.6722 | 0.091602 | 0 | 0 | 0.1832 | 338.9445 | 0.092192 | 0 | 0 | 0.18438 | 339.2168 | 0.092783 | 0 | 0 | 0.18557 | 339.3984 | 0.093177 | 0 | 0 | 0.18635 | 339.6707 | 0.093767 | 0 | 0 | 0.18753 | 339.943 | 0.094358 | 0 | 0 | 0.18872 | 340.0338 | 0.094555 | 0 | 0 | 0.18911 | 340.3061 | 0.095146 | 0 | 0 | 0.19029 | 340.5784 | 0.095736 | 0 | 0 | 0.19147 | 340.76 | 0.09613 | 0 | 0 | 0.19226 | 341.0323 | 0.096721 | 0 | 0 | 0.19344 | 341.2138 | 0.097114 | 0 | 0 | 0.19423 | 341.3954 | 0.097508 | 0 | 0 | 0.19502
2017-12-17 04:00 | 306.9627 | 0.91493 |  | 322.3307 | 0.056157 | 0 | 0 | 0.11231 | 331.3886 | 0.075803 | 0 | 0 | 0.15161 | 338.7995 | 0.091878 | 0 | 0 | 0.18376 | 339.074 | 0.092473 | 0 | 0 | 0.18495 | 339.257 | 0.09287 | 0 | 0 | 0.18574 | 339.5315 | 0.093465 | 0 | 0 | 0.18693 | 339.806 | 0.094061 | 0 | 0 | 0.18812 | 340.0804 | 0.094656 | 0 | 0 | 0.18931 | 340.4464 | 0.09545 | 0 | 0 | 0.1909 | 340.7209 | 0.096045 | 0 | 0 | 0.19209 | 340.9039 | 0.096442 | 0 | 0 | 0.19288 | 341.1784 | 0.097037 | 0 | 0 | 0.19407 | 341.3613 | 0.097434 | 0 | 0 | 0.19487 | 341.6358 | 0.09803 | 0 | 0 | 0.19606 | 341.9103 | 0.098625 | 0 | 0 | 0.19725 | 342.0933 | 0.099022 | 0 | 0 | 0.19804 | 342.3678 | 0.099617 | 0 | 0 | 0.19923 | 342.6422 | 0.10021 | 0 | 0 | 0.20043 | 342.7337 | 0.10041 | 0 | 0 | 0.20082 | 343.0082 | 0.10101 | 0 | 0 | 0.20201 | 343.2827 | 0.1016 | 0 | 0 | 0.2032 | 343.4657 | 0.102 | 0 | 0 | 0.204 | 343.7402 | 0.10259 | 0 | 0 | 0.20519 | 343.9232 | 0.10299 | 0 | 0 | 0.20598 | 344.1061 | 0.10339 | 0 | 0 | 0.20678
2017-12-17 05:00 | 302.7479 | 0.90237 |  | 317.9049 | 0.046557 | 0 | 0 | 0.093115 | 326.8384 | 0.065934 | 0 | 0 | 0.13187 | 334.1476 | 0.081788 | 0 | 0 | 0.16358 | 334.4183 | 0.082375 | 0 | 0 | 0.16475 | 334.5988 | 0.082766 | 0 | 0 | 0.16553 | 334.8695 | 0.083354 | 0 | 0 | 0.16671 | 335.1402 | 0.083941 | 0 | 0 | 0.16788 | 335.4109 | 0.084528 | 0 | 0 | 0.16906 | 335.7719 | 0.085311 | 0 | 0 | 0.17062 | 336.0426 | 0.085898 | 0 | 0 | 0.1718 | 336.2231 | 0.086289 | 0 | 0 | 0.17258 | 336.4938 | 0.086877 | 0 | 0 | 0.17375 | 336.6742 | 0.087268 | 0 | 0 | 0.17454 | 336.9449 | 0.087855 | 0 | 0 | 0.17571 | 337.2157 | 0.088442 | 0 | 0 | 0.17688 | 337.3961 | 0.088834 | 0 | 0 | 0.17767 | 337.6668 | 0.089421 | 0 | 0 | 0.17884 | 337.9376 | 0.090008 | 0 | 0 | 0.18002 | 338.0278 | 0.090204 | 0 | 0 | 0.18041 | 338.2985 | 0.090791 | 0 | 0 | 0.18158 | 338.5692 | 0.091378 | 0 | 0 | 0.18276 | 338.7497 | 0.09177 | 0 | 0 | 0.18354 | 339.0204 | 0.092357 | 0 | 0 | 0.18471 | 339.2009 | 0.092748 | 0 | 0 | 0.1855 | 339.3813 | 0.09314 | 0 | 0 | 0.18628
2017-12-17 06:00 | 310.6128 | 0.92581 |  | 326.1635 | 0.06447 | 0 | 0 | 0.12894 | 335.3291 | 0.08435 | 0 | 0 | 0.1687 | 342.8281 | 0.10062 | 0 | 0 | 0.20123 | 343.1059 | 0.10122 | 0 | 0 | 0.20244 | 343.291 | 0.10162 | 0 | 0 | 0.20324 | 343.5688 | 0.10222 | 0 | 0 | 0.20444 | 343.8465 | 0.10282 | 0 | 0 | 0.20565 | 344.1243 | 0.10343 | 0 | 0 | 0.20685 | 344.4946 | 0.10423 | 0 | 0 | 0.20846 | 344.7723 | 0.10483 | 0 | 0 | 0.20967 | 344.9575 | 0.10523 | 0 | 0 | 0.21047 | 345.2352 | 0.10584 | 0 | 0 | 0.21167 | 345.4204 | 0.10624 | 0 | 0 | 0.21248 | 345.6981 | 0.10684 | 0 | 0 | 0.21368 | 345.9759 | 0.10744 | 0 | 0 | 0.21489 | 346.161 | 0.10784 | 0 | 0 | 0.21569 | 346.4388 | 0.10845 | 0 | 0 | 0.21689 | 346.7165 | 0.10905 | 0 | 0 | 0.2181 | 346.8091 | 0.10925 | 0 | 0 | 0.2185 | 347.0869 | 0.10985 | 0 | 0 | 0.21971 | 347.3646 | 0.11046 | 0 | 0 | 0.22091 | 347.5498 | 0.11086 | 0 | 0 | 0.22171 | 347.8275 | 0.11146 | 0 | 0 | 0.22292 | 348.0127 | 0.11186 | 0 | 0 | 0.22372 | 348.1978 | 0.11226 | 0 | 0 | 0.22453
2017-12-17 07:00 | 309.5997 | 0.92279 |  | 325.0997 | 0.062163 | 0 | 0 | 0.12433 | 334.2353 | 0.081978 | 0 | 0 | 0.16396 | 341.7099 | 0.09819 | 0 | 0 | 0.19638 | 341.9868 | 0.098791 | 0 | 0 | 0.19758 | 342.1713 | 0.099191 | 0 | 0 | 0.19838 | 342.4482 | 0.099792 | 0 | 0 | 0.19958 | 342.725 | 0.10039 | 0 | 0 | 0.20078 | 343.0018 | 0.10099 | 0 | 0 | 0.20199 | 343.371 | 0.10179 | 0 | 0 | 0.20359 | 343.6478 | 0.10239 | 0 | 0 | 0.20479 | 343.8324 | 0.10279 | 0 | 0 | 0.20559 | 344.1092 | 0.10339 | 0 | 0 | 0.20679 | 344.2938 | 0.10379 | 0 | 0 | 0.20759 | 344.5706 | 0.1044 | 0 | 0 | 0.20879 | 344.8474 | 0.105 | 0 | 0 | 0.20999 | 345.032 | 0.1054 | 0 | 0 | 0.21079 | 345.3088 | 0.106 | 0 | 0 | 0.21199 | 345.5857 | 0.1066 | 0 | 0 | 0.21319 | 345.6779 | 0.1068 | 0 | 0 | 0.21359 | 345.9548 | 0.1074 | 0 | 0 | 0.2148 | 346.2316 | 0.108 | 0 | 0 | 0.216 | 346.4162 | 0.1084 | 0 | 0 | 0.2168 | 346.693 | 0.109 | 0 | 0 | 0.218 | 346.8776 | 0.1094 | 0 | 0 | 0.2188 | 347.0621 | 0.1098 | 0 | 0 | 0.2196
2017-12-17 08:00 | 308.3545 | 0.91908 |  | 323.7922 | 0.059327 | 0 | 0 | 0.11865 | 332.8911 | 0.079062 | 0 | 0 | 0.15812 | 340.3356 | 0.09521 | 0 | 0 | 0.19042 | 340.6114 | 0.095808 | 0 | 0 | 0.19162 | 340.7952 | 0.096206 | 0 | 0 | 0.19241 | 341.0709 | 0.096804 | 0 | 0 | 0.19361 | 341.3466 | 0.097402 | 0 | 0 | 0.1948 | 341.6223 | 0.098001 | 0 | 0 | 0.196 | 341.99 | 0.098798 | 0 | 0 | 0.1976 | 342.2657 | 0.099396 | 0 | 0 | 0.19879 | 342.4495 | 0.099795 | 0 | 0 | 0.19959 | 342.7252 | 0.10039 | 0 | 0 | 0.20079 | 342.9091 | 0.10079 | 0 | 0 | 0.20158 | 343.1848 | 0.10139 | 0 | 0 | 0.20278 | 343.4605 | 0.10199 | 0 | 0 | 0.20397 | 343.6443 | 0.10239 | 0 | 0 | 0.20477 | 343.92 | 0.10298 | 0 | 0 | 0.20597 | 344.1958 | 0.10358 | 0 | 0 | 0.20716 | 344.2877 | 0.10378 | 0 | 0 | 0.20756 | 344.5634 | 0.10438 | 0 | 0 | 0.20876 | 344.8391 | 0.10498 | 0 | 0 | 0.20996 | 345.0229 | 0.10538 | 0 | 0 | 0.21075 | 345.2987 | 0.10597 | 0 | 0 | 0.21195 | 345.4825 | 0.10637 | 0 | 0 | 0.21275 | 345.6663 | 0.10677 | 0 | 0 | 0.21354
2017-12-17 09:00 | 307.4711 | 0.91645 |  | 322.8646 | 0.057315 | 0 | 0 | 0.11463 | 331.9374 | 0.076994 | 0 | 0 | 0.15399 | 339.3606 | 0.093095 | 0 | 0 | 0.18619 | 339.6356 | 0.093691 | 0 | 0 | 0.18738 | 339.8189 | 0.094089 | 0 | 0 | 0.18818 | 340.0938 | 0.094685 | 0 | 0 | 0.18937 | 340.3687 | 0.095281 | 0 | 0 | 0.19056 | 340.6437 | 0.095878 | 0 | 0 | 0.19176 | 341.0103 | 0.096673 | 0 | 0 | 0.19335 | 341.2852 | 0.097269 | 0 | 0 | 0.19454 | 341.4685 | 0.097667 | 0 | 0 | 0.19533 | 341.7434 | 0.098263 | 0 | 0 | 0.19653 | 341.9267 | 0.098661 | 0 | 0 | 0.19732 | 342.2016 | 0.099257 | 0 | 0 | 0.19851 | 342.4766 | 0.099853 | 0 | 0 | 0.19971 | 342.6599 | 0.10025 | 0 | 0 | 0.2005 | 342.9348 | 0.10085 | 0 | 0 | 0.20169 | 343.2097 | 0.10144 | 0 | 0 | 0.20289 | 343.3014 | 0.10164 | 0 | 0 | 0.20328 | 343.5763 | 0.10224 | 0 | 0 | 0.20448 | 343.8512 | 0.10283 | 0 | 0 | 0.20567 | 344.0345 | 0.10323 | 0 | 0 | 0.20647 | 344.3095 | 0.10383 | 0 | 0 | 0.20766 | 344.4928 | 0.10423 | 0 | 0 | 0.20845 | 344.676 | 0.10462 | 0 | 0 | 0.20925
2017-12-17 10:00 | 303.2986 | 0.90401 |  | 318.4832 | 0.047812 | 0 | 0 | 0.095623 | 327.4329 | 0.067224 | 0 | 0 | 0.13445 | 334.7554 | 0.083106 | 0 | 0 | 0.16621 | 335.0266 | 0.083694 | 0 | 0 | 0.16739 | 335.2074 | 0.084086 | 0 | 0 | 0.16817 | 335.4786 | 0.084675 | 0 | 0 | 0.16935 | 335.7498 | 0.085263 | 0 | 0 | 0.17053 | 336.021 | 0.085851 | 0 | 0 | 0.1717 | 336.3826 | 0.086635 | 0 | 0 | 0.17327 | 336.6538 | 0.087224 | 0 | 0 | 0.17445 | 336.8346 | 0.087616 | 0 | 0 | 0.17523 | 337.1058 | 0.088204 | 0 | 0 | 0.17641 | 337.2866 | 0.088596 | 0 | 0 | 0.17719 | 337.5578 | 0.089185 | 0 | 0 | 0.17837 | 337.829 | 0.089773 | 0 | 0 | 0.17955 | 338.0098 | 0.090165 | 0 | 0 | 0.18033 | 338.281 | 0.090753 | 0 | 0 | 0.18151 | 338.5522 | 0.091341 | 0 | 0 | 0.18268 | 338.6426 | 0.091537 | 0 | 0 | 0.18307 | 338.9138 | 0.092126 | 0 | 0 | 0.18425 | 339.185 | 0.092714 | 0 | 0 | 0.18543 | 339.3658 | 0.093106 | 0 | 0 | 0.18621 | 339.637 | 0.093694 | 0 | 0 | 0.18739 | 339.8178 | 0.094087 | 0 | 0 | 0.18817 | 339.9986 | 0.094479 | 0 | 0 | 0.18896
2017-12-17 11:00 | 294.4688 | 0.87769 |  | 309.2113 | 0.027701 | 0 | 0 | 0.055402 | 317.9005 | 0.046548 | 0 | 0 | 0.093095 | 325.0098 | 0.061968 | 0 | 0 | 0.12394 | 325.2731 | 0.062539 | 0 | 0 | 0.12508 | 325.4486 | 0.06292 | 0 | 0 | 0.12584 | 325.7119 | 0.063491 | 0 | 0 | 0.12698 | 325.9752 | 0.064062 | 0 | 0 | 0.12812 | 326.2385 | 0.064633 | 0 | 0 | 0.12927 | 326.5896 | 0.065395 | 0 | 0 | 0.13079 | 326.8529 | 0.065966 | 0 | 0 | 0.13193 | 327.0285 | 0.066346 | 0 | 0 | 0.13269 | 327.2918 | 0.066917 | 0 | 0 | 0.13383 | 327.4673 | 0.067298 | 0 | 0 | 0.1346 | 327.7306 | 0.067869 | 0 | 0 | 0.13574 | 327.9939 | 0.06844 | 0 | 0 | 0.13688 | 328.1695 | 0.068821 | 0 | 0 | 0.13764 | 328.4328 | 0.069392 | 0 | 0 | 0.13878 | 328.6961 | 0.069963 | 0 | 0 | 0.13993 | 328.7839 | 0.070154 | 0 | 0 | 0.14031 | 329.0472 | 0.070725 | 0 | 0 | 0.14145 | 329.3105 | 0.071296 | 0 | 0 | 0.14259 | 329.486 | 0.071677 | 0 | 0 | 0.14335 | 329.7493 | 0.072248 | 0 | 0 | 0.1445 | 329.9249 | 0.072629 | 0 | 0 | 0.14526 | 330.1004 | 0.073009 | 0 | 0 | 0.14602
2017-12-17 12:00 | 300.2708 | 0.89499 |  | 315.3037 | 0.040915 | 0 | 0 | 0.081831 | 324.1641 | 0.060134 | 0 | 0 | 0.12027 | 331.4135 | 0.075857 | 0 | 0 | 0.15171 | 331.682 | 0.07644 | 0 | 0 | 0.15288 | 331.861 | 0.076828 | 0 | 0 | 0.15366 | 332.1295 | 0.07741 | 0 | 0 | 0.15482 | 332.398 | 0.077993 | 0 | 0 | 0.15599 | 332.6665 | 0.078575 | 0 | 0 | 0.15715 | 333.0245 | 0.079352 | 0 | 0 | 0.1587 | 333.293 | 0.079934 | 0 | 0 | 0.15987 | 333.472 | 0.080322 | 0 | 0 | 0.16064 | 333.7405 | 0.080905 | 0 | 0 | 0.16181 | 333.9195 | 0.081293 | 0 | 0 | 0.16259 | 334.1879 | 0.081875 | 0 | 0 | 0.16375 | 334.4564 | 0.082458 | 0 | 0 | 0.16492 | 334.6354 | 0.082846 | 0 | 0 | 0.16569 | 334.9039 | 0.083428 | 0 | 0 | 0.16686 | 335.1724 | 0.084011 | 0 | 0 | 0.16802 | 335.2619 | 0.084205 | 0 | 0 | 0.16841 | 335.5304 | 0.084787 | 0 | 0 | 0.16957 | 335.7989 | 0.08537 | 0 | 0 | 0.17074 | 335.9779 | 0.085758 | 0 | 0 | 0.17152 | 336.2464 | 0.08634 | 0 | 0 | 0.17268 | 336.4254 | 0.086728 | 0 | 0 | 0.17346 | 336.6044 | 0.087117 | 0 | 0 | 0.17423
2017-12-17 13:00 | 304.1402 | 0.90652 |  | 319.3669 | 0.049728 | 0 | 0 | 0.099457 | 328.3415 | 0.069194 | 0 | 0 | 0.13839 | 335.6843 | 0.085121 | 0 | 0 | 0.17024 | 335.9562 | 0.085711 | 0 | 0 | 0.17142 | 336.1375 | 0.086104 | 0 | 0 | 0.17221 | 336.4095 | 0.086694 | 0 | 0 | 0.17339 | 336.6814 | 0.087284 | 0 | 0 | 0.17457 | 336.9534 | 0.087874 | 0 | 0 | 0.17575 | 337.316 | 0.08866 | 0 | 0 | 0.17732 | 337.588 | 0.08925 | 0 | 0 | 0.1785 | 337.7693 | 0.089643 | 0 | 0 | 0.17929 | 338.0412 | 0.090233 | 0 | 0 | 0.18047 | 338.2225 | 0.090626 | 0 | 0 | 0.18125 | 338.4945 | 0.091216 | 0 | 0 | 0.18243 | 338.7664 | 0.091806 | 0 | 0 | 0.18361 | 338.9477 | 0.092199 | 0 | 0 | 0.1844 | 339.2197 | 0.092789 | 0 | 0 | 0.18558 | 339.4917 | 0.093379 | 0 | 0 | 0.18676 | 339.5823 | 0.093576 | 0 | 0 | 0.18715 | 339.8543 | 0.094166 | 0 | 0 | 0.18833 | 340.1262 | 0.094755 | 0 | 0 | 0.18951 | 340.3075 | 0.095149 | 0 | 0 | 0.1903 | 340.5795 | 0.095739 | 0 | 0 | 0.19148 | 340.7608 | 0.096132 | 0 | 0 | 0.19226 | 340.9421 | 0.096525 | 0 | 0 | 0.19305
2017-12-17 14:00 | 297.533 | 0.88683 |  | 312.4289 | 0.03468 | 0 | 0 | 0.06936 | 321.2085 | 0.053723 | 0 | 0 | 0.10745 | 328.3917 | 0.069303 | 0 | 0 | 0.13861 | 328.6578 | 0.06988 | 0 | 0 | 0.13976 | 328.8352 | 0.070265 | 0 | 0 | 0.14053 | 329.1012 | 0.070842 | 0 | 0 | 0.14168 | 329.3673 | 0.071419 | 0 | 0 | 0.14284 | 329.6333 | 0.071996 | 0 | 0 | 0.14399 | 329.988 | 0.072766 | 0 | 0 | 0.14553 | 330.2541 | 0.073343 | 0 | 0 | 0.14669 | 330.4314 | 0.073727 | 0 | 0 | 0.14745 | 330.6975 | 0.074305 | 0 | 0 | 0.14861 | 330.8749 | 0.074689 | 0 | 0 | 0.14938 | 331.1409 | 0.075266 | 0 | 0 | 0.15053 | 331.407 | 0.075843 | 0 | 0 | 0.15169 | 331.5843 | 0.076228 | 0 | 0 | 0.15246 | 331.8504 | 0.076805 | 0 | 0 | 0.15361 | 332.1164 | 0.077382 | 0 | 0 | 0.15476 | 332.2051 | 0.077574 | 0 | 0 | 0.15515 | 332.4711 | 0.078152 | 0 | 0 | 0.1563 | 332.7372 | 0.078729 | 0 | 0 | 0.15746 | 332.9146 | 0.079113 | 0 | 0 | 0.15823 | 333.1806 | 0.07969 | 0 | 0 | 0.15938 | 333.358 | 0.080075 | 0 | 0 | 0.16015 | 333.5353 | 0.08046 | 0 | 0 | 0.16092
2017-12-17 15:00 | 298.9823 | 0.89115 |  | 313.9508 | 0.037981 | 0 | 0 | 0.075962 | 322.7731 | 0.057116 | 0 | 0 | 0.11423 | 329.9914 | 0.072773 | 0 | 0 | 0.14555 | 330.2587 | 0.073353 | 0 | 0 | 0.14671 | 330.437 | 0.073739 | 0 | 0 | 0.14748 | 330.7043 | 0.074319 | 0 | 0 | 0.14864 | 330.9716 | 0.074899 | 0 | 0 | 0.1498 | 331.239 | 0.075479 | 0 | 0 | 0.15096 | 331.5954 | 0.076252 | 0 | 0 | 0.1525 | 331.8628 | 0.076832 | 0 | 0 | 0.15366 | 332.041 | 0.077219 | 0 | 0 | 0.15444 | 332.3084 | 0.077798 | 0 | 0 | 0.1556 | 332.4866 | 0.078185 | 0 | 0 | 0.15637 | 332.7539 | 0.078765 | 0 | 0 | 0.15753 | 333.0213 | 0.079345 | 0 | 0 | 0.15869 | 333.1995 | 0.079731 | 0 | 0 | 0.15946 | 333.4668 | 0.080311 | 0 | 0 | 0.16062 | 333.7342 | 0.080891 | 0 | 0 | 0.16178 | 333.8233 | 0.081084 | 0 | 0 | 0.16217 | 334.0907 | 0.081664 | 0 | 0 | 0.16333 | 334.358 | 0.082244 | 0 | 0 | 0.16449 | 334.5362 | 0.082631 | 0 | 0 | 0.16526 | 334.8036 | 0.083211 | 0 | 0 | 0.16642 | 334.9818 | 0.083597 | 0 | 0 | 0.16719 | 335.16 | 0.083984 | 0 | 0 | 0.16797
2017-12-17 16:00 | 306.638 | 0.91396 |  | 321.9897 | 0.055417 | 0 | 0 | 0.11083 | 331.038 | 0.075043 | 0 | 0 | 0.15009 | 338.4411 | 0.0911 | 0 | 0 | 0.1822 | 338.7153 | 0.091695 | 0 | 0 | 0.18339 | 338.8981 | 0.092092 | 0 | 0 | 0.18418 | 339.1723 | 0.092686 | 0 | 0 | 0.18537 | 339.4465 | 0.093281 | 0 | 0 | 0.18656 | 339.7207 | 0.093876 | 0 | 0 | 0.18775 | 340.0862 | 0.094669 | 0 | 0 | 0.18934 | 340.3604 | 0.095263 | 0 | 0 | 0.19053 | 340.5432 | 0.09566 | 0 | 0 | 0.19132 | 340.8174 | 0.096255 | 0 | 0 | 0.19251 | 341.0002 | 0.096651 | 0 | 0 | 0.1933 | 341.2744 | 0.097246 | 0 | 0 | 0.19449 | 341.5486 | 0.097841 | 0 | 0 | 0.19568 | 341.7314 | 0.098237 | 0 | 0 | 0.19647 | 342.0056 | 0.098832 | 0 | 0 | 0.19766 | 342.2798 | 0.099426 | 0 | 0 | 0.19885 | 342.3712 | 0.099625 | 0 | 0 | 0.19925 | 342.6453 | 0.10022 | 0 | 0 | 0.20044 | 342.9195 | 0.10081 | 0 | 0 | 0.20163 | 343.1023 | 0.10121 | 0 | 0 | 0.20242 | 343.3765 | 0.10181 | 0 | 0 | 0.20361 | 343.5593 | 0.1022 | 0 | 0 | 0.2044 | 343.7421 | 0.1026 | 0 | 0 | 0.2052
2017-12-17 17:00 | 309.6491 | 0.92294 |  | 325.1516 | 0.062275 | 0 | 0 | 0.12455 | 334.2887 | 0.082094 | 0 | 0 | 0.16419 | 341.7645 | 0.098309 | 0 | 0 | 0.19662 | 342.0414 | 0.098909 | 0 | 0 | 0.19782 | 342.226 | 0.09931 | 0 | 0 | 0.19862 | 342.5029 | 0.09991 | 0 | 0 | 0.19982 | 342.7797 | 0.10051 | 0 | 0 | 0.20102 | 343.0566 | 0.10111 | 0 | 0 | 0.20222 | 343.4258 | 0.10191 | 0 | 0 | 0.20382 | 343.7027 | 0.10251 | 0 | 0 | 0.20503 | 343.8873 | 0.10291 | 0 | 0 | 0.20583 | 344.1642 | 0.10351 | 0 | 0 | 0.20703 | 344.3487 | 0.10391 | 0 | 0 | 0.20783 | 344.6256 | 0.10451 | 0 | 0 | 0.20903 | 344.9025 | 0.10512 | 0 | 0 | 0.21023 | 345.0871 | 0.10552 | 0 | 0 | 0.21103 | 345.364 | 0.10612 | 0 | 0 | 0.21223 | 345.6409 | 0.10672 | 0 | 0 | 0.21343 | 345.7332 | 0.10692 | 0 | 0 | 0.21383 | 346.01 | 0.10752 | 0 | 0 | 0.21503 | 346.2869 | 0.10812 | 0 | 0 | 0.21624 | 346.4715 | 0.10852 | 0 | 0 | 0.21704 | 346.7484 | 0.10912 | 0 | 0 | 0.21824 | 346.933 | 0.10952 | 0 | 0 | 0.21904 | 347.1176 | 0.10992 | 0 | 0 | 0.21984
2017-12-17 18:00 | 311.0288 | 0.92705 |  | 326.6003 | 0.065418 | 0 | 0 | 0.13084 | 335.7781 | 0.085324 | 0 | 0 | 0.17065 | 343.2873 | 0.10161 | 0 | 0 | 0.20322 | 343.5654 | 0.10221 | 0 | 0 | 0.20443 | 343.7508 | 0.10262 | 0 | 0 | 0.20523 | 344.0289 | 0.10322 | 0 | 0 | 0.20644 | 344.307 | 0.10382 | 0 | 0 | 0.20765 | 344.5851 | 0.10443 | 0 | 0 | 0.20885 | 344.956 | 0.10523 | 0 | 0 | 0.21046 | 345.2341 | 0.10583 | 0 | 0 | 0.21167 | 345.4195 | 0.10624 | 0 | 0 | 0.21247 | 345.6976 | 0.10684 | 0 | 0 | 0.21368 | 345.883 | 0.10724 | 0 | 0 | 0.21448 | 346.1611 | 0.10785 | 0 | 0 | 0.21569 | 346.4392 | 0.10845 | 0 | 0 | 0.2169 | 346.6247 | 0.10885 | 0 | 0 | 0.2177 | 346.9028 | 0.10945 | 0 | 0 | 0.21891 | 347.1809 | 0.11006 | 0 | 0 | 0.22011 | 347.2736 | 0.11026 | 0 | 0 | 0.22052 | 347.5517 | 0.11086 | 0 | 0 | 0.22172 | 347.8298 | 0.11146 | 0 | 0 | 0.22293 | 348.0152 | 0.11187 | 0 | 0 | 0.22373 | 348.2933 | 0.11247 | 0 | 0 | 0.22494 | 348.4788 | 0.11287 | 0 | 0 | 0.22574 | 348.6642 | 0.11327 | 0 | 0 | 0.22655
2017-12-17 19:00 | 304.1194 | 0.90646 |  | 319.3451 | 0.049681 | 0 | 0 | 0.099362 | 328.319 | 0.069146 | 0 | 0 | 0.13829 | 335.6613 | 0.085071 | 0 | 0 | 0.17014 | 335.9333 | 0.085661 | 0 | 0 | 0.17132 | 336.1146 | 0.086054 | 0 | 0 | 0.17211 | 336.3865 | 0.086644 | 0 | 0 | 0.17329 | 336.6584 | 0.087234 | 0 | 0 | 0.17447 | 336.9304 | 0.087824 | 0 | 0 | 0.17565 | 337.293 | 0.08861 | 0 | 0 | 0.17722 | 337.5649 | 0.0892 | 0 | 0 | 0.1784 | 337.7462 | 0.089593 | 0 | 0 | 0.17919 | 338.0181 | 0.090183 | 0 | 0 | 0.18037 | 338.1994 | 0.090576 | 0 | 0 | 0.18115 | 338.4714 | 0.091166 | 0 | 0 | 0.18233 | 338.7433 | 0.091756 | 0 | 0 | 0.18351 | 338.9246 | 0.092149 | 0 | 0 | 0.1843 | 339.1965 | 0.092739 | 0 | 0 | 0.18548 | 339.4685 | 0.093329 | 0 | 0 | 0.18666 | 339.5591 | 0.093525 | 0 | 0 | 0.18705 | 339.831 | 0.094115 | 0 | 0 | 0.18823 | 340.103 | 0.094705 | 0 | 0 | 0.18941 | 340.2843 | 0.095098 | 0 | 0 | 0.1902 | 340.5562 | 0.095688 | 0 | 0 | 0.19138 | 340.7375 | 0.096081 | 0 | 0 | 0.19216 | 340.9188 | 0.096475 | 0 | 0 | 0.19295
2017-12-17 20:00 | 294.1633 | 0.87678 |  | 308.8905 | 0.027005 | 0 | 0 | 0.05401 | 317.5707 | 0.045832 | 0 | 0 | 0.091665 | 324.6726 | 0.061237 | 0 | 0 | 0.12247 | 324.9356 | 0.061807 | 0 | 0 | 0.12361 | 325.111 | 0.062187 | 0 | 0 | 0.12437 | 325.374 | 0.062758 | 0 | 0 | 0.12552 | 325.6371 | 0.063328 | 0 | 0 | 0.12666 | 325.9001 | 0.063899 | 0 | 0 | 0.1278 | 326.2508 | 0.06466 | 0 | 0 | 0.12932 | 326.5139 | 0.06523 | 0 | 0 | 0.13046 | 326.6892 | 0.065611 | 0 | 0 | 0.13122 | 326.9522 | 0.066181 | 0 | 0 | 0.13236 | 327.1276 | 0.066561 | 0 | 0 | 0.13312 | 327.3906 | 0.067132 | 0 | 0 | 0.13426 | 327.6537 | 0.067702 | 0 | 0 | 0.1354 | 327.829 | 0.068083 | 0 | 0 | 0.13617 | 328.0921 | 0.068653 | 0 | 0 | 0.13731 | 328.3551 | 0.069224 | 0 | 0 | 0.13845 | 328.4428 | 0.069414 | 0 | 0 | 0.13883 | 328.7058 | 0.069985 | 0 | 0 | 0.13997 | 328.9688 | 0.070555 | 0 | 0 | 0.14111 | 329.1442 | 0.070935 | 0 | 0 | 0.14187 | 329.4072 | 0.071506 | 0 | 0 | 0.14301 | 329.5826 | 0.071886 | 0 | 0 | 0.14377 | 329.7579 | 0.072267 | 0 | 0 | 0.14453
2017-12-17 21:00 | 306.1548 | 0.91252 |  | 321.4823 | 0.054317 | 0 | 0 | 0.10863 | 330.5163 | 0.073912 | 0 | 0 | 0.14782 | 337.9078 | 0.089944 | 0 | 0 | 0.17989 | 338.1815 | 0.090537 | 0 | 0 | 0.18107 | 338.364 | 0.090933 | 0 | 0 | 0.18187 | 338.6378 | 0.091527 | 0 | 0 | 0.18305 | 338.9115 | 0.092121 | 0 | 0 | 0.18424 | 339.1853 | 0.092715 | 0 | 0 | 0.18543 | 339.5503 | 0.093506 | 0 | 0 | 0.18701 | 339.8241 | 0.0941 | 0 | 0 | 0.1882 | 340.0066 | 0.094496 | 0 | 0 | 0.18899 | 340.2803 | 0.09509 | 0 | 0 | 0.19018 | 340.4628 | 0.095486 | 0 | 0 | 0.19097 | 340.7366 | 0.096079 | 0 | 0 | 0.19216 | 341.0103 | 0.096673 | 0 | 0 | 0.19335 | 341.1929 | 0.097069 | 0 | 0 | 0.19414 | 341.4666 | 0.097663 | 0 | 0 | 0.19533 | 341.7404 | 0.098256 | 0 | 0 | 0.19651 | 341.8316 | 0.098454 | 0 | 0 | 0.19691 | 342.1054 | 0.099048 | 0 | 0 | 0.1981 | 342.3791 | 0.099642 | 0 | 0 | 0.19928 | 342.5616 | 0.10004 | 0 | 0 | 0.20008 | 342.8354 | 0.10063 | 0 | 0 | 0.20126 | 343.0179 | 0.10103 | 0 | 0 | 0.20205 | 343.2004 | 0.10142 | 0 | 0 | 0.20285
2017-12-17 22:00 | 301.947 | 0.89998 |  | 317.0639 | 0.044733 | 0 | 0 | 0.089467 | 325.9738 | 0.064059 | 0 | 0 | 0.12812 | 333.2636 | 0.07987 | 0 | 0 | 0.15974 | 333.5336 | 0.080456 | 0 | 0 | 0.16091 | 333.7136 | 0.080846 | 0 | 0 | 0.16169 | 333.9836 | 0.081432 | 0 | 0 | 0.16286 | 334.2536 | 0.082018 | 0 | 0 | 0.16404 | 334.5236 | 0.082603 | 0 | 0 | 0.16521 | 334.8836 | 0.083384 | 0 | 0 | 0.16677 | 335.1536 | 0.08397 | 0 | 0 | 0.16794 | 335.3336 | 0.08436 | 0 | 0 | 0.16872 | 335.6036 | 0.084946 | 0 | 0 | 0.16989 | 335.7836 | 0.085336 | 0 | 0 | 0.17067 | 336.0536 | 0.085922 | 0 | 0 | 0.17184 | 336.3236 | 0.086507 | 0 | 0 | 0.17301 | 336.5036 | 0.086898 | 0 | 0 | 0.1738 | 336.7736 | 0.087483 | 0 | 0 | 0.17497 | 337.0435 | 0.088069 | 0 | 0 | 0.17614 | 337.1335 | 0.088264 | 0 | 0 | 0.17653 | 337.4035 | 0.08885 | 0 | 0 | 0.1777 | 337.6735 | 0.089436 | 0 | 0 | 0.17887 | 337.8535 | 0.089826 | 0 | 0 | 0.17965 | 338.1235 | 0.090412 | 0 | 0 | 0.18082 | 338.3035 | 0.090802 | 0 | 0 | 0.1816 | 338.4835 | 0.091192 | 0 | 0 | 0.18238
2017-12-17 23:00 | 305.3003 | 0.90998 |  | 320.5851 | 0.052371 | 0 | 0 | 0.10474 | 329.5939 | 0.071911 | 0 | 0 | 0.14382 | 336.9647 | 0.087898 | 0 | 0 | 0.1758 | 337.2377 | 0.08849 | 0 | 0 | 0.17698 | 337.4197 | 0.088885 | 0 | 0 | 0.17777 | 337.6927 | 0.089477 | 0 | 0 | 0.17895 | 337.9657 | 0.090069 | 0 | 0 | 0.18014 | 338.2387 | 0.090661 | 0 | 0 | 0.18132 | 338.6027 | 0.091451 | 0 | 0 | 0.1829 | 338.8756 | 0.092043 | 0 | 0 | 0.18409 | 339.0576 | 0.092438 | 0 | 0 | 0.18488 | 339.3306 | 0.09303 | 0 | 0 | 0.18606 | 339.5126 | 0.093425 | 0 | 0 | 0.18685 | 339.7856 | 0.094017 | 0 | 0 | 0.18803 | 340.0586 | 0.094609 | 0 | 0 | 0.18922 | 340.2406 | 0.095004 | 0 | 0 | 0.19001 | 340.5136 | 0.095596 | 0 | 0 | 0.19119 | 340.7866 | 0.096188 | 0 | 0 | 0.19238 | 340.8776 | 0.096385 | 0 | 0 | 0.19277 | 341.1506 | 0.096977 | 0 | 0 | 0.19395 | 341.4236 | 0.097569 | 0 | 0 | 0.19514 | 341.6056 | 0.097964 | 0 | 0 | 0.19593 | 341.8786 | 0.098556 | 0 | 0 | 0.19711 | 342.0606 | 0.098951 | 0 | 0 | 0.1979 | 342.2426 | 0.099346 | 0 | 0 | 0.19869
2017-12-18 | 302.1239 | 0.90051 |  | 317.2496 | 0.045136 | 0 | 0 | 0.090272 | 326.1647 | 0.064473 | 0 | 0 | 0.12895 | 333.4588 | 0.080294 | 0 | 0 | 0.16059 | 333.729 | 0.08088 | 0 | 0 | 0.16176 | 333.9091 | 0.08127 | 0 | 0 | 0.16254 | 334.1792 | 0.081856 | 0 | 0 | 0.16371 | 334.4494 | 0.082442 | 0 | 0 | 0.16488 | 334.7195 | 0.083028 | 0 | 0 | 0.16606 | 335.0797 | 0.08381 | 0 | 0 | 0.16762 | 335.3499 | 0.084396 | 0 | 0 | 0.16879 | 335.53 | 0.084786 | 0 | 0 | 0.16957 | 335.8001 | 0.085372 | 0 | 0 | 0.17074 | 335.9802 | 0.085763 | 0 | 0 | 0.17153 | 336.2504 | 0.086349 | 0 | 0 | 0.1727 | 336.5206 | 0.086935 | 0 | 0 | 0.17387 | 336.7007 | 0.087325 | 0 | 0 | 0.17465 | 336.9708 | 0.087911 | 0 | 0 | 0.17582 | 337.241 | 0.088497 | 0 | 0 | 0.17699 | 337.331 | 0.088693 | 0 | 0 | 0.17739 | 337.6012 | 0.089279 | 0 | 0 | 0.17856 | 337.8713 | 0.089865 | 0 | 0 | 0.17973 | 338.0514 | 0.090255 | 0 | 0 | 0.18051 | 338.3216 | 0.090841 | 0 | 0 | 0.18168 | 338.5017 | 0.091232 | 0 | 0 | 0.18246 | 338.6818 | 0.091622 | 0 | 0 | 0.18324
2017-12-18 01:00 | 307.1065 | 0.91536 |  | 322.4817 | 0.056484 | 0 | 0 | 0.11297 | 331.5438 | 0.07614 | 0 | 0 | 0.15228 | 338.9582 | 0.092222 | 0 | 0 | 0.18444 | 339.2328 | 0.092818 | 0 | 0 | 0.18564 | 339.4159 | 0.093215 | 0 | 0 | 0.18643 | 339.6905 | 0.09381 | 0 | 0 | 0.18762 | 339.9651 | 0.094406 | 0 | 0 | 0.18881 | 340.2397 | 0.095002 | 0 | 0 | 0.19 | 340.6059 | 0.095796 | 0 | 0 | 0.19159 | 340.8805 | 0.096391 | 0 | 0 | 0.19278 | 341.0635 | 0.096788 | 0 | 0 | 0.19358 | 341.3381 | 0.097384 | 0 | 0 | 0.19477 | 341.5212 | 0.097781 | 0 | 0 | 0.19556 | 341.7958 | 0.098377 | 0 | 0 | 0.19675 | 342.0704 | 0.098972 | 0 | 0 | 0.19794 | 342.2535 | 0.099369 | 0 | 0 | 0.19874 | 342.5281 | 0.099965 | 0 | 0 | 0.19993 | 342.8027 | 0.10056 | 0 | 0 | 0.20112 | 342.8943 | 0.10076 | 0 | 0 | 0.20152 | 343.1689 | 0.10135 | 0 | 0 | 0.20271 | 343.4435 | 0.10195 | 0 | 0 | 0.2039 | 343.6265 | 0.10235 | 0 | 0 | 0.2047 | 343.9012 | 0.10294 | 0 | 0 | 0.20589 | 344.0842 | 0.10334 | 0 | 0 | 0.20668 | 344.2673 | 0.10374 | 0 | 0 | 0.20747
2017-12-18 02:00 | 307.2542 | 0.9158 |  | 322.6367 | 0.056821 | 0 | 0 | 0.11364 | 331.7032 | 0.076486 | 0 | 0 | 0.15297 | 339.1212 | 0.092575 | 0 | 0 | 0.18515 | 339.3959 | 0.093171 | 0 | 0 | 0.18634 | 339.5791 | 0.093569 | 0 | 0 | 0.18714 | 339.8538 | 0.094165 | 0 | 0 | 0.18833 | 340.1285 | 0.09476 | 0 | 0 | 0.18952 | 340.4033 | 0.095356 | 0 | 0 | 0.19071 | 340.7696 | 0.096151 | 0 | 0 | 0.1923 | 341.0443 | 0.096747 | 0 | 0 | 0.19349 | 341.2275 | 0.097144 | 0 | 0 | 0.19429 | 341.5022 | 0.09774 | 0 | 0 | 0.19548 | 341.6854 | 0.098137 | 0 | 0 | 0.19627 | 341.9601 | 0.098733 | 0 | 0 | 0.19747 | 342.2349 | 0.099329 | 0 | 0 | 0.19866 | 342.418 | 0.099726 | 0 | 0 | 0.19945 | 342.6928 | 0.10032 | 0 | 0 | 0.20064 | 342.9675 | 0.10092 | 0 | 0 | 0.20184 | 343.0591 | 0.10112 | 0 | 0 | 0.20223 | 343.3339 | 0.10171 | 0 | 0 | 0.20343 | 343.6086 | 0.10231 | 0 | 0 | 0.20462 | 343.7918 | 0.10271 | 0 | 0 | 0.20541 | 344.0665 | 0.1033 | 0 | 0 | 0.2066 | 344.2497 | 0.1037 | 0 | 0 | 0.2074 | 344.4328 | 0.1041 | 0 | 0 | 0.20819
2017-12-18 03:00 | 317.6238 | 0.94671 |  | 333.5255 | 0.080438 | 0 | 0 | 0.16088 | 342.8979 | 0.10077 | 0 | 0 | 0.20153 | 350.5663 | 0.1174 | 0 | 0 | 0.2348 | 350.8503 | 0.11802 | 0 | 0 | 0.23603 | 351.0396 | 0.11843 | 0 | 0 | 0.23685 | 351.3236 | 0.11904 | 0 | 0 | 0.23809 | 351.6076 | 0.11966 | 0 | 0 | 0.23932 | 351.8917 | 0.12027 | 0 | 0 | 0.24055 | 352.2703 | 0.1211 | 0 | 0 | 0.24219 | 352.5543 | 0.12171 | 0 | 0 | 0.24342 | 352.7437 | 0.12212 | 0 | 0 | 0.24425 | 353.0277 | 0.12274 | 0 | 0 | 0.24548 | 353.217 | 0.12315 | 0 | 0 | 0.2463 | 353.5011 | 0.12377 | 0 | 0 | 0.24753 | 353.7851 | 0.12438 | 0 | 0 | 0.24876 | 353.9744 | 0.12479 | 0 | 0 | 0.24958 | 354.2584 | 0.12541 | 0 | 0 | 0.25082 | 354.5424 | 0.12602 | 0 | 0 | 0.25205 | 354.6371 | 0.12623 | 0 | 0 | 0.25246 | 354.9211 | 0.12685 | 0 | 0 | 0.25369 | 355.2051 | 0.12746 | 0 | 0 | 0.25492 | 355.3945 | 0.12787 | 0 | 0 | 0.25574 | 355.6785 | 0.12849 | 0 | 0 | 0.25698 | 355.8678 | 0.1289 | 0 | 0 | 0.2578 | 356.0572 | 0.12931 | 0 | 0 | 0.25862
2017-12-18 04:00 | 310.6962 | 0.92606 |  | 326.2512 | 0.06466 | 0 | 0 | 0.12932 | 335.4192 | 0.084546 | 0 | 0 | 0.16909 | 342.9203 | 0.10082 | 0 | 0 | 0.20163 | 343.1981 | 0.10142 | 0 | 0 | 0.20284 | 343.3833 | 0.10182 | 0 | 0 | 0.20364 | 343.6611 | 0.10242 | 0 | 0 | 0.20485 | 343.9389 | 0.10303 | 0 | 0 | 0.20605 | 344.2167 | 0.10363 | 0 | 0 | 0.20726 | 344.5872 | 0.10443 | 0 | 0 | 0.20886 | 344.865 | 0.10503 | 0 | 0 | 0.21007 | 345.0502 | 0.10544 | 0 | 0 | 0.21087 | 345.328 | 0.10604 | 0 | 0 | 0.21208 | 345.5132 | 0.10644 | 0 | 0 | 0.21288 | 345.791 | 0.10704 | 0 | 0 | 0.21408 | 346.0689 | 0.10765 | 0 | 0 | 0.21529 | 346.2541 | 0.10805 | 0 | 0 | 0.21609 | 346.5319 | 0.10865 | 0 | 0 | 0.2173 | 346.8097 | 0.10925 | 0 | 0 | 0.2185 | 346.9023 | 0.10945 | 0 | 0 | 0.21891 | 347.1801 | 0.11006 | 0 | 0 | 0.22011 | 347.458 | 0.11066 | 0 | 0 | 0.22132 | 347.6432 | 0.11106 | 0 | 0 | 0.22212 | 347.921 | 0.11166 | 0 | 0 | 0.22332 | 348.1062 | 0.11206 | 0 | 0 | 0.22413 | 348.2914 | 0.11247 | 0 | 0 | 0.22493
2017-12-18 05:00 | 306.228 | 0.91274 |  | 321.5592 | 0.054483 | 0 | 0 | 0.10897 | 330.5953 | 0.074083 | 0 | 0 | 0.14817 | 337.9885 | 0.090119 | 0 | 0 | 0.18024 | 338.2624 | 0.090713 | 0 | 0 | 0.18143 | 338.4449 | 0.091109 | 0 | 0 | 0.18222 | 338.7187 | 0.091703 | 0 | 0 | 0.18341 | 338.9926 | 0.092296 | 0 | 0 | 0.18459 | 339.2664 | 0.09289 | 0 | 0 | 0.18578 | 339.6315 | 0.093682 | 0 | 0 | 0.18736 | 339.9053 | 0.094276 | 0 | 0 | 0.18855 | 340.0878 | 0.094672 | 0 | 0 | 0.18934 | 340.3617 | 0.095266 | 0 | 0 | 0.19053 | 340.5442 | 0.095662 | 0 | 0 | 0.19132 | 340.818 | 0.096256 | 0 | 0 | 0.19251 | 341.0919 | 0.09685 | 0 | 0 | 0.1937 | 341.2744 | 0.097246 | 0 | 0 | 0.19449 | 341.5482 | 0.09784 | 0 | 0 | 0.19568 | 341.8221 | 0.098434 | 0 | 0 | 0.19687 | 341.9133 | 0.098632 | 0 | 0 | 0.19726 | 342.1871 | 0.099226 | 0 | 0 | 0.19845 | 342.461 | 0.099819 | 0 | 0 | 0.19964 | 342.6435 | 0.10022 | 0 | 0 | 0.20043 | 342.9173 | 0.10081 | 0 | 0 | 0.20162 | 343.0999 | 0.10121 | 0 | 0 | 0.20241 | 343.2824 | 0.1016 | 0 | 0 | 0.2032
2017-12-18 06:00 | 305.2583 | 0.90985 |  | 320.541 | 0.052275 | 0 | 0 | 0.10455 | 329.5485 | 0.071812 | 0 | 0 | 0.14362 | 336.9183 | 0.087798 | 0 | 0 | 0.1756 | 337.1913 | 0.08839 | 0 | 0 | 0.17678 | 337.3733 | 0.088784 | 0 | 0 | 0.17757 | 337.6462 | 0.089376 | 0 | 0 | 0.17875 | 337.9192 | 0.089968 | 0 | 0 | 0.17994 | 338.1921 | 0.09056 | 0 | 0 | 0.18112 | 338.5561 | 0.09135 | 0 | 0 | 0.1827 | 338.829 | 0.091942 | 0 | 0 | 0.18388 | 339.011 | 0.092337 | 0 | 0 | 0.18467 | 339.284 | 0.092929 | 0 | 0 | 0.18586 | 339.4659 | 0.093323 | 0 | 0 | 0.18665 | 339.7389 | 0.093915 | 0 | 0 | 0.18783 | 340.0118 | 0.094507 | 0 | 0 | 0.18901 | 340.1938 | 0.094902 | 0 | 0 | 0.1898 | 340.4668 | 0.095494 | 0 | 0 | 0.19099 | 340.7397 | 0.096086 | 0 | 0 | 0.19217 | 340.8307 | 0.096283 | 0 | 0 | 0.19257 | 341.1037 | 0.096875 | 0 | 0 | 0.19375 | 341.3766 | 0.097468 | 0 | 0 | 0.19494 | 341.5586 | 0.097862 | 0 | 0 | 0.19572 | 341.8315 | 0.098454 | 0 | 0 | 0.19691 | 342.0135 | 0.098849 | 0 | 0 | 0.1977 | 342.1955 | 0.099244 | 0 | 0 | 0.19849
2017-12-18 07:00 | 305.0289 | 0.90917 |  | 320.3001 | 0.051753 | 0 | 0 | 0.10351 | 329.3009 | 0.071275 | 0 | 0 | 0.14255 | 336.6652 | 0.087248 | 0 | 0 | 0.1745 | 336.9379 | 0.08784 | 0 | 0 | 0.17568 | 337.1198 | 0.088234 | 0 | 0 | 0.17647 | 337.3925 | 0.088826 | 0 | 0 | 0.17765 | 337.6653 | 0.089418 | 0 | 0 | 0.17884 | 337.938 | 0.090009 | 0 | 0 | 0.18002 | 338.3017 | 0.090798 | 0 | 0 | 0.1816 | 338.5744 | 0.09139 | 0 | 0 | 0.18278 | 338.7563 | 0.091784 | 0 | 0 | 0.18357 | 339.029 | 0.092376 | 0 | 0 | 0.18475 | 339.2108 | 0.09277 | 0 | 0 | 0.18554 | 339.4836 | 0.093362 | 0 | 0 | 0.18672 | 339.7563 | 0.093953 | 0 | 0 | 0.18791 | 339.9382 | 0.094348 | 0 | 0 | 0.1887 | 340.2109 | 0.094939 | 0 | 0 | 0.18988 | 340.4837 | 0.095531 | 0 | 0 | 0.19106 | 340.5746 | 0.095728 | 0 | 0 | 0.19146 | 340.8473 | 0.09632 | 0 | 0 | 0.19264 | 341.1201 | 0.096911 | 0 | 0 | 0.19382 | 341.3019 | 0.097306 | 0 | 0 | 0.19461 | 341.5747 | 0.097897 | 0 | 0 | 0.19579 | 341.7565 | 0.098292 | 0 | 0 | 0.19658 | 341.9384 | 0.098686 | 0 | 0 | 0.19737
2017-12-18 08:00 | 298.399 | 0.88941 |  | 313.3383 | 0.036652 | 0 | 0 | 0.073305 | 322.1434 | 0.055751 | 0 | 0 | 0.1115 | 329.3476 | 0.071377 | 0 | 0 | 0.14275 | 329.6144 | 0.071955 | 0 | 0 | 0.14391 | 329.7923 | 0.072341 | 0 | 0 | 0.14468 | 330.0591 | 0.07292 | 0 | 0 | 0.14584 | 330.3259 | 0.073499 | 0 | 0 | 0.147 | 330.5928 | 0.074077 | 0 | 0 | 0.14815 | 330.9485 | 0.074849 | 0 | 0 | 0.1497 | 331.2153 | 0.075428 | 0 | 0 | 0.15086 | 331.3932 | 0.075814 | 0 | 0 | 0.15163 | 331.6601 | 0.076392 | 0 | 0 | 0.15278 | 331.8379 | 0.076778 | 0 | 0 | 0.15356 | 332.1048 | 0.077357 | 0 | 0 | 0.15471 | 332.3716 | 0.077936 | 0 | 0 | 0.15587 | 332.5495 | 0.078321 | 0 | 0 | 0.15664 | 332.8163 | 0.0789 | 0 | 0 | 0.1578 | 333.0831 | 0.079479 | 0 | 0 | 0.15896 | 333.172 | 0.079672 | 0 | 0 | 0.15934 | 333.4389 | 0.080251 | 0 | 0 | 0.1605 | 333.7057 | 0.080829 | 0 | 0 | 0.16166 | 333.8836 | 0.081215 | 0 | 0 | 0.16243 | 334.1504 | 0.081794 | 0 | 0 | 0.16359 | 334.3283 | 0.08218 | 0 | 0 | 0.16436 | 334.5062 | 0.082565 | 0 | 0 | 0.16513
2017-12-18 09:00 | 288.7924 | 0.86077 |  | 303.2507 | 0.014772 | 0 | 0 | 0.029545 | 311.7723 | 0.033256 | 0 | 0 | 0.066512 | 318.7446 | 0.048379 | 0 | 0 | 0.096757 | 319.0028 | 0.048939 | 0 | 0 | 0.097878 | 319.175 | 0.049312 | 0 | 0 | 0.098624 | 319.4332 | 0.049872 | 0 | 0 | 0.099745 | 319.6915 | 0.050432 | 0 | 0 | 0.10086 | 319.9497 | 0.050993 | 0 | 0 | 0.10199 | 320.294 | 0.051739 | 0 | 0 | 0.10348 | 320.5522 | 0.052299 | 0 | 0 | 0.1046 | 320.7244 | 0.052673 | 0 | 0 | 0.10535 | 320.9826 | 0.053233 | 0 | 0 | 0.10647 | 321.1548 | 0.053606 | 0 | 0 | 0.10721 | 321.413 | 0.054166 | 0 | 0 | 0.10833 | 321.6712 | 0.054727 | 0 | 0 | 0.10945 | 321.8434 | 0.0551 | 0 | 0 | 0.1102 | 322.1016 | 0.05566 | 0 | 0 | 0.11132 | 322.3599 | 0.05622 | 0 | 0 | 0.11244 | 322.4459 | 0.056407 | 0 | 0 | 0.11281 | 322.7042 | 0.056967 | 0 | 0 | 0.11393 | 322.9624 | 0.057527 | 0 | 0 | 0.11505 | 323.1346 | 0.0579 | 0 | 0 | 0.1158 | 323.3928 | 0.058461 | 0 | 0 | 0.11692 | 323.5649 | 0.058834 | 0 | 0 | 0.11767 | 323.7371 | 0.059207 | 0 | 0 | 0.11841
2017-12-18 10:00 | 297.2177 | 0.88589 |  | 312.0978 | 0.033962 | 0 | 0 | 0.067924 | 320.8681 | 0.052985 | 0 | 0 | 0.10597 | 328.0438 | 0.068549 | 0 | 0 | 0.1371 | 328.3096 | 0.069125 | 0 | 0 | 0.13825 | 328.4867 | 0.069509 | 0 | 0 | 0.13902 | 328.7525 | 0.070086 | 0 | 0 | 0.14017 | 329.0183 | 0.070662 | 0 | 0 | 0.14132 | 329.284 | 0.071239 | 0 | 0 | 0.14248 | 329.6384 | 0.072007 | 0 | 0 | 0.14401 | 329.9042 | 0.072584 | 0 | 0 | 0.14517 | 330.0813 | 0.072968 | 0 | 0 | 0.14594 | 330.3471 | 0.073545 | 0 | 0 | 0.14709 | 330.5243 | 0.073929 | 0 | 0 | 0.14786 | 330.7901 | 0.074505 | 0 | 0 | 0.14901 | 331.0558 | 0.075082 | 0 | 0 | 0.15016 | 331.233 | 0.075466 | 0 | 0 | 0.15093 | 331.4988 | 0.076042 | 0 | 0 | 0.15208 | 331.7645 | 0.076619 | 0 | 0 | 0.15324 | 331.8531 | 0.076811 | 0 | 0 | 0.15362 | 332.1189 | 0.077387 | 0 | 0 | 0.15477 | 332.3846 | 0.077964 | 0 | 0 | 0.15593 | 332.5618 | 0.078348 | 0 | 0 | 0.1567 | 332.8276 | 0.078925 | 0 | 0 | 0.15785 | 333.0048 | 0.079309 | 0 | 0 | 0.15862 | 333.1819 | 0.079693 | 0 | 0 | 0.15939
2017-12-18 11:00 | 296.4591 | 0.88363 |  | 311.3012 | 0.032234 | 0 | 0 | 0.064468 | 320.0491 | 0.051208 | 0 | 0 | 0.10242 | 327.2065 | 0.066733 | 0 | 0 | 0.13347 | 327.4716 | 0.067307 | 0 | 0 | 0.13461 | 327.6483 | 0.067691 | 0 | 0 | 0.13538 | 327.9134 | 0.068266 | 0 | 0 | 0.13653 | 328.1785 | 0.068841 | 0 | 0 | 0.13768 | 328.4436 | 0.069416 | 0 | 0 | 0.13883 | 328.797 | 0.070182 | 0 | 0 | 0.14036 | 329.0621 | 0.070757 | 0 | 0 | 0.14151 | 329.2388 | 0.071141 | 0 | 0 | 0.14228 | 329.5039 | 0.071716 | 0 | 0 | 0.14343 | 329.6806 | 0.072099 | 0 | 0 | 0.1442 | 329.9457 | 0.072674 | 0 | 0 | 0.14535 | 330.2108 | 0.073249 | 0 | 0 | 0.1465 | 330.3875 | 0.073632 | 0 | 0 | 0.14726 | 330.6526 | 0.074207 | 0 | 0 | 0.14841 | 330.9177 | 0.074782 | 0 | 0 | 0.14956 | 331.0061 | 0.074974 | 0 | 0 | 0.14995 | 331.2712 | 0.075549 | 0 | 0 | 0.1511 | 331.5362 | 0.076124 | 0 | 0 | 0.15225 | 331.713 | 0.076507 | 0 | 0 | 0.15301 | 331.9781 | 0.077082 | 0 | 0 | 0.15416 | 332.1548 | 0.077465 | 0 | 0 | 0.15493 | 332.3315 | 0.077849 | 0 | 0 | 0.1557
2017-12-18 12:00 | 289.1401 | 0.86181 |  | 303.6159 | 0.015564 | 0 | 0 | 0.031129 | 312.1478 | 0.03407 | 0 | 0 | 0.06814 | 319.1284 | 0.049211 | 0 | 0 | 0.098422 | 319.387 | 0.049772 | 0 | 0 | 0.099544 | 319.5594 | 0.050146 | 0 | 0 | 0.10029 | 319.8179 | 0.050707 | 0 | 0 | 0.10141 | 320.0764 | 0.051267 | 0 | 0 | 0.10253 | 320.335 | 0.051828 | 0 | 0 | 0.10366 | 320.6797 | 0.052576 | 0 | 0 | 0.10515 | 320.9383 | 0.053137 | 0 | 0 | 0.10627 | 321.1106 | 0.053511 | 0 | 0 | 0.10702 | 321.3692 | 0.054071 | 0 | 0 | 0.10814 | 321.5415 | 0.054445 | 0 | 0 | 0.10889 | 321.8001 | 0.055006 | 0 | 0 | 0.11001 | 322.0586 | 0.055567 | 0 | 0 | 0.11113 | 322.231 | 0.055941 | 0 | 0 | 0.11188 | 322.4895 | 0.056501 | 0 | 0 | 0.113 | 322.7481 | 0.057062 | 0 | 0 | 0.11412 | 322.8342 | 0.057249 | 0 | 0 | 0.1145 | 323.0928 | 0.05781 | 0 | 0 | 0.11562 | 323.3513 | 0.058371 | 0 | 0 | 0.11674 | 323.5237 | 0.058745 | 0 | 0 | 0.11749 | 323.7822 | 0.059305 | 0 | 0 | 0.11861 | 323.9546 | 0.059679 | 0 | 0 | 0.11936 | 324.1269 | 0.060053 | 0 | 0 | 0.12011
2017-12-18 13:00 | 284.4277 | 0.84776 |  | 298.6675 | 0.0048315 | 0 | 0 | 0.0096629 | 307.0604 | 0.023036 | 0 | 0 | 0.046071 | 313.9273 | 0.03793 | 0 | 0 | 0.07586 | 314.1816 | 0.038482 | 0 | 0 | 0.076963 | 314.3512 | 0.038849 | 0 | 0 | 0.077699 | 314.6055 | 0.039401 | 0 | 0 | 0.078802 | 314.8598 | 0.039953 | 0 | 0 | 0.079905 | 315.1141 | 0.040504 | 0 | 0 | 0.081008 | 315.4532 | 0.04124 | 0 | 0 | 0.082479 | 315.7076 | 0.041791 | 0 | 0 | 0.083583 | 315.8771 | 0.042159 | 0 | 0 | 0.084318 | 316.1315 | 0.042711 | 0 | 0 | 0.085422 | 316.301 | 0.043079 | 0 | 0 | 0.086157 | 316.5553 | 0.04363 | 0 | 0 | 0.08726 | 316.8097 | 0.044182 | 0 | 0 | 0.088364 | 316.9792 | 0.04455 | 0 | 0 | 0.089099 | 317.2336 | 0.045101 | 0 | 0 | 0.090202 | 317.4879 | 0.045653 | 0 | 0 | 0.091306 | 317.5727 | 0.045837 | 0 | 0 | 0.091673 | 317.827 | 0.046388 | 0 | 0 | 0.092777 | 318.0813 | 0.04694 | 0 | 0 | 0.09388 | 318.2509 | 0.047308 | 0 | 0 | 0.094616 | 318.5052 | 0.047859 | 0 | 0 | 0.095719 | 318.6748 | 0.048227 | 0 | 0 | 0.096454 | 318.8443 | 0.048595 | 0 | 0 | 0.09719
2017-12-18 14:00 | 288.051 | 0.85856 |  | 302.4722 | 0.013084 | 0 | 0 | 0.026168 | 310.972 | 0.03152 | 0 | 0 | 0.06304 | 317.9264 | 0.046604 | 0 | 0 | 0.093208 | 318.1839 | 0.047163 | 0 | 0 | 0.094325 | 318.3556 | 0.047535 | 0 | 0 | 0.09507 | 318.6132 | 0.048094 | 0 | 0 | 0.096187 | 318.8708 | 0.048652 | 0 | 0 | 0.097305 | 319.1284 | 0.049211 | 0 | 0 | 0.098422 | 319.4718 | 0.049956 | 0 | 0 | 0.099912 | 319.7293 | 0.050515 | 0 | 0 | 0.10103 | 319.9011 | 0.050887 | 0 | 0 | 0.10177 | 320.1586 | 0.051446 | 0 | 0 | 0.10289 | 320.3303 | 0.051818 | 0 | 0 | 0.10364 | 320.5879 | 0.052377 | 0 | 0 | 0.10475 | 320.8455 | 0.052935 | 0 | 0 | 0.10587 | 321.0172 | 0.053308 | 0 | 0 | 0.10662 | 321.2748 | 0.053867 | 0 | 0 | 0.10773 | 321.5323 | 0.054425 | 0 | 0 | 0.10885 | 321.6182 | 0.054611 | 0 | 0 | 0.10922 | 321.8758 | 0.05517 | 0 | 0 | 0.11034 | 322.1333 | 0.055729 | 0 | 0 | 0.11146 | 322.305 | 0.056101 | 0 | 0 | 0.1122 | 322.5626 | 0.05666 | 0 | 0 | 0.11332 | 322.7343 | 0.057032 | 0 | 0 | 0.11406 | 322.906 | 0.057405 | 0 | 0 | 0.11481
2017-12-18 15:00 | 290.6198 | 0.86622 |  | 305.1696 | 0.018935 | 0 | 0 | 0.037869 | 313.7452 | 0.037535 | 0 | 0 | 0.07507 | 320.7616 | 0.052754 | 0 | 0 | 0.10551 | 321.0215 | 0.053317 | 0 | 0 | 0.10663 | 321.1947 | 0.053693 | 0 | 0 | 0.10739 | 321.4546 | 0.054257 | 0 | 0 | 0.10851 | 321.7145 | 0.05482 | 0 | 0 | 0.10964 | 321.9743 | 0.055384 | 0 | 0 | 0.11077 | 322.3208 | 0.056135 | 0 | 0 | 0.11227 | 322.5807 | 0.056699 | 0 | 0 | 0.1134 | 322.7539 | 0.057075 | 0 | 0 | 0.11415 | 323.0138 | 0.057639 | 0 | 0 | 0.11528 | 323.187 | 0.058014 | 0 | 0 | 0.11603 | 323.4469 | 0.058578 | 0 | 0 | 0.11716 | 323.7068 | 0.059142 | 0 | 0 | 0.11828 | 323.88 | 0.059517 | 0 | 0 | 0.11903 | 324.1399 | 0.060081 | 0 | 0 | 0.12016 | 324.3997 | 0.060645 | 0 | 0 | 0.12129 | 324.4864 | 0.060833 | 0 | 0 | 0.12167 | 324.7462 | 0.061396 | 0 | 0 | 0.12279 | 325.0061 | 0.06196 | 0 | 0 | 0.12392 | 325.1793 | 0.062336 | 0 | 0 | 0.12467 | 325.4392 | 0.062899 | 0 | 0 | 0.1258 | 325.6125 | 0.063275 | 0 | 0 | 0.12655 | 325.7857 | 0.063651 | 0 | 0 | 0.1273
2017-12-18 16:00 | 298.6811 | 0.89025 |  | 313.6345 | 0.037295 | 0 | 0 | 0.07459 | 322.448 | 0.056411 | 0 | 0 | 0.11282 | 329.659 | 0.072052 | 0 | 0 | 0.1441 | 329.9261 | 0.072631 | 0 | 0 | 0.14526 | 330.1041 | 0.073017 | 0 | 0 | 0.14603 | 330.3712 | 0.073597 | 0 | 0 | 0.14719 | 330.6383 | 0.074176 | 0 | 0 | 0.14835 | 330.9053 | 0.074755 | 0 | 0 | 0.14951 | 331.2614 | 0.075528 | 0 | 0 | 0.15106 | 331.5285 | 0.076107 | 0 | 0 | 0.15221 | 331.7066 | 0.076493 | 0 | 0 | 0.15299 | 331.9736 | 0.077072 | 0 | 0 | 0.15414 | 332.1517 | 0.077459 | 0 | 0 | 0.15492 | 332.4188 | 0.078038 | 0 | 0 | 0.15608 | 332.6858 | 0.078617 | 0 | 0 | 0.15723 | 332.8639 | 0.079003 | 0 | 0 | 0.15801 | 333.131 | 0.079583 | 0 | 0 | 0.15917 | 333.398 | 0.080162 | 0 | 0 | 0.16032 | 333.4871 | 0.080355 | 0 | 0 | 0.16071 | 333.7541 | 0.080934 | 0 | 0 | 0.16187 | 334.0212 | 0.081514 | 0 | 0 | 0.16303 | 334.1993 | 0.0819 | 0 | 0 | 0.1638 | 334.4663 | 0.082479 | 0 | 0 | 0.16496 | 334.6444 | 0.082865 | 0 | 0 | 0.16573 | 334.8224 | 0.083252 | 0 | 0 | 0.1665
2017-12-18 17:00 | 307.1458 | 0.91548 |  | 322.523 | 0.056574 | 0 | 0 | 0.11315 | 331.5862 | 0.076232 | 0 | 0 | 0.15246 | 339.0016 | 0.092316 | 0 | 0 | 0.18463 | 339.2762 | 0.092912 | 0 | 0 | 0.18582 | 339.4593 | 0.093309 | 0 | 0 | 0.18662 | 339.734 | 0.093905 | 0 | 0 | 0.18781 | 340.0086 | 0.0945 | 0 | 0 | 0.189 | 340.2833 | 0.095096 | 0 | 0 | 0.19019 | 340.6494 | 0.09589 | 0 | 0 | 0.19178 | 340.9241 | 0.096486 | 0 | 0 | 0.19297 | 341.1072 | 0.096883 | 0 | 0 | 0.19377 | 341.3818 | 0.097479 | 0 | 0 | 0.19496 | 341.5649 | 0.097876 | 0 | 0 | 0.19575 | 341.8396 | 0.098472 | 0 | 0 | 0.19694 | 342.1142 | 0.099067 | 0 | 0 | 0.19813 | 342.2973 | 0.099464 | 0 | 0 | 0.19893 | 342.5719 | 0.10006 | 0 | 0 | 0.20012 | 342.8466 | 0.10066 | 0 | 0 | 0.20131 | 342.9381 | 0.10085 | 0 | 0 | 0.20171 | 343.2128 | 0.10145 | 0 | 0 | 0.2029 | 343.4874 | 0.10205 | 0 | 0 | 0.20409 | 343.6705 | 0.10244 | 0 | 0 | 0.20489 | 343.9452 | 0.10304 | 0 | 0 | 0.20608 | 344.1283 | 0.10344 | 0 | 0 | 0.20687 | 344.3114 | 0.10383 | 0 | 0 | 0.20767
2017-12-18 18:00 | 311.6854 | 0.92901 |  | 327.2898 | 0.066913 | 0 | 0 | 0.13383 | 336.487 | 0.086862 | 0 | 0 | 0.17372 | 344.012 | 0.10318 | 0 | 0 | 0.20637 | 344.2907 | 0.10379 | 0 | 0 | 0.20758 | 344.4765 | 0.10419 | 0 | 0 | 0.20838 | 344.7552 | 0.1048 | 0 | 0 | 0.20959 | 345.0339 | 0.1054 | 0 | 0 | 0.2108 | 345.3126 | 0.106 | 0 | 0 | 0.21201 | 345.6842 | 0.10681 | 0 | 0 | 0.21362 | 345.9629 | 0.10742 | 0 | 0 | 0.21483 | 346.1487 | 0.10782 | 0 | 0 | 0.21564 | 346.4274 | 0.10842 | 0 | 0 | 0.21685 | 346.6132 | 0.10883 | 0 | 0 | 0.21765 | 346.8919 | 0.10943 | 0 | 0 | 0.21886 | 347.1706 | 0.11003 | 0 | 0 | 0.22007 | 347.3564 | 0.11044 | 0 | 0 | 0.22088 | 347.6351 | 0.11104 | 0 | 0 | 0.22208 | 347.9138 | 0.11165 | 0 | 0 | 0.22329 | 348.0067 | 0.11185 | 0 | 0 | 0.2237 | 348.2854 | 0.11245 | 0 | 0 | 0.22491 | 348.5641 | 0.11306 | 0 | 0 | 0.22611 | 348.7499 | 0.11346 | 0 | 0 | 0.22692 | 349.0286 | 0.11406 | 0 | 0 | 0.22813 | 349.2144 | 0.11447 | 0 | 0 | 0.22894 | 349.4002 | 0.11487 | 0 | 0 | 0.22974
2017-12-18 19:00 | 312.1664 | 0.93044 |  | 327.7949 | 0.068009 | 0 | 0 | 0.13602 | 337.0063 | 0.087988 | 0 | 0 | 0.17598 | 344.5429 | 0.10434 | 0 | 0 | 0.20867 | 344.822 | 0.10494 | 0 | 0 | 0.20988 | 345.0081 | 0.10534 | 0 | 0 | 0.21069 | 345.2873 | 0.10595 | 0 | 0 | 0.2119 | 345.5664 | 0.10656 | 0 | 0 | 0.21311 | 345.8455 | 0.10716 | 0 | 0 | 0.21432 | 346.2177 | 0.10797 | 0 | 0 | 0.21594 | 346.4968 | 0.10857 | 0 | 0 | 0.21715 | 346.6829 | 0.10898 | 0 | 0 | 0.21795 | 346.9621 | 0.10958 | 0 | 0 | 0.21916 | 347.1481 | 0.10999 | 0 | 0 | 0.21997 | 347.4273 | 0.11059 | 0 | 0 | 0.22118 | 347.7064 | 0.1112 | 0 | 0 | 0.22239 | 347.8925 | 0.1116 | 0 | 0 | 0.2232 | 348.1716 | 0.11221 | 0 | 0 | 0.22441 | 348.4508 | 0.11281 | 0 | 0 | 0.22562 | 348.5438 | 0.11301 | 0 | 0 | 0.22603 | 348.8229 | 0.11362 | 0 | 0 | 0.22724 | 349.1021 | 0.11422 | 0 | 0 | 0.22845 | 349.2882 | 0.11463 | 0 | 0 | 0.22926 | 349.5673 | 0.11523 | 0 | 0 | 0.23047 | 349.7534 | 0.11564 | 0 | 0 | 0.23127 | 349.9395 | 0.11604 | 0 | 0 | 0.23208
2017-12-18 20:00 | 313.1908 | 0.9335 |  | 328.8706 | 0.070342 | 0 | 0 | 0.14068 | 338.1122 | 0.090387 | 0 | 0 | 0.18077 | 345.6735 | 0.10679 | 0 | 0 | 0.21357 | 345.9536 | 0.10739 | 0 | 0 | 0.21479 | 346.1403 | 0.1078 | 0 | 0 | 0.2156 | 346.4203 | 0.10841 | 0 | 0 | 0.21681 | 346.7004 | 0.10901 | 0 | 0 | 0.21803 | 346.9804 | 0.10962 | 0 | 0 | 0.21924 | 347.3538 | 0.11043 | 0 | 0 | 0.22086 | 347.6339 | 0.11104 | 0 | 0 | 0.22208 | 347.8206 | 0.11144 | 0 | 0 | 0.22289 | 348.1006 | 0.11205 | 0 | 0 | 0.2241 | 348.2873 | 0.11246 | 0 | 0 | 0.22491 | 348.5674 | 0.11306 | 0 | 0 | 0.22613 | 348.8474 | 0.11367 | 0 | 0 | 0.22734 | 349.0341 | 0.11408 | 0 | 0 | 0.22815 | 349.3142 | 0.11468 | 0 | 0 | 0.22937 | 349.5942 | 0.11529 | 0 | 0 | 0.23058 | 349.6875 | 0.11549 | 0 | 0 | 0.23099 | 349.9676 | 0.1161 | 0 | 0 | 0.2322 | 350.2476 | 0.11671 | 0 | 0 | 0.23342 | 350.4343 | 0.11711 | 0 | 0 | 0.23423 | 350.7144 | 0.11772 | 0 | 0 | 0.23544 | 350.9011 | 0.11813 | 0 | 0 | 0.23625 | 351.0878 | 0.11853 | 0 | 0 | 0.23706
2017-12-18 21:00 | 321.8363 | 0.95926 |  | 337.949 | 0.090033 | 0 | 0 | 0.18007 | 347.4457 | 0.11063 | 0 | 0 | 0.22126 | 355.2157 | 0.12748 | 0 | 0 | 0.25497 | 355.5035 | 0.12811 | 0 | 0 | 0.25622 | 355.6954 | 0.12852 | 0 | 0 | 0.25705 | 355.9831 | 0.12915 | 0 | 0 | 0.2583 | 356.2709 | 0.12977 | 0 | 0 | 0.25955 | 356.5587 | 0.1304 | 0 | 0 | 0.26079 | 356.9424 | 0.13123 | 0 | 0 | 0.26246 | 357.2302 | 0.13185 | 0 | 0 | 0.26371 | 357.422 | 0.13227 | 0 | 0 | 0.26454 | 357.7098 | 0.13289 | 0 | 0 | 0.26579 | 357.9017 | 0.13331 | 0 | 0 | 0.26662 | 358.1895 | 0.13393 | 0 | 0 | 0.26787 | 358.4772 | 0.13456 | 0 | 0 | 0.26912 | 358.6691 | 0.13497 | 0 | 0 | 0.26995 | 358.9569 | 0.1356 | 0 | 0 | 0.2712 | 359.2446 | 0.13622 | 0 | 0 | 0.27245 | 359.3406 | 0.13643 | 0 | 0 | 0.27286 | 359.6283 | 0.13706 | 0 | 0 | 0.27411 | 359.9161 | 0.13768 | 0 | 0 | 0.27536 | 360.108 | 0.1381 | 0 | 0 | 0.27619 | 360.3958 | 0.13872 | 0 | 0 | 0.27744 | 360.5876 | 0.13914 | 0 | 0 | 0.27827 | 360.7795 | 0.13955 | 0 | 0 | 0.2791
2017-12-18 22:00 | 321.8026 | 0.95916 |  | 337.9136 | 0.089956 | 0 | 0 | 0.17991 | 347.4093 | 0.11055 | 0 | 0 | 0.2211 | 355.1785 | 0.1274 | 0 | 0 | 0.25481 | 355.4663 | 0.12803 | 0 | 0 | 0.25606 | 355.6581 | 0.12844 | 0 | 0 | 0.25689 | 355.9458 | 0.12907 | 0 | 0 | 0.25814 | 356.2336 | 0.12969 | 0 | 0 | 0.25938 | 356.5213 | 0.13032 | 0 | 0 | 0.26063 | 356.905 | 0.13115 | 0 | 0 | 0.2623 | 357.1928 | 0.13177 | 0 | 0 | 0.26355 | 357.3846 | 0.13219 | 0 | 0 | 0.26438 | 357.6723 | 0.13281 | 0 | 0 | 0.26563 | 357.8642 | 0.13323 | 0 | 0 | 0.26646 | 358.1519 | 0.13385 | 0 | 0 | 0.26771 | 358.4397 | 0.13448 | 0 | 0 | 0.26895 | 358.6315 | 0.13489 | 0 | 0 | 0.26979 | 358.9193 | 0.13552 | 0 | 0 | 0.27103 | 359.207 | 0.13614 | 0 | 0 | 0.27228 | 359.3029 | 0.13635 | 0 | 0 | 0.2727 | 359.5907 | 0.13697 | 0 | 0 | 0.27395 | 359.8784 | 0.1376 | 0 | 0 | 0.2752 | 360.0702 | 0.13801 | 0 | 0 | 0.27603 | 360.358 | 0.13864 | 0 | 0 | 0.27728 | 360.5498 | 0.13905 | 0 | 0 | 0.27811 | 360.7417 | 0.13947 | 0 | 0 | 0.27894
2017-12-18 23:00 | 318.8317 | 0.95031 |  | 334.794 | 0.08319 | 0 | 0 | 0.16638 | 344.202 | 0.1036 | 0 | 0 | 0.20719 | 351.8995 | 0.12029 | 0 | 0 | 0.24058 | 352.1846 | 0.12091 | 0 | 0 | 0.24182 | 352.3747 | 0.12132 | 0 | 0 | 0.24264 | 352.6598 | 0.12194 | 0 | 0 | 0.24388 | 352.9449 | 0.12256 | 0 | 0 | 0.24512 | 353.23 | 0.12318 | 0 | 0 | 0.24635 | 353.6101 | 0.124 | 0 | 0 | 0.248 | 353.8952 | 0.12462 | 0 | 0 | 0.24924 | 354.0852 | 0.12503 | 0 | 0 | 0.25007 | 354.3703 | 0.12565 | 0 | 0 | 0.2513 | 354.5604 | 0.12606 | 0 | 0 | 0.25213 | 354.8455 | 0.12668 | 0 | 0 | 0.25336 | 355.1306 | 0.1273 | 0 | 0 | 0.2546 | 355.3206 | 0.12771 | 0 | 0 | 0.25542 | 355.6057 | 0.12833 | 0 | 0 | 0.25666 | 355.8908 | 0.12895 | 0 | 0 | 0.2579 | 355.9859 | 0.12915 | 0 | 0 | 0.25831 | 356.271 | 0.12977 | 0 | 0 | 0.25955 | 356.556 | 0.13039 | 0 | 0 | 0.26078 | 356.7461 | 0.1308 | 0 | 0 | 0.26161 | 357.0312 | 0.13142 | 0 | 0 | 0.26284 | 357.2213 | 0.13183 | 0 | 0 | 0.26367 | 357.4113 | 0.13225 | 0 | 0 | 0.26449
2017-12-19 | 315.0807 | 0.93913 |  | 330.8552 | 0.074646 | 0 | 0 | 0.14929 | 340.1525 | 0.094813 | 0 | 0 | 0.18963 | 347.7595 | 0.11131 | 0 | 0 | 0.22262 | 348.0412 | 0.11192 | 0 | 0 | 0.22385 | 348.2291 | 0.11233 | 0 | 0 | 0.22466 | 348.5108 | 0.11294 | 0 | 0 | 0.22588 | 348.7925 | 0.11355 | 0 | 0 | 0.22711 | 349.0743 | 0.11416 | 0 | 0 | 0.22833 | 349.4499 | 0.11498 | 0 | 0 | 0.22996 | 349.7317 | 0.11559 | 0 | 0 | 0.23118 | 349.9195 | 0.116 | 0 | 0 | 0.23199 | 350.2012 | 0.11661 | 0 | 0 | 0.23322 | 350.389 | 0.11702 | 0 | 0 | 0.23403 | 350.6708 | 0.11763 | 0 | 0 | 0.23525 | 350.9525 | 0.11824 | 0 | 0 | 0.23648 | 351.1404 | 0.11865 | 0 | 0 | 0.23729 | 351.4221 | 0.11926 | 0 | 0 | 0.23851 | 351.7038 | 0.11987 | 0 | 0 | 0.23973 | 351.7977 | 0.12007 | 0 | 0 | 0.24014 | 352.0795 | 0.12068 | 0 | 0 | 0.24136 | 352.3612 | 0.12129 | 0 | 0 | 0.24259 | 352.549 | 0.1217 | 0 | 0 | 0.2434 | 352.8308 | 0.12231 | 0 | 0 | 0.24462 | 353.0186 | 0.12272 | 0 | 0 | 0.24544 | 353.2064 | 0.12313 | 0 | 0 | 0.24625
2017-12-19 01:00 | 315.8309 | 0.94136 |  | 331.6429 | 0.076355 | 0 | 0 | 0.15271 | 340.9624 | 0.096569 | 0 | 0 | 0.19314 | 348.5875 | 0.11311 | 0 | 0 | 0.22622 | 348.8699 | 0.11372 | 0 | 0 | 0.22744 | 349.0581 | 0.11413 | 0 | 0 | 0.22826 | 349.3406 | 0.11474 | 0 | 0 | 0.22948 | 349.623 | 0.11535 | 0 | 0 | 0.23071 | 349.9054 | 0.11597 | 0 | 0 | 0.23193 | 350.2819 | 0.11678 | 0 | 0 | 0.23357 | 350.5643 | 0.1174 | 0 | 0 | 0.23479 | 350.7526 | 0.1178 | 0 | 0 | 0.23561 | 351.035 | 0.11842 | 0 | 0 | 0.23683 | 351.2233 | 0.11882 | 0 | 0 | 0.23765 | 351.5057 | 0.11944 | 0 | 0 | 0.23887 | 351.7881 | 0.12005 | 0 | 0 | 0.2401 | 351.9764 | 0.12046 | 0 | 0 | 0.24092 | 352.2588 | 0.12107 | 0 | 0 | 0.24214 | 352.5412 | 0.12168 | 0 | 0 | 0.24337 | 352.6353 | 0.12189 | 0 | 0 | 0.24378 | 352.9177 | 0.1225 | 0 | 0 | 0.245 | 353.2001 | 0.12311 | 0 | 0 | 0.24623 | 353.3884 | 0.12352 | 0 | 0 | 0.24704 | 353.6708 | 0.12413 | 0 | 0 | 0.24827 | 353.8591 | 0.12454 | 0 | 0 | 0.24908 | 354.0474 | 0.12495 | 0 | 0 | 0.2499
2017-12-19 02:00 | 318.098 | 0.94812 |  | 334.0235 | 0.081519 | 0 | 0 | 0.16304 | 343.4099 | 0.10188 | 0 | 0 | 0.20376 | 351.0897 | 0.11854 | 0 | 0 | 0.23707 | 351.3741 | 0.11915 | 0 | 0 | 0.2383 | 351.5637 | 0.11956 | 0 | 0 | 0.23913 | 351.8482 | 0.12018 | 0 | 0 | 0.24036 | 352.1326 | 0.1208 | 0 | 0 | 0.24159 | 352.417 | 0.12141 | 0 | 0 | 0.24283 | 352.7963 | 0.12224 | 0 | 0 | 0.24447 | 353.0807 | 0.12285 | 0 | 0 | 0.24571 | 353.2703 | 0.12327 | 0 | 0 | 0.24653 | 353.5548 | 0.12388 | 0 | 0 | 0.24776 | 353.7444 | 0.12429 | 0 | 0 | 0.24859 | 354.0288 | 0.12491 | 0 | 0 | 0.24982 | 354.3133 | 0.12553 | 0 | 0 | 0.25105 | 354.5029 | 0.12594 | 0 | 0 | 0.25188 | 354.7873 | 0.12656 | 0 | 0 | 0.25311 | 355.0718 | 0.12717 | 0 | 0 | 0.25434 | 355.1666 | 0.12738 | 0 | 0 | 0.25476 | 355.451 | 0.12799 | 0 | 0 | 0.25599 | 355.7355 | 0.12861 | 0 | 0 | 0.25722 | 355.9251 | 0.12902 | 0 | 0 | 0.25805 | 356.2095 | 0.12964 | 0 | 0 | 0.25928 | 356.3991 | 0.13005 | 0 | 0 | 0.2601 | 356.5888 | 0.13046 | 0 | 0 | 0.26093
2017-12-19 03:00 | 319.2358 | 0.95151 |  | 335.2183 | 0.08411 | 0 | 0 | 0.16822 | 344.6382 | 0.10454 | 0 | 0 | 0.20908 | 352.3455 | 0.12126 | 0 | 0 | 0.24252 | 352.631 | 0.12188 | 0 | 0 | 0.24376 | 352.8213 | 0.12229 | 0 | 0 | 0.24458 | 353.1067 | 0.12291 | 0 | 0 | 0.24582 | 353.3922 | 0.12353 | 0 | 0 | 0.24706 | 353.6776 | 0.12415 | 0 | 0 | 0.2483 | 354.0582 | 0.12497 | 0 | 0 | 0.24995 | 354.3437 | 0.12559 | 0 | 0 | 0.25119 | 354.534 | 0.12601 | 0 | 0 | 0.25201 | 354.8194 | 0.12663 | 0 | 0 | 0.25325 | 355.0097 | 0.12704 | 0 | 0 | 0.25408 | 355.2952 | 0.12766 | 0 | 0 | 0.25531 | 355.5807 | 0.12828 | 0 | 0 | 0.25655 | 355.771 | 0.12869 | 0 | 0 | 0.25738 | 356.0564 | 0.12931 | 0 | 0 | 0.25862 | 356.3419 | 0.12993 | 0 | 0 | 0.25985 | 356.437 | 0.13013 | 0 | 0 | 0.26027 | 356.7225 | 0.13075 | 0 | 0 | 0.26151 | 357.0079 | 0.13137 | 0 | 0 | 0.26274 | 357.1982 | 0.13178 | 0 | 0 | 0.26357 | 357.4837 | 0.1324 | 0 | 0 | 0.26481 | 357.674 | 0.13282 | 0 | 0 | 0.26563 | 357.8643 | 0.13323 | 0 | 0 | 0.26646
2017-12-19 04:00 | 318.9872 | 0.95077 |  | 334.9572 | 0.083544 | 0 | 0 | 0.16709 | 344.3698 | 0.10396 | 0 | 0 | 0.20792 | 352.0711 | 0.12066 | 0 | 0 | 0.24133 | 352.3563 | 0.12128 | 0 | 0 | 0.24256 | 352.5465 | 0.12169 | 0 | 0 | 0.24339 | 352.8317 | 0.12231 | 0 | 0 | 0.24463 | 353.1169 | 0.12293 | 0 | 0 | 0.24586 | 353.4022 | 0.12355 | 0 | 0 | 0.2471 | 353.7825 | 0.12438 | 0 | 0 | 0.24875 | 354.0677 | 0.12499 | 0 | 0 | 0.24999 | 354.2579 | 0.12541 | 0 | 0 | 0.25081 | 354.5431 | 0.12603 | 0 | 0 | 0.25205 | 354.7332 | 0.12644 | 0 | 0 | 0.25288 | 355.0185 | 0.12706 | 0 | 0 | 0.25411 | 355.3037 | 0.12768 | 0 | 0 | 0.25535 | 355.4939 | 0.12809 | 0 | 0 | 0.25618 | 355.7791 | 0.12871 | 0 | 0 | 0.25741 | 356.0643 | 0.12933 | 0 | 0 | 0.25865 | 356.1594 | 0.12953 | 0 | 0 | 0.25906 | 356.4446 | 0.13015 | 0 | 0 | 0.2603 | 356.7299 | 0.13077 | 0 | 0 | 0.26154 | 356.92 | 0.13118 | 0 | 0 | 0.26236 | 357.2053 | 0.1318 | 0 | 0 | 0.2636 | 357.3954 | 0.13221 | 0 | 0 | 0.26442 | 357.5856 | 0.13262 | 0 | 0 | 0.26525
2017-12-19 05:00 | 318.9029 | 0.95052 |  | 334.8687 | 0.083352 | 0 | 0 | 0.1667 | 344.2789 | 0.10376 | 0 | 0 | 0.20753 | 351.9781 | 0.12046 | 0 | 0 | 0.24092 | 352.2633 | 0.12108 | 0 | 0 | 0.24216 | 352.4534 | 0.12149 | 0 | 0 | 0.24299 | 352.7385 | 0.12211 | 0 | 0 | 0.24422 | 353.0237 | 0.12273 | 0 | 0 | 0.24546 | 353.3088 | 0.12335 | 0 | 0 | 0.2467 | 353.689 | 0.12417 | 0 | 0 | 0.24835 | 353.9742 | 0.12479 | 0 | 0 | 0.24958 | 354.1643 | 0.1252 | 0 | 0 | 0.25041 | 354.4495 | 0.12582 | 0 | 0 | 0.25165 | 354.6396 | 0.12623 | 0 | 0 | 0.25247 | 354.9247 | 0.12685 | 0 | 0 | 0.25371 | 355.2099 | 0.12747 | 0 | 0 | 0.25494 | 355.4 | 0.12788 | 0 | 0 | 0.25577 | 355.6851 | 0.1285 | 0 | 0 | 0.25701 | 355.9703 | 0.12912 | 0 | 0 | 0.25824 | 356.0653 | 0.12933 | 0 | 0 | 0.25865 | 356.3505 | 0.12995 | 0 | 0 | 0.25989 | 356.6357 | 0.13056 | 0 | 0 | 0.26113 | 356.8258 | 0.13098 | 0 | 0 | 0.26195 | 357.1109 | 0.1316 | 0 | 0 | 0.26319 | 357.301 | 0.13201 | 0 | 0 | 0.26402 | 357.4911 | 0.13242 | 0 | 0 | 0.26484
2017-12-19 06:00 | 317.2432 | 0.94557 |  | 333.1259 | 0.079572 | 0 | 0 | 0.15914 | 342.4871 | 0.099876 | 0 | 0 | 0.19975 | 350.1462 | 0.11649 | 0 | 0 | 0.23298 | 350.4299 | 0.1171 | 0 | 0 | 0.23421 | 350.619 | 0.11751 | 0 | 0 | 0.23503 | 350.9027 | 0.11813 | 0 | 0 | 0.23626 | 351.1864 | 0.11874 | 0 | 0 | 0.23749 | 351.47 | 0.11936 | 0 | 0 | 0.23872 | 351.8483 | 0.12018 | 0 | 0 | 0.24036 | 352.1319 | 0.1208 | 0 | 0 | 0.24159 | 352.321 | 0.12121 | 0 | 0 | 0.24241 | 352.6047 | 0.12182 | 0 | 0 | 0.24364 | 352.7938 | 0.12223 | 0 | 0 | 0.24446 | 353.0775 | 0.12285 | 0 | 0 | 0.24569 | 353.3612 | 0.12346 | 0 | 0 | 0.24692 | 353.5503 | 0.12387 | 0 | 0 | 0.24774 | 353.834 | 0.12449 | 0 | 0 | 0.24898 | 354.1176 | 0.1251 | 0 | 0 | 0.25021 | 354.2122 | 0.12531 | 0 | 0 | 0.25062 | 354.4959 | 0.12592 | 0 | 0 | 0.25185 | 354.7795 | 0.12654 | 0 | 0 | 0.25308 | 354.9686 | 0.12695 | 0 | 0 | 0.2539 | 355.2523 | 0.12756 | 0 | 0 | 0.25513 | 355.4414 | 0.12797 | 0 | 0 | 0.25595 | 355.6306 | 0.12838 | 0 | 0 | 0.25677
2017-12-19 07:00 | 319.7077 | 0.95292 |  | 335.7138 | 0.085185 | 0 | 0 | 0.17037 | 345.1477 | 0.10565 | 0 | 0 | 0.21129 | 352.8664 | 0.12239 | 0 | 0 | 0.24478 | 353.1523 | 0.12301 | 0 | 0 | 0.24602 | 353.3428 | 0.12342 | 0 | 0 | 0.24684 | 353.6287 | 0.12404 | 0 | 0 | 0.24808 | 353.9146 | 0.12466 | 0 | 0 | 0.24932 | 354.2005 | 0.12528 | 0 | 0 | 0.25056 | 354.5816 | 0.12611 | 0 | 0 | 0.25222 | 354.8675 | 0.12673 | 0 | 0 | 0.25346 | 355.0581 | 0.12714 | 0 | 0 | 0.25429 | 355.344 | 0.12776 | 0 | 0 | 0.25553 | 355.5346 | 0.12818 | 0 | 0 | 0.25635 | 355.8204 | 0.1288 | 0 | 0 | 0.25759 | 356.1063 | 0.12942 | 0 | 0 | 0.25883 | 356.2969 | 0.12983 | 0 | 0 | 0.25966 | 356.5828 | 0.13045 | 0 | 0 | 0.2609 | 356.8687 | 0.13107 | 0 | 0 | 0.26214 | 356.9639 | 0.13128 | 0 | 0 | 0.26255 | 357.2498 | 0.1319 | 0 | 0 | 0.26379 | 357.5357 | 0.13252 | 0 | 0 | 0.26503 | 357.7263 | 0.13293 | 0 | 0 | 0.26586 | 358.0122 | 0.13355 | 0 | 0 | 0.2671 | 358.2027 | 0.13396 | 0 | 0 | 0.26793 | 358.3933 | 0.13438 | 0 | 0 | 0.26875
2017-12-19 08:00 | 310.0509 | 0.92414 |  | 325.5736 | 0.063191 | 0 | 0 | 0.12638 | 334.7225 | 0.083035 | 0 | 0 | 0.16607 | 342.208 | 0.099271 | 0 | 0 | 0.19854 | 342.4853 | 0.099872 | 0 | 0 | 0.19974 | 342.6701 | 0.10027 | 0 | 0 | 0.20055 | 342.9473 | 0.10087 | 0 | 0 | 0.20175 | 343.2246 | 0.10148 | 0 | 0 | 0.20295 | 343.5018 | 0.10208 | 0 | 0 | 0.20415 | 343.8715 | 0.10288 | 0 | 0 | 0.20576 | 344.1487 | 0.10348 | 0 | 0 | 0.20696 | 344.3335 | 0.10388 | 0 | 0 | 0.20776 | 344.6108 | 0.10448 | 0 | 0 | 0.20896 | 344.7956 | 0.10488 | 0 | 0 | 0.20977 | 345.0729 | 0.10548 | 0 | 0 | 0.21097 | 345.3501 | 0.10609 | 0 | 0 | 0.21217 | 345.5349 | 0.10649 | 0 | 0 | 0.21297 | 345.8122 | 0.10709 | 0 | 0 | 0.21418 | 346.0894 | 0.10769 | 0 | 0 | 0.21538 | 346.1818 | 0.10789 | 0 | 0 | 0.21578 | 346.4591 | 0.10849 | 0 | 0 | 0.21698 | 346.7363 | 0.10909 | 0 | 0 | 0.21819 | 346.9211 | 0.10949 | 0 | 0 | 0.21899 | 347.1984 | 0.11009 | 0 | 0 | 0.22019 | 347.3832 | 0.1105 | 0 | 0 | 0.22099 | 347.568 | 0.1109 | 0 | 0 | 0.22179
2017-12-19 09:00 | 299.0518 | 0.89135 |  | 314.0237 | 0.038139 | 0 | 0 | 0.076278 | 322.8481 | 0.057279 | 0 | 0 | 0.11456 | 330.0681 | 0.072939 | 0 | 0 | 0.14588 | 330.3355 | 0.073519 | 0 | 0 | 0.14704 | 330.5138 | 0.073906 | 0 | 0 | 0.14781 | 330.7812 | 0.074486 | 0 | 0 | 0.14897 | 331.0486 | 0.075066 | 0 | 0 | 0.15013 | 331.316 | 0.075646 | 0 | 0 | 0.15129 | 331.6725 | 0.076419 | 0 | 0 | 0.15284 | 331.9399 | 0.076999 | 0 | 0 | 0.154 | 332.1182 | 0.077386 | 0 | 0 | 0.15477 | 332.3856 | 0.077966 | 0 | 0 | 0.15593 | 332.5639 | 0.078353 | 0 | 0 | 0.15671 | 332.8313 | 0.078933 | 0 | 0 | 0.15787 | 333.0987 | 0.079513 | 0 | 0 | 0.15903 | 333.277 | 0.079899 | 0 | 0 | 0.1598 | 333.5444 | 0.080479 | 0 | 0 | 0.16096 | 333.8118 | 0.081059 | 0 | 0 | 0.16212 | 333.9009 | 0.081253 | 0 | 0 | 0.16251 | 334.1683 | 0.081833 | 0 | 0 | 0.16367 | 334.4357 | 0.082413 | 0 | 0 | 0.16483 | 334.614 | 0.082799 | 0 | 0 | 0.1656 | 334.8814 | 0.083379 | 0 | 0 | 0.16676 | 335.0597 | 0.083766 | 0 | 0 | 0.16753 | 335.2379 | 0.084153 | 0 | 0 | 0.16831
2017-12-19 10:00 | 300.6977 | 0.89626 |  | 315.752 | 0.041888 | 0 | 0 | 0.083776 | 324.625 | 0.061133 | 0 | 0 | 0.12227 | 331.8847 | 0.07688 | 0 | 0 | 0.15376 | 332.1536 | 0.077463 | 0 | 0 | 0.15493 | 332.3328 | 0.077852 | 0 | 0 | 0.1557 | 332.6017 | 0.078435 | 0 | 0 | 0.15687 | 332.8706 | 0.079018 | 0 | 0 | 0.15804 | 333.1395 | 0.079601 | 0 | 0 | 0.1592 | 333.498 | 0.080379 | 0 | 0 | 0.16076 | 333.7669 | 0.080962 | 0 | 0 | 0.16192 | 333.9461 | 0.081351 | 0 | 0 | 0.1627 | 334.215 | 0.081934 | 0 | 0 | 0.16387 | 334.3942 | 0.082323 | 0 | 0 | 0.16465 | 334.6631 | 0.082906 | 0 | 0 | 0.16581 | 334.932 | 0.083489 | 0 | 0 | 0.16698 | 335.1112 | 0.083878 | 0 | 0 | 0.16776 | 335.3801 | 0.084461 | 0 | 0 | 0.16892 | 335.649 | 0.085044 | 0 | 0 | 0.17009 | 335.7386 | 0.085239 | 0 | 0 | 0.17048 | 336.0075 | 0.085822 | 0 | 0 | 0.17164 | 336.2764 | 0.086405 | 0 | 0 | 0.17281 | 336.4556 | 0.086794 | 0 | 0 | 0.17359 | 336.7245 | 0.087377 | 0 | 0 | 0.17475 | 336.9038 | 0.087766 | 0 | 0 | 0.17553 | 337.083 | 0.088155 | 0 | 0 | 0.17631
2017-12-19 11:00 | 291.0125 | 0.86739 |  | 305.582 | 0.019829 | 0 | 0 | 0.039658 | 314.1692 | 0.038455 | 0 | 0 | 0.076909 | 321.195 | 0.053694 | 0 | 0 | 0.10739 | 321.4553 | 0.054258 | 0 | 0 | 0.10852 | 321.6287 | 0.054634 | 0 | 0 | 0.10927 | 321.889 | 0.055199 | 0 | 0 | 0.1104 | 322.1492 | 0.055763 | 0 | 0 | 0.11153 | 322.4094 | 0.056328 | 0 | 0 | 0.11266 | 322.7563 | 0.05708 | 0 | 0 | 0.11416 | 323.0166 | 0.057645 | 0 | 0 | 0.11529 | 323.19 | 0.058021 | 0 | 0 | 0.11604 | 323.4503 | 0.058585 | 0 | 0 | 0.11717 | 323.6237 | 0.058962 | 0 | 0 | 0.11792 | 323.884 | 0.059526 | 0 | 0 | 0.11905 | 324.1442 | 0.06009 | 0 | 0 | 0.12018 | 324.3177 | 0.060467 | 0 | 0 | 0.12093 | 324.5779 | 0.061031 | 0 | 0 | 0.12206 | 324.8381 | 0.061595 | 0 | 0 | 0.12319 | 324.9248 | 0.061784 | 0 | 0 | 0.12357 | 325.185 | 0.062348 | 0 | 0 | 0.1247 | 325.4453 | 0.062912 | 0 | 0 | 0.12582 | 325.6187 | 0.063289 | 0 | 0 | 0.12658 | 325.879 | 0.063853 | 0 | 0 | 0.12771 | 326.0524 | 0.064229 | 0 | 0 | 0.12846 | 326.2259 | 0.064606 | 0 | 0 | 0.12921
2017-12-19 12:00 | 290.4729 | 0.86578 |  | 305.0154 | 0.0186 | 0 | 0 | 0.0372 | 313.5866 | 0.037191 | 0 | 0 | 0.074382 | 320.5995 | 0.052402 | 0 | 0 | 0.1048 | 320.8592 | 0.052965 | 0 | 0 | 0.10593 | 321.0323 | 0.053341 | 0 | 0 | 0.10668 | 321.2921 | 0.053904 | 0 | 0 | 0.10781 | 321.5518 | 0.054468 | 0 | 0 | 0.10894 | 321.8116 | 0.055031 | 0 | 0 | 0.11006 | 322.1579 | 0.055782 | 0 | 0 | 0.11156 | 322.4176 | 0.056345 | 0 | 0 | 0.11269 | 322.5908 | 0.056721 | 0 | 0 | 0.11344 | 322.8505 | 0.057284 | 0 | 0 | 0.11457 | 323.0236 | 0.05766 | 0 | 0 | 0.11532 | 323.2834 | 0.058223 | 0 | 0 | 0.11645 | 323.5431 | 0.058787 | 0 | 0 | 0.11757 | 323.7163 | 0.059162 | 0 | 0 | 0.11832 | 323.976 | 0.059726 | 0 | 0 | 0.11945 | 324.2357 | 0.060289 | 0 | 0 | 0.12058 | 324.3223 | 0.060477 | 0 | 0 | 0.12095 | 324.5821 | 0.06104 | 0 | 0 | 0.12208 | 324.8418 | 0.061603 | 0 | 0 | 0.12321 | 325.015 | 0.061979 | 0 | 0 | 0.12396 | 325.2747 | 0.062542 | 0 | 0 | 0.12508 | 325.4478 | 0.062918 | 0 | 0 | 0.12584 | 325.621 | 0.063294 | 0 | 0 | 0.12659
2017-12-19 13:00 | 297.4113 | 0.88646 |  | 312.3012 | 0.034403 | 0 | 0 | 0.068806 | 321.0771 | 0.053438 | 0 | 0 | 0.10688 | 328.2575 | 0.069012 | 0 | 0 | 0.13802 | 328.5234 | 0.069589 | 0 | 0 | 0.13918 | 328.7007 | 0.069974 | 0 | 0 | 0.13995 | 328.9667 | 0.07055 | 0 | 0 | 0.1411 | 329.2326 | 0.071127 | 0 | 0 | 0.14225 | 329.4986 | 0.071704 | 0 | 0 | 0.14341 | 329.8531 | 0.072473 | 0 | 0 | 0.14495 | 330.1191 | 0.07305 | 0 | 0 | 0.1461 | 330.2964 | 0.073434 | 0 | 0 | 0.14687 | 330.5623 | 0.074011 | 0 | 0 | 0.14802 | 330.7396 | 0.074396 | 0 | 0 | 0.14879 | 331.0055 | 0.074973 | 0 | 0 | 0.14995 | 331.2715 | 0.075549 | 0 | 0 | 0.1511 | 331.4488 | 0.075934 | 0 | 0 | 0.15187 | 331.7147 | 0.076511 | 0 | 0 | 0.15302 | 331.9806 | 0.077088 | 0 | 0 | 0.15418 | 332.0693 | 0.07728 | 0 | 0 | 0.15456 | 332.3352 | 0.077857 | 0 | 0 | 0.15571 | 332.6012 | 0.078434 | 0 | 0 | 0.15687 | 332.7785 | 0.078818 | 0 | 0 | 0.15764 | 333.0444 | 0.079395 | 0 | 0 | 0.15879 | 333.2217 | 0.07978 | 0 | 0 | 0.15956 | 333.399 | 0.080164 | 0 | 0 | 0.16033
2017-12-19 14:00 | 299.5847 | 0.89294 |  | 314.5833 | 0.039353 | 0 | 0 | 0.078706 | 323.4234 | 0.058527 | 0 | 0 | 0.11705 | 330.6562 | 0.074215 | 0 | 0 | 0.14843 | 330.9241 | 0.074796 | 0 | 0 | 0.14959 | 331.1027 | 0.075183 | 0 | 0 | 0.15037 | 331.3706 | 0.075764 | 0 | 0 | 0.15153 | 331.6385 | 0.076345 | 0 | 0 | 0.15269 | 331.9064 | 0.076927 | 0 | 0 | 0.15385 | 332.2635 | 0.077701 | 0 | 0 | 0.1554 | 332.5314 | 0.078282 | 0 | 0 | 0.15656 | 332.71 | 0.07867 | 0 | 0 | 0.15734 | 332.9779 | 0.079251 | 0 | 0 | 0.1585 | 333.1565 | 0.079638 | 0 | 0 | 0.15928 | 333.4244 | 0.080219 | 0 | 0 | 0.16044 | 333.6922 | 0.0808 | 0 | 0 | 0.1616 | 333.8708 | 0.081187 | 0 | 0 | 0.16237 | 334.1387 | 0.081768 | 0 | 0 | 0.16354 | 334.4066 | 0.08235 | 0 | 0 | 0.1647 | 334.4959 | 0.082543 | 0 | 0 | 0.16509 | 334.7638 | 0.083124 | 0 | 0 | 0.16625 | 335.0316 | 0.083705 | 0 | 0 | 0.16741 | 335.2102 | 0.084093 | 0 | 0 | 0.16819 | 335.4781 | 0.084674 | 0 | 0 | 0.16935 | 335.6567 | 0.085061 | 0 | 0 | 0.17012 | 335.8353 | 0.085448 | 0 | 0 | 0.1709
2017-12-19 15:00 | 306.375 | 0.91318 |  | 321.7136 | 0.054818 | 0 | 0 | 0.10964 | 330.7541 | 0.074427 | 0 | 0 | 0.14885 | 338.1509 | 0.090471 | 0 | 0 | 0.18094 | 338.4248 | 0.091065 | 0 | 0 | 0.18213 | 338.6075 | 0.091461 | 0 | 0 | 0.18292 | 338.8814 | 0.092055 | 0 | 0 | 0.18411 | 339.1554 | 0.09265 | 0 | 0 | 0.1853 | 339.4293 | 0.093244 | 0 | 0 | 0.18649 | 339.7946 | 0.094036 | 0 | 0 | 0.18807 | 340.0686 | 0.09463 | 0 | 0 | 0.18926 | 340.2512 | 0.095026 | 0 | 0 | 0.19005 | 340.5251 | 0.095621 | 0 | 0 | 0.19124 | 340.7078 | 0.096017 | 0 | 0 | 0.19203 | 340.9817 | 0.096611 | 0 | 0 | 0.19322 | 341.2557 | 0.097205 | 0 | 0 | 0.19441 | 341.4383 | 0.097601 | 0 | 0 | 0.1952 | 341.7123 | 0.098196 | 0 | 0 | 0.19639 | 341.9862 | 0.09879 | 0 | 0 | 0.19758 | 342.0776 | 0.098988 | 0 | 0 | 0.19798 | 342.3515 | 0.099582 | 0 | 0 | 0.19916 | 342.6255 | 0.10018 | 0 | 0 | 0.20035 | 342.8081 | 0.10057 | 0 | 0 | 0.20114 | 343.0821 | 0.10117 | 0 | 0 | 0.20233 | 343.2647 | 0.10156 | 0 | 0 | 0.20313 | 343.4473 | 0.10196 | 0 | 0 | 0.20392
2017-12-19 16:00 | 305.8256 | 0.91154 |  | 321.1366 | 0.053567 | 0 | 0 | 0.10713 | 330.1609 | 0.073141 | 0 | 0 | 0.14628 | 337.5444 | 0.089155 | 0 | 0 | 0.17831 | 337.8179 | 0.089749 | 0 | 0 | 0.1795 | 338.0002 | 0.090144 | 0 | 0 | 0.18029 | 338.2736 | 0.090737 | 0 | 0 | 0.18147 | 338.5471 | 0.09133 | 0 | 0 | 0.18266 | 338.8206 | 0.091923 | 0 | 0 | 0.18385 | 339.1852 | 0.092714 | 0 | 0 | 0.18543 | 339.4587 | 0.093307 | 0 | 0 | 0.18661 | 339.641 | 0.093703 | 0 | 0 | 0.18741 | 339.9144 | 0.094296 | 0 | 0 | 0.18859 | 340.0967 | 0.094691 | 0 | 0 | 0.18938 | 340.3702 | 0.095285 | 0 | 0 | 0.19057 | 340.6437 | 0.095878 | 0 | 0 | 0.19176 | 340.826 | 0.096273 | 0 | 0 | 0.19255 | 341.0994 | 0.096866 | 0 | 0 | 0.19373 | 341.3729 | 0.097459 | 0 | 0 | 0.19492 | 341.464 | 0.097657 | 0 | 0 | 0.19531 | 341.7375 | 0.09825 | 0 | 0 | 0.1965 | 342.011 | 0.098843 | 0 | 0 | 0.19769 | 342.1933 | 0.099239 | 0 | 0 | 0.19848 | 342.4667 | 0.099832 | 0 | 0 | 0.19966 | 342.6491 | 0.10023 | 0 | 0 | 0.20045 | 342.8314 | 0.10062 | 0 | 0 | 0.20125
2017-12-19 17:00 | 302.1991 | 0.90073 |  | 317.3286 | 0.045307 | 0 | 0 | 0.090615 | 326.2459 | 0.064649 | 0 | 0 | 0.1293 | 333.5419 | 0.080474 | 0 | 0 | 0.16095 | 333.8121 | 0.08106 | 0 | 0 | 0.16212 | 333.9922 | 0.081451 | 0 | 0 | 0.1629 | 334.2624 | 0.082037 | 0 | 0 | 0.16407 | 334.5327 | 0.082623 | 0 | 0 | 0.16525 | 334.8029 | 0.083209 | 0 | 0 | 0.16642 | 335.1632 | 0.083991 | 0 | 0 | 0.16798 | 335.4334 | 0.084577 | 0 | 0 | 0.16915 | 335.6135 | 0.084967 | 0 | 0 | 0.16993 | 335.8838 | 0.085554 | 0 | 0 | 0.17111 | 336.0639 | 0.085944 | 0 | 0 | 0.17189 | 336.3341 | 0.08653 | 0 | 0 | 0.17306 | 336.6044 | 0.087116 | 0 | 0 | 0.17423 | 336.7845 | 0.087507 | 0 | 0 | 0.17501 | 337.0547 | 0.088093 | 0 | 0 | 0.17619 | 337.3249 | 0.088679 | 0 | 0 | 0.17736 | 337.415 | 0.088875 | 0 | 0 | 0.17775 | 337.6852 | 0.089461 | 0 | 0 | 0.17892 | 337.9555 | 0.090047 | 0 | 0 | 0.18009 | 338.1356 | 0.090438 | 0 | 0 | 0.18088 | 338.4058 | 0.091024 | 0 | 0 | 0.18205 | 338.586 | 0.091415 | 0 | 0 | 0.18283 | 338.7661 | 0.091805 | 0 | 0 | 0.18361
2017-12-19 18:00 | 311.7986 | 0.92935 |  | 327.4087 | 0.067171 | 0 | 0 | 0.13434 | 336.6092 | 0.087127 | 0 | 0 | 0.17425 | 344.1369 | 0.10345 | 0 | 0 | 0.20691 | 344.4157 | 0.10406 | 0 | 0 | 0.20812 | 344.6016 | 0.10446 | 0 | 0 | 0.20892 | 344.8804 | 0.10507 | 0 | 0 | 0.21013 | 345.1592 | 0.10567 | 0 | 0 | 0.21134 | 345.438 | 0.10628 | 0 | 0 | 0.21255 | 345.8097 | 0.10708 | 0 | 0 | 0.21417 | 346.0885 | 0.10769 | 0 | 0 | 0.21538 | 346.2744 | 0.10809 | 0 | 0 | 0.21618 | 346.5532 | 0.1087 | 0 | 0 | 0.21739 | 346.7391 | 0.1091 | 0 | 0 | 0.2182 | 347.0179 | 0.1097 | 0 | 0 | 0.21941 | 347.2967 | 0.11031 | 0 | 0 | 0.22062 | 347.4825 | 0.11071 | 0 | 0 | 0.22142 | 347.7614 | 0.11132 | 0 | 0 | 0.22263 | 348.0402 | 0.11192 | 0 | 0 | 0.22384 | 348.1331 | 0.11212 | 0 | 0 | 0.22424 | 348.4119 | 0.11273 | 0 | 0 | 0.22545 | 348.6907 | 0.11333 | 0 | 0 | 0.22666 | 348.8766 | 0.11373 | 0 | 0 | 0.22747 | 349.1554 | 0.11434 | 0 | 0 | 0.22868 | 349.3412 | 0.11474 | 0 | 0 | 0.22949 | 349.5271 | 0.11515 | 0 | 0 | 0.23029
2017-12-19 19:00 | 316.711 | 0.94399 |  | 332.5671 | 0.07836 | 0 | 0 | 0.15672 | 341.9126 | 0.09863 | 0 | 0 | 0.19726 | 349.5589 | 0.11521 | 0 | 0 | 0.23043 | 349.8421 | 0.11583 | 0 | 0 | 0.23166 | 350.0309 | 0.11624 | 0 | 0 | 0.23248 | 350.3141 | 0.11685 | 0 | 0 | 0.23371 | 350.5973 | 0.11747 | 0 | 0 | 0.23493 | 350.8805 | 0.11808 | 0 | 0 | 0.23616 | 351.2581 | 0.1189 | 0 | 0 | 0.2378 | 351.5413 | 0.11951 | 0 | 0 | 0.23903 | 351.7301 | 0.11992 | 0 | 0 | 0.23985 | 352.0132 | 0.12054 | 0 | 0 | 0.24108 | 352.202 | 0.12095 | 0 | 0 | 0.2419 | 352.4852 | 0.12156 | 0 | 0 | 0.24312 | 352.7684 | 0.12218 | 0 | 0 | 0.24435 | 352.9572 | 0.12259 | 0 | 0 | 0.24517 | 353.2404 | 0.1232 | 0 | 0 | 0.2464 | 353.5236 | 0.12381 | 0 | 0 | 0.24763 | 353.618 | 0.12402 | 0 | 0 | 0.24804 | 353.9012 | 0.12463 | 0 | 0 | 0.24927 | 354.1844 | 0.12525 | 0 | 0 | 0.2505 | 354.3732 | 0.12566 | 0 | 0 | 0.25131 | 354.6564 | 0.12627 | 0 | 0 | 0.25254 | 354.8452 | 0.12668 | 0 | 0 | 0.25336 | 355.034 | 0.12709 | 0 | 0 | 0.25418
2017-12-19 20:00 | 305.7491 | 0.91132 |  | 321.0564 | 0.053393 | 0 | 0 | 0.10679 | 330.0784 | 0.072962 | 0 | 0 | 0.14592 | 337.46 | 0.088972 | 0 | 0 | 0.17794 | 337.7334 | 0.089565 | 0 | 0 | 0.17913 | 337.9157 | 0.089961 | 0 | 0 | 0.17992 | 338.1891 | 0.090554 | 0 | 0 | 0.18111 | 338.4625 | 0.091147 | 0 | 0 | 0.18229 | 338.7359 | 0.09174 | 0 | 0 | 0.18348 | 339.1004 | 0.09253 | 0 | 0 | 0.18506 | 339.3738 | 0.093123 | 0 | 0 | 0.18625 | 339.5561 | 0.093519 | 0 | 0 | 0.18704 | 339.8295 | 0.094112 | 0 | 0 | 0.18822 | 340.0117 | 0.094507 | 0 | 0 | 0.18901 | 340.2851 | 0.0951 | 0 | 0 | 0.1902 | 340.5585 | 0.095693 | 0 | 0 | 0.19139 | 340.7408 | 0.096088 | 0 | 0 | 0.19218 | 341.0142 | 0.096681 | 0 | 0 | 0.19336 | 341.2876 | 0.097274 | 0 | 0 | 0.19455 | 341.3787 | 0.097472 | 0 | 0 | 0.19494 | 341.6521 | 0.098065 | 0 | 0 | 0.19613 | 341.9255 | 0.098658 | 0 | 0 | 0.19732 | 342.1077 | 0.099053 | 0 | 0 | 0.19811 | 342.3811 | 0.099646 | 0 | 0 | 0.19929 | 342.5634 | 0.10004 | 0 | 0 | 0.20008 | 342.7457 | 0.10044 | 0 | 0 | 0.20087
2017-12-19 21:00 | 311.8431 | 0.92948 |  | 327.4554 | 0.067272 | 0 | 0 | 0.13454 | 336.6572 | 0.087231 | 0 | 0 | 0.17446 | 344.186 | 0.10356 | 0 | 0 | 0.20712 | 344.4649 | 0.10417 | 0 | 0 | 0.20833 | 344.6508 | 0.10457 | 0 | 0 | 0.20914 | 344.9296 | 0.10517 | 0 | 0 | 0.21035 | 345.2084 | 0.10578 | 0 | 0 | 0.21156 | 345.4873 | 0.10638 | 0 | 0 | 0.21277 | 345.8591 | 0.10719 | 0 | 0 | 0.21438 | 346.1379 | 0.10779 | 0 | 0 | 0.21559 | 346.3238 | 0.1082 | 0 | 0 | 0.2164 | 346.6027 | 0.1088 | 0 | 0 | 0.21761 | 346.7886 | 0.10921 | 0 | 0 | 0.21841 | 347.0674 | 0.10981 | 0 | 0 | 0.21962 | 347.3462 | 0.11042 | 0 | 0 | 0.22083 | 347.5321 | 0.11082 | 0 | 0 | 0.22164 | 347.811 | 0.11142 | 0 | 0 | 0.22285 | 348.0898 | 0.11203 | 0 | 0 | 0.22406 | 348.1828 | 0.11223 | 0 | 0 | 0.22446 | 348.4616 | 0.11283 | 0 | 0 | 0.22567 | 348.7405 | 0.11344 | 0 | 0 | 0.22688 | 348.9264 | 0.11384 | 0 | 0 | 0.22769 | 349.2052 | 0.11445 | 0 | 0 | 0.2289 | 349.3911 | 0.11485 | 0 | 0 | 0.2297 | 349.577 | 0.11525 | 0 | 0 | 0.23051
2017-12-19 22:00 | 304.3571 | 0.90717 |  | 319.5947 | 0.050223 | 0 | 0 | 0.10045 | 328.5756 | 0.069702 | 0 | 0 | 0.1394 | 335.9237 | 0.08564 | 0 | 0 | 0.17128 | 336.1958 | 0.08623 | 0 | 0 | 0.17246 | 336.3773 | 0.086624 | 0 | 0 | 0.17325 | 336.6494 | 0.087214 | 0 | 0 | 0.17443 | 336.9216 | 0.087805 | 0 | 0 | 0.17561 | 337.1937 | 0.088395 | 0 | 0 | 0.17679 | 337.5566 | 0.089182 | 0 | 0 | 0.17836 | 337.8287 | 0.089772 | 0 | 0 | 0.17954 | 338.0102 | 0.090166 | 0 | 0 | 0.18033 | 338.2823 | 0.090756 | 0 | 0 | 0.18151 | 338.4637 | 0.09115 | 0 | 0 | 0.1823 | 338.7359 | 0.09174 | 0 | 0 | 0.18348 | 339.008 | 0.09233 | 0 | 0 | 0.18466 | 339.1895 | 0.092724 | 0 | 0 | 0.18545 | 339.4616 | 0.093314 | 0 | 0 | 0.18663 | 339.7338 | 0.093904 | 0 | 0 | 0.18781 | 339.8245 | 0.094101 | 0 | 0 | 0.1882 | 340.0966 | 0.094691 | 0 | 0 | 0.18938 | 340.3688 | 0.095282 | 0 | 0 | 0.19056 | 340.5502 | 0.095675 | 0 | 0 | 0.19135 | 340.8224 | 0.096265 | 0 | 0 | 0.19253 | 341.0038 | 0.096659 | 0 | 0 | 0.19332 | 341.1852 | 0.097052 | 0 | 0 | 0.1941
2017-12-19 23:00 | 312.3076 | 0.93086 |  | 327.9432 | 0.06833 | 0 | 0 | 0.13666 | 337.1588 | 0.088319 | 0 | 0 | 0.17664 | 344.6988 | 0.10467 | 0 | 0 | 0.20935 | 344.978 | 0.10528 | 0 | 0 | 0.21056 | 345.1642 | 0.10568 | 0 | 0 | 0.21137 | 345.4435 | 0.10629 | 0 | 0 | 0.21258 | 345.7227 | 0.10689 | 0 | 0 | 0.21379 | 346.002 | 0.1075 | 0 | 0 | 0.215 | 346.3743 | 0.10831 | 0 | 0 | 0.21662 | 346.6536 | 0.10891 | 0 | 0 | 0.21783 | 346.8397 | 0.10932 | 0 | 0 | 0.21863 | 347.119 | 0.10992 | 0 | 0 | 0.21985 | 347.3052 | 0.11033 | 0 | 0 | 0.22065 | 347.5844 | 0.11093 | 0 | 0 | 0.22186 | 347.8637 | 0.11154 | 0 | 0 | 0.22308 | 348.0499 | 0.11194 | 0 | 0 | 0.22388 | 348.3291 | 0.11255 | 0 | 0 | 0.2251 | 348.6084 | 0.11315 | 0 | 0 | 0.22631 | 348.7015 | 0.11336 | 0 | 0 | 0.22671 | 348.9807 | 0.11396 | 0 | 0 | 0.22792 | 349.26 | 0.11457 | 0 | 0 | 0.22913 | 349.4462 | 0.11497 | 0 | 0 | 0.22994 | 349.7254 | 0.11558 | 0 | 0 | 0.23115 | 349.9116 | 0.11598 | 0 | 0 | 0.23196 | 350.0978 | 0.11638 | 0 | 0 | 0.23277
2017-12-20 | 315.7537 | 0.94113 |  | 331.5618 | 0.076179 | 0 | 0 | 0.15236 | 340.879 | 0.096388 | 0 | 0 | 0.19278 | 348.5022 | 0.11292 | 0 | 0 | 0.22585 | 348.7846 | 0.11354 | 0 | 0 | 0.22707 | 348.9728 | 0.11394 | 0 | 0 | 0.22789 | 349.2551 | 0.11456 | 0 | 0 | 0.22911 | 349.5375 | 0.11517 | 0 | 0 | 0.23034 | 349.8198 | 0.11578 | 0 | 0 | 0.23156 | 350.1963 | 0.1166 | 0 | 0 | 0.23319 | 350.4786 | 0.11721 | 0 | 0 | 0.23442 | 350.6668 | 0.11762 | 0 | 0 | 0.23524 | 350.9492 | 0.11823 | 0 | 0 | 0.23646 | 351.1374 | 0.11864 | 0 | 0 | 0.23728 | 351.4197 | 0.11925 | 0 | 0 | 0.2385 | 351.7021 | 0.11986 | 0 | 0 | 0.23973 | 351.8903 | 0.12027 | 0 | 0 | 0.24054 | 352.1727 | 0.12088 | 0 | 0 | 0.24177 | 352.455 | 0.1215 | 0 | 0 | 0.24299 | 352.5491 | 0.1217 | 0 | 0 | 0.2434 | 352.8314 | 0.12231 | 0 | 0 | 0.24463 | 353.1138 | 0.12293 | 0 | 0 | 0.24585 | 353.302 | 0.12333 | 0 | 0 | 0.24667 | 353.5844 | 0.12395 | 0 | 0 | 0.24789 | 353.7726 | 0.12435 | 0 | 0 | 0.24871 | 353.9608 | 0.12476 | 0 | 0 | 0.24953
2017-12-20 01:00 | 308.4998 | 0.91951 |  | 323.9448 | 0.059658 | 0 | 0 | 0.11932 | 333.0479 | 0.079403 | 0 | 0 | 0.15881 | 340.496 | 0.095557 | 0 | 0 | 0.19111 | 340.7719 | 0.096156 | 0 | 0 | 0.19231 | 340.9558 | 0.096555 | 0 | 0 | 0.19311 | 341.2316 | 0.097153 | 0 | 0 | 0.19431 | 341.5075 | 0.097751 | 0 | 0 | 0.1955 | 341.7833 | 0.09835 | 0 | 0 | 0.1967 | 342.1511 | 0.099147 | 0 | 0 | 0.19829 | 342.427 | 0.099746 | 0 | 0 | 0.19949 | 342.6109 | 0.10014 | 0 | 0 | 0.20029 | 342.8867 | 0.10074 | 0 | 0 | 0.20149 | 343.0706 | 0.10114 | 0 | 0 | 0.20228 | 343.3465 | 0.10174 | 0 | 0 | 0.20348 | 343.6223 | 0.10234 | 0 | 0 | 0.20468 | 343.8063 | 0.10274 | 0 | 0 | 0.20547 | 344.0821 | 0.10334 | 0 | 0 | 0.20667 | 344.358 | 0.10393 | 0 | 0 | 0.20787 | 344.4499 | 0.10413 | 0 | 0 | 0.20827 | 344.7258 | 0.10473 | 0 | 0 | 0.20946 | 345.0016 | 0.10533 | 0 | 0 | 0.21066 | 345.1855 | 0.10573 | 0 | 0 | 0.21146 | 345.4614 | 0.10633 | 0 | 0 | 0.21265 | 345.6453 | 0.10673 | 0 | 0 | 0.21345 | 345.8292 | 0.10713 | 0 | 0 | 0.21425
2017-12-20 02:00 | 313.9909 | 0.93588 |  | 329.7107 | 0.072164 | 0 | 0 | 0.14433 | 338.9759 | 0.09226 | 0 | 0 | 0.18452 | 346.5566 | 0.1087 | 0 | 0 | 0.21741 | 346.8373 | 0.10931 | 0 | 0 | 0.21862 | 347.0245 | 0.10972 | 0 | 0 | 0.21944 | 347.3053 | 0.11033 | 0 | 0 | 0.22065 | 347.586 | 0.11094 | 0 | 0 | 0.22187 | 347.8668 | 0.11154 | 0 | 0 | 0.22309 | 348.2412 | 0.11236 | 0 | 0 | 0.22471 | 348.5219 | 0.11297 | 0 | 0 | 0.22593 | 348.7091 | 0.11337 | 0 | 0 | 0.22674 | 348.9899 | 0.11398 | 0 | 0 | 0.22796 | 349.177 | 0.11439 | 0 | 0 | 0.22877 | 349.4578 | 0.115 | 0 | 0 | 0.22999 | 349.7386 | 0.1156 | 0 | 0 | 0.23121 | 349.9257 | 0.11601 | 0 | 0 | 0.23202 | 350.2065 | 0.11662 | 0 | 0 | 0.23324 | 350.4873 | 0.11723 | 0 | 0 | 0.23446 | 350.5809 | 0.11743 | 0 | 0 | 0.23486 | 350.8616 | 0.11804 | 0 | 0 | 0.23608 | 351.1424 | 0.11865 | 0 | 0 | 0.2373 | 351.3296 | 0.11906 | 0 | 0 | 0.23811 | 351.6103 | 0.11966 | 0 | 0 | 0.23933 | 351.7975 | 0.12007 | 0 | 0 | 0.24014 | 351.9847 | 0.12048 | 0 | 0 | 0.24095
2017-12-20 03:00 | 314.46 | 0.93728 |  | 330.2034 | 0.073233 | 0 | 0 | 0.14647 | 339.4824 | 0.093359 | 0 | 0 | 0.18672 | 347.0744 | 0.10983 | 0 | 0 | 0.21965 | 347.3556 | 0.11044 | 0 | 0 | 0.22087 | 347.543 | 0.11084 | 0 | 0 | 0.22168 | 347.8242 | 0.11145 | 0 | 0 | 0.2229 | 348.1054 | 0.11206 | 0 | 0 | 0.22412 | 348.3866 | 0.11267 | 0 | 0 | 0.22534 | 348.7615 | 0.11349 | 0 | 0 | 0.22697 | 349.0427 | 0.1141 | 0 | 0 | 0.22819 | 349.2301 | 0.1145 | 0 | 0 | 0.229 | 349.5113 | 0.11511 | 0 | 0 | 0.23022 | 349.6988 | 0.11552 | 0 | 0 | 0.23104 | 349.98 | 0.11613 | 0 | 0 | 0.23226 | 350.2611 | 0.11674 | 0 | 0 | 0.23348 | 350.4486 | 0.11714 | 0 | 0 | 0.23429 | 350.7298 | 0.11775 | 0 | 0 | 0.23551 | 351.011 | 0.11836 | 0 | 0 | 0.23673 | 351.1047 | 0.11857 | 0 | 0 | 0.23714 | 351.3859 | 0.11918 | 0 | 0 | 0.23836 | 351.6671 | 0.11979 | 0 | 0 | 0.23957 | 351.8545 | 0.12019 | 0 | 0 | 0.24039 | 352.1357 | 0.1208 | 0 | 0 | 0.24161 | 352.3232 | 0.12121 | 0 | 0 | 0.24242 | 352.5106 | 0.12162 | 0 | 0 | 0.24323
2017-12-20 04:00 | 299.4073 | 0.89241 |  | 314.397 | 0.038949 | 0 | 0 | 0.077898 | 323.2319 | 0.058112 | 0 | 0 | 0.11622 | 330.4605 | 0.07379 | 0 | 0 | 0.14758 | 330.7282 | 0.074371 | 0 | 0 | 0.14874 | 330.9067 | 0.074758 | 0 | 0 | 0.14952 | 331.1744 | 0.075339 | 0 | 0 | 0.15068 | 331.4421 | 0.07592 | 0 | 0 | 0.15184 | 331.7099 | 0.0765 | 0 | 0 | 0.153 | 332.0668 | 0.077275 | 0 | 0 | 0.15455 | 332.3345 | 0.077855 | 0 | 0 | 0.15571 | 332.513 | 0.078242 | 0 | 0 | 0.15648 | 332.7808 | 0.078823 | 0 | 0 | 0.15765 | 332.9592 | 0.07921 | 0 | 0 | 0.15842 | 333.227 | 0.079791 | 0 | 0 | 0.15958 | 333.4947 | 0.080372 | 0 | 0 | 0.16074 | 333.6732 | 0.080759 | 0 | 0 | 0.16152 | 333.9409 | 0.081339 | 0 | 0 | 0.16268 | 334.2086 | 0.08192 | 0 | 0 | 0.16384 | 334.2979 | 0.082114 | 0 | 0 | 0.16423 | 334.5656 | 0.082694 | 0 | 0 | 0.16539 | 334.8333 | 0.083275 | 0 | 0 | 0.16655 | 335.0118 | 0.083662 | 0 | 0 | 0.16732 | 335.2795 | 0.084243 | 0 | 0 | 0.16849 | 335.458 | 0.08463 | 0 | 0 | 0.16926 | 335.6365 | 0.085017 | 0 | 0 | 0.17003
2017-12-20 05:00 | 278.9733 | 0.83151 |  | 292.94 | 0 | 0 | 0 | 0 | 301.1719 | 0.010264 | 0 | 0 | 0.020527 | 307.9071 | 0.024872 | 0 | 0 | 0.049744 | 308.1566 | 0.025413 | 0 | 0 | 0.050826 | 308.3229 | 0.025774 | 0 | 0 | 0.051548 | 308.5723 | 0.026315 | 0 | 0 | 0.05263 | 308.8218 | 0.026856 | 0 | 0 | 0.053712 | 309.0712 | 0.027397 | 0 | 0 | 0.054794 | 309.4038 | 0.028119 | 0 | 0 | 0.056237 | 309.6533 | 0.02866 | 0 | 0 | 0.057319 | 309.8196 | 0.02902 | 0 | 0 | 0.058041 | 310.069 | 0.029561 | 0 | 0 | 0.059123 | 310.2353 | 0.029922 | 0 | 0 | 0.059844 | 310.4848 | 0.030463 | 0 | 0 | 0.060926 | 310.7342 | 0.031004 | 0 | 0 | 0.062008 | 310.9005 | 0.031365 | 0 | 0 | 0.06273 | 311.15 | 0.031906 | 0 | 0 | 0.063812 | 311.3994 | 0.032447 | 0 | 0 | 0.064894 | 311.4826 | 0.032627 | 0 | 0 | 0.065255 | 311.732 | 0.033168 | 0 | 0 | 0.066337 | 311.9815 | 0.03371 | 0 | 0 | 0.067419 | 312.1478 | 0.03407 | 0 | 0 | 0.06814 | 312.3973 | 0.034611 | 0 | 0 | 0.069223 | 312.5636 | 0.034972 | 0 | 0 | 0.069944 | 312.7299 | 0.035333 | 0 | 0 | 0.070665
2017-12-20 06:00 | 272.0811 | 0.81096 |  | 285.7028 | 0 | 0 | 0 | 0 | 293.7313 | 0 | 0 | 0 | 0 | 300.3001 | 0.0083726 | 0 | 0 | 0.016745 | 300.5434 | 0.0089003 | 0 | 0 | 0.017801 | 300.7056 | 0.0092521 | 0 | 0 | 0.018504 | 300.9489 | 0.0097798 | 0 | 0 | 0.01956 | 301.1922 | 0.010307 | 0 | 0 | 0.020615 | 301.4355 | 0.010835 | 0 | 0 | 0.02167 | 301.7599 | 0.011539 | 0 | 0 | 0.023078 | 302.0032 | 0.012066 | 0 | 0 | 0.024133 | 302.1653 | 0.012418 | 0 | 0 | 0.024837 | 302.4086 | 0.012946 | 0 | 0 | 0.025892 | 302.5708 | 0.013298 | 0 | 0 | 0.026596 | 302.8141 | 0.013825 | 0 | 0 | 0.027651 | 303.0574 | 0.014353 | 0 | 0 | 0.028706 | 303.2196 | 0.014705 | 0 | 0 | 0.02941 | 303.4629 | 0.015233 | 0 | 0 | 0.030465 | 303.7062 | 0.01576 | 0 | 0 | 0.031521 | 303.7873 | 0.015936 | 0 | 0 | 0.031872 | 304.0306 | 0.016464 | 0 | 0 | 0.032928 | 304.2739 | 0.016992 | 0 | 0 | 0.033983 | 304.436 | 0.017343 | 0 | 0 | 0.034687 | 304.6793 | 0.017871 | 0 | 0 | 0.035742 | 304.8415 | 0.018223 | 0 | 0 | 0.036446 | 305.0037 | 0.018575 | 0 | 0 | 0.037149
2017-12-20 07:00 | 256.3996 | 0.76422 |  | 269.2362 | 0 | 0 | 0 | 0 | 276.802 | 0 | 0 | 0 | 0 | 282.9922 | 0 | 0 | 0 | 0 | 283.2215 | 0 | 0 | 0 | 0 | 283.3743 | 0 | 0 | 0 | 0 | 283.6036 | 0 | 0 | 0 | 0 | 283.8329 | 0 | 0 | 0 | 0 | 284.0621 | 0 | 0 | 0 | 0 | 284.3678 | 0 | 0 | 0 | 0 | 284.5971 | 0 | 0 | 0 | 0 | 284.7499 | 0 | 0 | 0 | 0 | 284.9792 | 0 | 0 | 0 | 0 | 285.1321 | 0 | 0 | 0 | 0 | 285.3613 | 0 | 0 | 0 | 0 | 285.5906 | 0 | 0 | 0 | 0 | 285.7434 | 0 | 0 | 0 | 0 | 285.9727 | 0 | 0 | 0 | 0 | 286.202 | 0 | 0 | 0 | 0 | 286.2784 | 0 | 0 | 0 | 0 | 286.5077 | 0 | 0 | 0 | 0 | 286.7369 | 0 | 0 | 0 | 0 | 286.8898 | 0 | 0 | 0 | 0 | 287.119 | 0 | 0 | 0 | 0 | 287.2719 | 0 | 0 | 0 | 0 | 287.4247 | 0 | 0 | 0 | 0
2017-12-20 08:00 | 243.8299 | 0.72676 |  | 256.0371 | 0 | 0 | 0 | 0 | 263.2321 | 0 | 0 | 0 | 0 | 269.1188 | 0 | 0 | 0 | 0 | 269.3368 | 0 | 0 | 0 | 0 | 269.4822 | 0 | 0 | 0 | 0 | 269.7002 | 0 | 0 | 0 | 0 | 269.9182 | 0 | 0 | 0 | 0 | 270.1363 | 0 | 0 | 0 | 0 | 270.427 | 0 | 0 | 0 | 0 | 270.645 | 0 | 0 | 0 | 0 | 270.7904 | 0 | 0 | 0 | 0 | 271.0084 | 0 | 0 | 0 | 0 | 271.1537 | 0 | 0 | 0 | 0 | 271.3718 | 0 | 0 | 0 | 0 | 271.5898 | 0 | 0 | 0 | 0 | 271.7351 | 0 | 0 | 0 | 0 | 271.9532 | 0 | 0 | 0 | 0 | 272.1712 | 0 | 0 | 0 | 0 | 272.2439 | 0 | 0 | 0 | 0 | 272.4619 | 0 | 0 | 0 | 0 | 272.6799 | 0 | 0 | 0 | 0 | 272.8253 | 0 | 0 | 0 | 0 | 273.0433 | 0 | 0 | 0 | 0 | 273.1887 | 0 | 0 | 0 | 0 | 273.334 | 0 | 0 | 0 | 0
2017-12-20 09:00 | 237.4309 | 0.70769 |  | 249.3178 | 0 | 0 | 0 | 0 | 256.3239 | 0 | 0 | 0 | 0 | 262.0561 | 0 | 0 | 0 | 0 | 262.2684 | 0 | 0 | 0 | 0 | 262.41 | 0 | 0 | 0 | 0 | 262.6223 | 0 | 0 | 0 | 0 | 262.8346 | 0 | 0 | 0 | 0 | 263.0469 | 0 | 0 | 0 | 0 | 263.3299 | 0 | 0 | 0 | 0 | 263.5423 | 0 | 0 | 0 | 0 | 263.6838 | 0 | 0 | 0 | 0 | 263.8961 | 0 | 0 | 0 | 0 | 264.0376 | 0 | 0 | 0 | 0 | 264.2499 | 0 | 0 | 0 | 0 | 264.4622 | 0 | 0 | 0 | 0 | 264.6038 | 0 | 0 | 0 | 0 | 264.8161 | 0 | 0 | 0 | 0 | 265.0284 | 0 | 0 | 0 | 0 | 265.0992 | 0 | 0 | 0 | 0 | 265.3115 | 0 | 0 | 0 | 0 | 265.5238 | 0 | 0 | 0 | 0 | 265.6653 | 0 | 0 | 0 | 0 | 265.8776 | 0 | 0 | 0 | 0 | 266.0192 | 0 | 0 | 0 | 0 | 266.1607 | 0 | 0 | 0 | 0
2017-12-20 10:00 | 238.8118 | 0.7118 |  | 250.7679 | 0 | 0 | 0 | 0 | 257.8147 | 0 | 0 | 0 | 0 | 263.5803 | 0 | 0 | 0 | 0 | 263.7939 | 0 | 0 | 0 | 0 | 263.9362 | 0 | 0 | 0 | 0 | 264.1498 | 0 | 0 | 0 | 0 | 264.3633 | 0 | 0 | 0 | 0 | 264.5768 | 0 | 0 | 0 | 0 | 264.8616 | 0 | 0 | 0 | 0 | 265.0751 | 0 | 0 | 0 | 0 | 265.2175 | 0 | 0 | 0 | 0 | 265.431 | 0 | 0 | 0 | 0 | 265.5734 | 0 | 0 | 0 | 0 | 265.7869 | 0 | 0 | 0 | 0 | 266.0004 | 0 | 0 | 0 | 0 | 266.1428 | 0 | 0 | 0 | 0 | 266.3563 | 0 | 0 | 0 | 0 | 266.5699 | 0 | 0 | 0 | 0 | 266.6411 | 0 | 0 | 0 | 0 | 266.8546 | 0 | 0 | 0 | 0 | 267.0681 | 0 | 0 | 0 | 0 | 267.2105 | 0 | 0 | 0 | 0 | 267.424 | 0 | 0 | 0 | 0 | 267.5664 | 0 | 0 | 0 | 0 | 267.7088 | 0 | 0 | 0 | 0
2017-12-20 11:00 | 244.7216 | 0.72942 |  | 256.9736 | 0 | 0 | 0 | 0 | 264.1948 | 0 | 0 | 0 | 0 | 270.1031 | 0 | 0 | 0 | 0 | 270.3219 | 0 | 0 | 0 | 0 | 270.4678 | 0 | 0 | 0 | 0 | 270.6866 | 0 | 0 | 0 | 0 | 270.9054 | 0 | 0 | 0 | 0 | 271.1242 | 0 | 0 | 0 | 0 | 271.416 | 0 | 0 | 0 | 0 | 271.6348 | 0 | 0 | 0 | 0 | 271.7807 | 0 | 0 | 0 | 0 | 271.9995 | 0 | 0 | 0 | 0 | 272.1454 | 0 | 0 | 0 | 0 | 272.3642 | 0 | 0 | 0 | 0 | 272.5831 | 0 | 0 | 0 | 0 | 272.729 | 0 | 0 | 0 | 0 | 272.9478 | 0 | 0 | 0 | 0 | 273.1666 | 0 | 0 | 0 | 0 | 273.2395 | 0 | 0 | 0 | 0 | 273.4584 | 0 | 0 | 0 | 0 | 273.6772 | 0 | 0 | 0 | 0 | 273.8231 | 0 | 0 | 0 | 0 | 274.0419 | 0 | 0 | 0 | 0 | 274.1878 | 0 | 0 | 0 | 0 | 274.3337 | 0 | 0 | 0 | 0
2017-12-20 12:00 | 244.1621 | 0.72775 |  | 256.386 | 0 | 0 | 0 | 0 | 263.5908 | 0 | 0 | 0 | 0 | 269.4855 | 0 | 0 | 0 | 0 | 269.7039 | 0 | 0 | 0 | 0 | 269.8494 | 0 | 0 | 0 | 0 | 270.0677 | 0 | 0 | 0 | 0 | 270.2861 | 0 | 0 | 0 | 0 | 270.5044 | 0 | 0 | 0 | 0 | 270.7955 | 0 | 0 | 0 | 0 | 271.0138 | 0 | 0 | 0 | 0 | 271.1594 | 0 | 0 | 0 | 0 | 271.3777 | 0 | 0 | 0 | 0 | 271.5232 | 0 | 0 | 0 | 0 | 271.7416 | 0 | 0 | 0 | 0 | 271.9599 | 0 | 0 | 0 | 0 | 272.1054 | 0 | 0 | 0 | 0 | 272.3237 | 0 | 0 | 0 | 0 | 272.5421 | 0 | 0 | 0 | 0 | 272.6148 | 0 | 0 | 0 | 0 | 272.8332 | 0 | 0 | 0 | 0 | 273.0515 | 0 | 0 | 0 | 0 | 273.197 | 0 | 0 | 0 | 0 | 273.4154 | 0 | 0 | 0 | 0 | 273.5609 | 0 | 0 | 0 | 0 | 273.7065 | 0 | 0 | 0 | 0
2017-12-20 13:00 | 241.5615 | 0.72 |  | 253.6552 | 0 | 0 | 0 | 0 | 260.7832 | 0 | 0 | 0 | 0 | 266.6151 | 0 | 0 | 0 | 0 | 266.8311 | 0 | 0 | 0 | 0 | 266.9751 | 0 | 0 | 0 | 0 | 267.1911 | 0 | 0 | 0 | 0 | 267.4071 | 0 | 0 | 0 | 0 | 267.6231 | 0 | 0 | 0 | 0 | 267.9111 | 0 | 0 | 0 | 0 | 268.1271 | 0 | 0 | 0 | 0 | 268.2711 | 0 | 0 | 0 | 0 | 268.4871 | 0 | 0 | 0 | 0 | 268.6311 | 0 | 0 | 0 | 0 | 268.8471 | 0 | 0 | 0 | 0 | 269.0631 | 0 | 0 | 0 | 0 | 269.2071 | 0 | 0 | 0 | 0 | 269.4231 | 0 | 0 | 0 | 0 | 269.6391 | 0 | 0 | 0 | 0 | 269.7111 | 0 | 0 | 0 | 0 | 269.9271 | 0 | 0 | 0 | 0 | 270.1431 | 0 | 0 | 0 | 0 | 270.2871 | 0 | 0 | 0 | 0 | 270.5031 | 0 | 0 | 0 | 0 | 270.6471 | 0 | 0 | 0 | 0 | 270.7911 | 0 | 0 | 0 | 0
2017-12-20 14:00 | 237.8005 | 0.70879 |  | 249.7059 | 0 | 0 | 0 | 0 | 256.7229 | 0 | 0 | 0 | 0 | 262.4641 | 0 | 0 | 0 | 0 | 262.6767 | 0 | 0 | 0 | 0 | 262.8185 | 0 | 0 | 0 | 0 | 263.0311 | 0 | 0 | 0 | 0 | 263.2438 | 0 | 0 | 0 | 0 | 263.4564 | 0 | 0 | 0 | 0 | 263.7399 | 0 | 0 | 0 | 0 | 263.9525 | 0 | 0 | 0 | 0 | 264.0943 | 0 | 0 | 0 | 0 | 264.3069 | 0 | 0 | 0 | 0 | 264.4487 | 0 | 0 | 0 | 0 | 264.6613 | 0 | 0 | 0 | 0 | 264.874 | 0 | 0 | 0 | 0 | 265.0157 | 0 | 0 | 0 | 0 | 265.2284 | 0 | 0 | 0 | 0 | 265.441 | 0 | 0 | 0 | 0 | 265.5119 | 0 | 0 | 0 | 0 | 265.7245 | 0 | 0 | 0 | 0 | 265.9372 | 0 | 0 | 0 | 0 | 266.0789 | 0 | 0 | 0 | 0 | 266.2915 | 0 | 0 | 0 | 0 | 266.4333 | 0 | 0 | 0 | 0 | 266.5751 | 0 | 0 | 0 | 0
2017-12-20 15:00 | 239.4783 | 0.71379 |  | 251.4677 | 0 | 0 | 0 | 0 | 258.5342 | 0 | 0 | 0 | 0 | 264.3159 | 0 | 0 | 0 | 0 | 264.53 | 0 | 0 | 0 | 0 | 264.6728 | 0 | 0 | 0 | 0 | 264.8869 | 0 | 0 | 0 | 0 | 265.101 | 0 | 0 | 0 | 0 | 265.3152 | 0 | 0 | 0 | 0 | 265.6007 | 0 | 0 | 0 | 0 | 265.8148 | 0 | 0 | 0 | 0 | 265.9576 | 0 | 0 | 0 | 0 | 266.1717 | 0 | 0 | 0 | 0 | 266.3145 | 0 | 0 | 0 | 0 | 266.5286 | 0 | 0 | 0 | 0 | 266.7427 | 0 | 0 | 0 | 0 | 266.8855 | 0 | 0 | 0 | 0 | 267.0996 | 0 | 0 | 0 | 0 | 267.3138 | 0 | 0 | 0 | 0 | 267.3852 | 0 | 0 | 0 | 0 | 267.5993 | 0 | 0 | 0 | 0 | 267.8134 | 0 | 0 | 0 | 0 | 267.9562 | 0 | 0 | 0 | 0 | 268.1703 | 0 | 0 | 0 | 0 | 268.3131 | 0 | 0 | 0 | 0 | 268.4558 | 0 | 0 | 0 | 0
2017-12-20 16:00 | 240.6437 | 0.71726 |  | 252.6914 | 0 | 0 | 0 | 0 | 259.7923 | 0 | 0 | 0 | 0 | 265.6022 | 0 | 0 | 0 | 0 | 265.8173 | 0 | 0 | 0 | 0 | 265.9608 | 0 | 0 | 0 | 0 | 266.176 | 0 | 0 | 0 | 0 | 266.3911 | 0 | 0 | 0 | 0 | 266.6063 | 0 | 0 | 0 | 0 | 266.8932 | 0 | 0 | 0 | 0 | 267.1084 | 0 | 0 | 0 | 0 | 267.2519 | 0 | 0 | 0 | 0 | 267.467 | 0 | 0 | 0 | 0 | 267.6105 | 0 | 0 | 0 | 0 | 267.8257 | 0 | 0 | 0 | 0 | 268.0408 | 0 | 0 | 0 | 0 | 268.1843 | 0 | 0 | 0 | 0 | 268.3995 | 0 | 0 | 0 | 0 | 268.6147 | 0 | 0 | 0 | 0 | 268.6864 | 0 | 0 | 0 | 0 | 268.9016 | 0 | 0 | 0 | 0 | 269.1167 | 0 | 0 | 0 | 0 | 269.2602 | 0 | 0 | 0 | 0 | 269.4754 | 0 | 0 | 0 | 0 | 269.6188 | 0 | 0 | 0 | 0 | 269.7623 | 0 | 0 | 0 | 0
2017-12-20 17:00 | 241.7456 | 0.72055 |  | 253.8485 | 0 | 0 | 0 | 0 | 260.9819 | 0 | 0 | 0 | 0 | 266.8183 | 0 | 0 | 0 | 0 | 267.0345 | 0 | 0 | 0 | 0 | 267.1786 | 0 | 0 | 0 | 0 | 267.3948 | 0 | 0 | 0 | 0 | 267.6109 | 0 | 0 | 0 | 0 | 267.8271 | 0 | 0 | 0 | 0 | 268.1153 | 0 | 0 | 0 | 0 | 268.3315 | 0 | 0 | 0 | 0 | 268.4756 | 0 | 0 | 0 | 0 | 268.6917 | 0 | 0 | 0 | 0 | 268.8359 | 0 | 0 | 0 | 0 | 269.052 | 0 | 0 | 0 | 0 | 269.2682 | 0 | 0 | 0 | 0 | 269.4123 | 0 | 0 | 0 | 0 | 269.6285 | 0 | 0 | 0 | 0 | 269.8446 | 0 | 0 | 0 | 0 | 269.9167 | 0 | 0 | 0 | 0 | 270.1328 | 0 | 0 | 0 | 0 | 270.349 | 0 | 0 | 0 | 0 | 270.4931 | 0 | 0 | 0 | 0 | 270.7093 | 0 | 0 | 0 | 0 | 270.8534 | 0 | 0 | 0 | 0 | 270.9975 | 0 | 0 | 0 | 0
2017-12-20 18:00 | 241.8918 | 0.72098 |  | 254.002 | 0 | 0 | 0 | 0 | 261.1397 | 0 | 0 | 0 | 0 | 266.9797 | 0 | 0 | 0 | 0 | 267.196 | 0 | 0 | 0 | 0 | 267.3402 | 0 | 0 | 0 | 0 | 267.5565 | 0 | 0 | 0 | 0 | 267.7728 | 0 | 0 | 0 | 0 | 267.9891 | 0 | 0 | 0 | 0 | 268.2775 | 0 | 0 | 0 | 0 | 268.4937 | 0 | 0 | 0 | 0 | 268.6379 | 0 | 0 | 0 | 0 | 268.8542 | 0 | 0 | 0 | 0 | 268.9984 | 0 | 0 | 0 | 0 | 269.2147 | 0 | 0 | 0 | 0 | 269.431 | 0 | 0 | 0 | 0 | 269.5752 | 0 | 0 | 0 | 0 | 269.7915 | 0 | 0 | 0 | 0 | 270.0078 | 0 | 0 | 0 | 0 | 270.0799 | 0 | 0 | 0 | 0 | 270.2962 | 0 | 0 | 0 | 0 | 270.5125 | 0 | 0 | 0 | 0 | 270.6567 | 0 | 0 | 0 | 0 | 270.873 | 0 | 0 | 0 | 0 | 271.0172 | 0 | 0 | 0 | 0 | 271.1614 | 0 | 0 | 0 | 0
2017-12-20 19:00 | 249.4373 | 0.74347 |  | 261.9253 | 0 | 0 | 0 | 0 | 269.2856 | 0 | 0 | 0 | 0 | 275.3078 | 0 | 0 | 0 | 0 | 275.5308 | 0 | 0 | 0 | 0 | 275.6795 | 0 | 0 | 0 | 0 | 275.9025 | 0 | 0 | 0 | 0 | 276.1256 | 0 | 0 | 0 | 0 | 276.3486 | 0 | 0 | 0 | 0 | 276.646 | 0 | 0 | 0 | 0 | 276.8691 | 0 | 0 | 0 | 0 | 277.0177 | 0 | 0 | 0 | 0 | 277.2408 | 0 | 0 | 0 | 0 | 277.3895 | 0 | 0 | 0 | 0 | 277.6125 | 0 | 0 | 0 | 0 | 277.8356 | 0 | 0 | 0 | 0 | 277.9843 | 0 | 0 | 0 | 0 | 278.2073 | 0 | 0 | 0 | 0 | 278.4303 | 0 | 0 | 0 | 0 | 278.5047 | 0 | 0 | 0 | 0 | 278.7277 | 0 | 0 | 0 | 0 | 278.9508 | 0 | 0 | 0 | 0 | 279.0995 | 0 | 0 | 0 | 0 | 279.3225 | 0 | 0 | 0 | 0 | 279.4712 | 0 | 0 | 0 | 0 | 279.6199 | 0 | 0 | 0 | 0
2017-12-20 20:00 | 251.9428 | 0.75094 |  | 264.5562 | 0 | 0 | 0 | 0 | 271.9905 | 0 | 0 | 0 | 0 | 278.0732 | 0 | 0 | 0 | 0 | 278.2984 | 0 | 0 | 0 | 0 | 278.4486 | 0 | 0 | 0 | 0 | 278.6739 | 0 | 0 | 0 | 0 | 278.8992 | 0 | 0 | 0 | 0 | 279.1245 | 0 | 0 | 0 | 0 | 279.4248 | 0 | 0 | 0 | 0 | 279.6501 | 0 | 0 | 0 | 0 | 279.8003 | 0 | 0 | 0 | 0 | 280.0256 | 0 | 0 | 0 | 0 | 280.1758 | 0 | 0 | 0 | 0 | 280.4011 | 0 | 0 | 0 | 0 | 280.6264 | 0 | 0 | 0 | 0 | 280.7765 | 0 | 0 | 0 | 0 | 281.0018 | 0 | 0 | 0 | 0 | 281.2271 | 0 | 0 | 0 | 0 | 281.3022 | 0 | 0 | 0 | 0 | 281.5275 | 0 | 0 | 0 | 0 | 281.7528 | 0 | 0 | 0 | 0 | 281.903 | 0 | 0 | 0 | 0 | 282.1282 | 0 | 0 | 0 | 0 | 282.2784 | 0 | 0 | 0 | 0 | 282.4286 | 0 | 0 | 0 | 0
2017-12-20 21:00 | 262.0744 | 0.78114 |  | 275.1951 | 0 | 0 | 0 | 0 | 282.9284 | 0 | 0 | 0 | 0 | 289.2556 | 0 | 0 | 0 | 0 | 289.49 | 0 | 0 | 0 | 0 | 289.6462 | 0 | 0 | 0 | 0 | 289.8805 | 0 | 0 | 0 | 0 | 290.1149 | 0 | 0 | 0 | 0 | 290.3492 | 0 | 0 | 0 | 0 | 290.6617 | 0 | 0 | 0 | 0 | 290.896 | 0 | 0 | 0 | 0 | 291.0522 | 0 | 0 | 0 | 0 | 291.2866 | 0 | 0 | 0 | 0 | 291.4428 | 0 | 0 | 0 | 0 | 291.6771 | 0 | 0 | 0 | 0 | 291.9115 | 0 | 0 | 0 | 0 | 292.0677 | 0 | 0 | 0 | 0 | 292.3021 | 0 | 0 | 0 | 0 | 292.5364 | 0 | 0 | 0 | 0 | 292.6145 | 0 | 0 | 0 | 0 | 292.8488 | 0 | 0 | 0 | 0 | 293.0832 | 0 | 0 | 0 | 0 | 293.2394 | 0 | 0 | 0 | 0 | 293.4738 | 0 | 0 | 0 | 0 | 293.63 | 0 | 0 | 0 | 0 | 293.7862 | 0 | 0 | 0 | 0
2017-12-20 22:00 | 271.0579 | 0.80791 |  | 284.6284 | 0 | 0 | 0 | 0 | 292.6267 | 0 | 0 | 0 | 0 | 299.1708 | 0.0059232 | 0 | 0 | 0.011846 | 299.4132 | 0.0064489 | 0 | 0 | 0.012898 | 299.5748 | 0.0067993 | 0 | 0 | 0.013599 | 299.8172 | 0.0073251 | 0 | 0 | 0.01465 | 300.0595 | 0.0078508 | 0 | 0 | 0.015702 | 300.3019 | 0.0083765 | 0 | 0 | 0.016753 | 300.6251 | 0.0090774 | 0 | 0 | 0.018155 | 300.8674 | 0.0096031 | 0 | 0 | 0.019206 | 301.029 | 0.0099536 | 0 | 0 | 0.019907 | 301.2714 | 0.010479 | 0 | 0 | 0.020959 | 301.433 | 0.01083 | 0 | 0 | 0.02166 | 301.6754 | 0.011356 | 0 | 0 | 0.022711 | 301.9177 | 0.011881 | 0 | 0 | 0.023762 | 302.0793 | 0.012232 | 0 | 0 | 0.024463 | 302.3217 | 0.012757 | 0 | 0 | 0.025515 | 302.5641 | 0.013283 | 0 | 0 | 0.026566 | 302.6449 | 0.013458 | 0 | 0 | 0.026917 | 302.8872 | 0.013984 | 0 | 0 | 0.027968 | 303.1296 | 0.01451 | 0 | 0 | 0.02902 | 303.2912 | 0.01486 | 0 | 0 | 0.02972 | 303.5336 | 0.015386 | 0 | 0 | 0.030772 | 303.6952 | 0.015736 | 0 | 0 | 0.031473 | 303.8567 | 0.016087 | 0 | 0 | 0.032174
2017-12-20 23:00 | 276.6486 | 0.82458 |  | 290.4989 | 0 | 0 | 0 | 0 | 298.6623 | 0.0048201 | 0 | 0 | 0.0096401 | 305.3413 | 0.019307 | 0 | 0 | 0.038614 | 305.5887 | 0.019844 | 0 | 0 | 0.039687 | 305.7536 | 0.020201 | 0 | 0 | 0.040403 | 306.001 | 0.020738 | 0 | 0 | 0.041476 | 306.2484 | 0.021274 | 0 | 0 | 0.042549 | 306.4957 | 0.021811 | 0 | 0 | 0.043622 | 306.8256 | 0.022526 | 0 | 0 | 0.045053 | 307.0729 | 0.023063 | 0 | 0 | 0.046126 | 307.2379 | 0.023421 | 0 | 0 | 0.046841 | 307.4852 | 0.023957 | 0 | 0 | 0.047914 | 307.6502 | 0.024315 | 0 | 0 | 0.04863 | 307.8975 | 0.024851 | 0 | 0 | 0.049703 | 308.1449 | 0.025388 | 0 | 0 | 0.050776 | 308.3098 | 0.025746 | 0 | 0 | 0.051491 | 308.5572 | 0.026282 | 0 | 0 | 0.052564 | 308.8046 | 0.026819 | 0 | 0 | 0.053637 | 308.887 | 0.026998 | 0 | 0 | 0.053995 | 309.1344 | 0.027534 | 0 | 0 | 0.055068 | 309.3818 | 0.028071 | 0 | 0 | 0.056141 | 309.5467 | 0.028428 | 0 | 0 | 0.056857 | 309.7941 | 0.028965 | 0 | 0 | 0.05793 | 309.959 | 0.029323 | 0 | 0 | 0.058645 | 310.1239 | 0.02968 | 0 | 0 | 0.059361
2017-12-21 | 271.5836 | 0.80948 |  | 285.1803 | 0 | 0 | 0 | 0 | 293.1942 | 0 | 0 | 0 | 0 | 299.751 | 0.0071816 | 0 | 0 | 0.014363 | 299.9938 | 0.0077083 | 0 | 0 | 0.015417 | 300.1557 | 0.0080594 | 0 | 0 | 0.016119 | 300.3986 | 0.0085862 | 0 | 0 | 0.017172 | 300.6414 | 0.0091129 | 0 | 0 | 0.018226 | 300.8843 | 0.0096396 | 0 | 0 | 0.019279 | 301.2081 | 0.010342 | 0 | 0 | 0.020684 | 301.4509 | 0.010869 | 0 | 0 | 0.021737 | 301.6128 | 0.01122 | 0 | 0 | 0.02244 | 301.8556 | 0.011747 | 0 | 0 | 0.023493 | 302.0175 | 0.012098 | 0 | 0 | 0.024195 | 302.2604 | 0.012624 | 0 | 0 | 0.025249 | 302.5032 | 0.013151 | 0 | 0 | 0.026302 | 302.6651 | 0.013502 | 0 | 0 | 0.027005 | 302.908 | 0.014029 | 0 | 0 | 0.028058 | 303.1508 | 0.014556 | 0 | 0 | 0.029112 | 303.2318 | 0.014731 | 0 | 0 | 0.029463 | 303.4746 | 0.015258 | 0 | 0 | 0.030516 | 303.7175 | 0.015785 | 0 | 0 | 0.03157 | 303.8794 | 0.016136 | 0 | 0 | 0.032272 | 304.1222 | 0.016663 | 0 | 0 | 0.033325 | 304.2841 | 0.017014 | 0 | 0 | 0.034028 | 304.446 | 0.017365 | 0 | 0 | 0.03473
2017-12-21 01:00 | 279.4065 | 0.8328 |  | 293.3949 | 0 | 0 | 0 | 0 | 301.6396 | 0.011278 | 0 | 0 | 0.022556 | 308.3853 | 0.025909 | 0 | 0 | 0.051818 | 308.6351 | 0.026451 | 0 | 0 | 0.052902 | 308.8017 | 0.026812 | 0 | 0 | 0.053625 | 309.0515 | 0.027354 | 0 | 0 | 0.054709 | 309.3013 | 0.027896 | 0 | 0 | 0.055792 | 309.5512 | 0.028438 | 0 | 0 | 0.056876 | 309.8843 | 0.029161 | 0 | 0 | 0.058321 | 310.1341 | 0.029703 | 0 | 0 | 0.059405 | 310.3007 | 0.030064 | 0 | 0 | 0.060128 | 310.5505 | 0.030606 | 0 | 0 | 0.061211 | 310.7171 | 0.030967 | 0 | 0 | 0.061934 | 310.9669 | 0.031509 | 0 | 0 | 0.063018 | 311.2168 | 0.032051 | 0 | 0 | 0.064102 | 311.3833 | 0.032412 | 0 | 0 | 0.064824 | 311.6332 | 0.032954 | 0 | 0 | 0.065908 | 311.883 | 0.033496 | 0 | 0 | 0.066992 | 311.9663 | 0.033677 | 0 | 0 | 0.067353 | 312.2161 | 0.034218 | 0 | 0 | 0.068437 | 312.466 | 0.03476 | 0 | 0 | 0.069521 | 312.6325 | 0.035122 | 0 | 0 | 0.070243 | 312.8824 | 0.035663 | 0 | 0 | 0.071327 | 313.0489 | 0.036025 | 0 | 0 | 0.07205 | 313.2155 | 0.036386 | 0 | 0 | 0.072772
2017-12-21 02:00 | 265.1214 | 0.79022 |  | 278.3946 | 0 | 0 | 0 | 0 | 286.2178 | 0 | 0 | 0 | 0 | 292.6186 | 0 | 0 | 0 | 0 | 292.8557 | 0 | 0 | 0 | 0 | 293.0137 | 0 | 0 | 0 | 0 | 293.2508 | 0 | 0 | 0 | 0 | 293.4879 | 0 | 0 | 0 | 0 | 293.7249 | 0 | 0 | 0 | 0 | 294.041 | 0 | 0 | 0 | 0 | 294.2781 | 0 | 0 | 0 | 0 | 294.4361 | 0 | 0 | 0 | 0 | 294.6732 | 0 | 0 | 0 | 0 | 294.8312 | 0 | 0 | 0 | 0 | 295.0683 | 0 | 0 | 0 | 0 | 295.3054 | 0 | 0 | 0 | 0 | 295.4634 | 0 | 0 | 0 | 0 | 295.7005 | 0 | 0 | 0 | 0 | 295.9375 | 0 | 0 | 0 | 0 | 296.0166 | 0 | 0 | 0 | 0 | 296.2536 | 0 | 0 | 0 | 0 | 296.4907 | 0.00010996 | 0 | 0 | 0.00021992 | 296.6487 | 0.00045276 | 0 | 0 | 0.00090552 | 296.8858 | 0.00096695 | 0 | 0 | 0.0019339 | 297.0439 | 0.0013098 | 0 | 0 | 0.0026195 | 297.2019 | 0.0016525 | 0 | 0 | 0.0033051
2017-12-21 03:00 | 262.2626 | 0.7817 |  | 275.3927 | 0 | 0 | 0 | 0 | 283.1315 | 0 | 0 | 0 | 0 | 289.4632 | 0 | 0 | 0 | 0 | 289.6977 | 0 | 0 | 0 | 0 | 289.8541 | 0 | 0 | 0 | 0 | 290.0886 | 0 | 0 | 0 | 0 | 290.3231 | 0 | 0 | 0 | 0 | 290.5576 | 0 | 0 | 0 | 0 | 290.8703 | 0 | 0 | 0 | 0 | 291.1048 | 0 | 0 | 0 | 0 | 291.2611 | 0 | 0 | 0 | 0 | 291.4957 | 0 | 0 | 0 | 0 | 291.652 | 0 | 0 | 0 | 0 | 291.8865 | 0 | 0 | 0 | 0 | 292.121 | 0 | 0 | 0 | 0 | 292.2774 | 0 | 0 | 0 | 0 | 292.5119 | 0 | 0 | 0 | 0 | 292.7464 | 0 | 0 | 0 | 0 | 292.8245 | 0 | 0 | 0 | 0 | 293.0591 | 0 | 0 | 0 | 0 | 293.2936 | 0 | 0 | 0 | 0 | 293.4499 | 0 | 0 | 0 | 0 | 293.6844 | 0 | 0 | 0 | 0 | 293.8408 | 0 | 0 | 0 | 0 | 293.9971 | 0 | 0 | 0 | 0
2017-12-21 04:00 | 264.6071 | 0.78869 |  | 277.8546 | 0 | 0 | 0 | 0 | 285.6626 | 0 | 0 | 0 | 0 | 292.051 | 0 | 0 | 0 | 0 | 292.2876 | 0 | 0 | 0 | 0 | 292.4453 | 0 | 0 | 0 | 0 | 292.6819 | 0 | 0 | 0 | 0 | 292.9185 | 0 | 0 | 0 | 0 | 293.1551 | 0 | 0 | 0 | 0 | 293.4706 | 0 | 0 | 0 | 0 | 293.7072 | 0 | 0 | 0 | 0 | 293.865 | 0 | 0 | 0 | 0 | 294.1016 | 0 | 0 | 0 | 0 | 294.2593 | 0 | 0 | 0 | 0 | 294.4959 | 0 | 0 | 0 | 0 | 294.7325 | 0 | 0 | 0 | 0 | 294.8903 | 0 | 0 | 0 | 0 | 295.1269 | 0 | 0 | 0 | 0 | 295.3635 | 0 | 0 | 0 | 0 | 295.4423 | 0 | 0 | 0 | 0 | 295.6789 | 0 | 0 | 0 | 0 | 295.9155 | 0 | 0 | 0 | 0 | 296.0733 | 0 | 0 | 0 | 0 | 296.3099 | 0 | 0 | 0 | 0 | 296.4676 | 5.9925e-05 | 0 | 0 | 0.00011985 | 296.6254 | 0.00040206 | 0 | 0 | 0.00080412
2017-12-21 05:00 | 256.6916 | 0.76509 |  | 269.5428 | 0 | 0 | 0 | 0 | 277.1173 | 0 | 0 | 0 | 0 | 283.3145 | 0 | 0 | 0 | 0 | 283.5441 | 0 | 0 | 0 | 0 | 283.6971 | 0 | 0 | 0 | 0 | 283.9266 | 0 | 0 | 0 | 0 | 284.1561 | 0 | 0 | 0 | 0 | 284.3857 | 0 | 0 | 0 | 0 | 284.6917 | 0 | 0 | 0 | 0 | 284.9212 | 0 | 0 | 0 | 0 | 285.0743 | 0 | 0 | 0 | 0 | 285.3038 | 0 | 0 | 0 | 0 | 285.4568 | 0 | 0 | 0 | 0 | 285.6863 | 0 | 0 | 0 | 0 | 285.9159 | 0 | 0 | 0 | 0 | 286.0689 | 0 | 0 | 0 | 0 | 286.2984 | 0 | 0 | 0 | 0 | 286.5279 | 0 | 0 | 0 | 0 | 286.6044 | 0 | 0 | 0 | 0 | 286.834 | 0 | 0 | 0 | 0 | 287.0635 | 0 | 0 | 0 | 0 | 287.2165 | 0 | 0 | 0 | 0 | 287.446 | 0 | 0 | 0 | 0 | 287.5991 | 0 | 0 | 0 | 0 | 287.7521 | 0 | 0 | 0 | 0
2017-12-21 06:00 | 258.7907 | 0.77135 |  | 271.747 | 0 | 0 | 0 | 0 | 279.3833 | 0 | 0 | 0 | 0 | 285.6313 | 0 | 0 | 0 | 0 | 285.8627 | 0 | 0 | 0 | 0 | 286.0169 | 0 | 0 | 0 | 0 | 286.2484 | 0 | 0 | 0 | 0 | 286.4798 | 0 | 0 | 0 | 0 | 286.7112 | 0 | 0 | 0 | 0 | 287.0197 | 0 | 0 | 0 | 0 | 287.2511 | 0 | 0 | 0 | 0 | 287.4054 | 0 | 0 | 0 | 0 | 287.6368 | 0 | 0 | 0 | 0 | 287.7911 | 0 | 0 | 0 | 0 | 288.0225 | 0 | 0 | 0 | 0 | 288.2539 | 0 | 0 | 0 | 0 | 288.4081 | 0 | 0 | 0 | 0 | 288.6395 | 0 | 0 | 0 | 0 | 288.8709 | 0 | 0 | 0 | 0 | 288.9481 | 0 | 0 | 0 | 0 | 289.1795 | 0 | 0 | 0 | 0 | 289.4109 | 0 | 0 | 0 | 0 | 289.5652 | 0 | 0 | 0 | 0 | 289.7966 | 0 | 0 | 0 | 0 | 289.9508 | 0 | 0 | 0 | 0 | 290.1051 | 0 | 0 | 0 | 0
2017-12-21 07:00 | 261.8949 | 0.7806 |  | 275.0066 | 0 | 0 | 0 | 0 | 282.7346 | 0 | 0 | 0 | 0 | 289.0575 | 0 | 0 | 0 | 0 | 289.2917 | 0 | 0 | 0 | 0 | 289.4478 | 0 | 0 | 0 | 0 | 289.682 | 0 | 0 | 0 | 0 | 289.9161 | 0 | 0 | 0 | 0 | 290.1503 | 0 | 0 | 0 | 0 | 290.4626 | 0 | 0 | 0 | 0 | 290.6967 | 0 | 0 | 0 | 0 | 290.8529 | 0 | 0 | 0 | 0 | 291.087 | 0 | 0 | 0 | 0 | 291.2432 | 0 | 0 | 0 | 0 | 291.4773 | 0 | 0 | 0 | 0 | 291.7115 | 0 | 0 | 0 | 0 | 291.8676 | 0 | 0 | 0 | 0 | 292.1018 | 0 | 0 | 0 | 0 | 292.336 | 0 | 0 | 0 | 0 | 292.4141 | 0 | 0 | 0 | 0 | 292.6482 | 0 | 0 | 0 | 0 | 292.8824 | 0 | 0 | 0 | 0 | 293.0386 | 0 | 0 | 0 | 0 | 293.2727 | 0 | 0 | 0 | 0 | 293.4289 | 0 | 0 | 0 | 0 | 293.585 | 0 | 0 | 0 | 0
2017-12-21 08:00 | 258.3196 | 0.76995 |  | 271.2523 | 0 | 0 | 0 | 0 | 278.8747 | 0 | 0 | 0 | 0 | 285.1113 | 0 | 0 | 0 | 0 | 285.3423 | 0 | 0 | 0 | 0 | 285.4963 | 0 | 0 | 0 | 0 | 285.7273 | 0 | 0 | 0 | 0 | 285.9583 | 0 | 0 | 0 | 0 | 286.1892 | 0 | 0 | 0 | 0 | 286.4972 | 0 | 0 | 0 | 0 | 286.7282 | 0 | 0 | 0 | 0 | 286.8822 | 0 | 0 | 0 | 0 | 287.1132 | 0 | 0 | 0 | 0 | 287.2672 | 0 | 0 | 0 | 0 | 287.4982 | 0 | 0 | 0 | 0 | 287.7291 | 0 | 0 | 0 | 0 | 287.8831 | 0 | 0 | 0 | 0 | 288.1141 | 0 | 0 | 0 | 0 | 288.3451 | 0 | 0 | 0 | 0 | 288.4221 | 0 | 0 | 0 | 0 | 288.6531 | 0 | 0 | 0 | 0 | 288.8841 | 0 | 0 | 0 | 0 | 289.038 | 0 | 0 | 0 | 0 | 289.269 | 0 | 0 | 0 | 0 | 289.423 | 0 | 0 | 0 | 0 | 289.577 | 0 | 0 | 0 | 0
2017-12-21 09:00 | 265.9014 | 0.79255 |  | 279.2136 | 0 | 0 | 0 | 0 | 287.0598 | 0 | 0 | 0 | 0 | 293.4795 | 0 | 0 | 0 | 0 | 293.7172 | 0 | 0 | 0 | 0 | 293.8757 | 0 | 0 | 0 | 0 | 294.1135 | 0 | 0 | 0 | 0 | 294.3513 | 0 | 0 | 0 | 0 | 294.589 | 0 | 0 | 0 | 0 | 294.906 | 0 | 0 | 0 | 0 | 295.1438 | 0 | 0 | 0 | 0 | 295.3023 | 0 | 0 | 0 | 0 | 295.5401 | 0 | 0 | 0 | 0 | 295.6986 | 0 | 0 | 0 | 0 | 295.9363 | 0 | 0 | 0 | 0 | 296.1741 | 0 | 0 | 0 | 0 | 296.3326 | 0 | 0 | 0 | 0 | 296.5704 | 0.00028279 | 0 | 0 | 0.00056559 | 296.8081 | 0.0007985 | 0 | 0 | 0.001597 | 296.8874 | 0.00097041 | 0 | 0 | 0.0019408 | 297.1252 | 0.0014861 | 0 | 0 | 0.0029722 | 297.3629 | 0.0020018 | 0 | 0 | 0.0040036 | 297.5214 | 0.0023456 | 0 | 0 | 0.0046913 | 297.7592 | 0.0028613 | 0 | 0 | 0.0057227 | 297.9177 | 0.0032051 | 0 | 0 | 0.0064103 | 298.0762 | 0.003549 | 0 | 0 | 0.0070979
2017-12-21 10:00 | 264.4605 | 0.78825 |  | 277.7006 | 0 | 0 | 0 | 0 | 285.5043 | 0 | 0 | 0 | 0 | 291.8891 | 0 | 0 | 0 | 0 | 292.1256 | 0 | 0 | 0 | 0 | 292.2832 | 0 | 0 | 0 | 0 | 292.5197 | 0 | 0 | 0 | 0 | 292.7562 | 0 | 0 | 0 | 0 | 292.9927 | 0 | 0 | 0 | 0 | 293.308 | 0 | 0 | 0 | 0 | 293.5444 | 0 | 0 | 0 | 0 | 293.7021 | 0 | 0 | 0 | 0 | 293.9386 | 0 | 0 | 0 | 0 | 294.0962 | 0 | 0 | 0 | 0 | 294.3327 | 0 | 0 | 0 | 0 | 294.5692 | 0 | 0 | 0 | 0 | 294.7268 | 0 | 0 | 0 | 0 | 294.9633 | 0 | 0 | 0 | 0 | 295.1998 | 0 | 0 | 0 | 0 | 295.2786 | 0 | 0 | 0 | 0 | 295.5151 | 0 | 0 | 0 | 0 | 295.7515 | 0 | 0 | 0 | 0 | 295.9092 | 0 | 0 | 0 | 0 | 296.1457 | 0 | 0 | 0 | 0 | 296.3033 | 0 | 0 | 0 | 0 | 296.461 | 4.547e-05 | 0 | 0 | 9.0941e-05
2017-12-21 11:00 | 266.805 | 0.79524 |  | 280.1626 | 0 | 0 | 0 | 0 | 288.0354 | 0 | 0 | 0 | 0 | 294.4769 | 0 | 0 | 0 | 0 | 294.7154 | 0 | 0 | 0 | 0 | 294.8745 | 0 | 0 | 0 | 0 | 295.113 | 0 | 0 | 0 | 0 | 295.3516 | 0 | 0 | 0 | 0 | 295.5902 | 0 | 0 | 0 | 0 | 295.9083 | 0 | 0 | 0 | 0 | 296.1469 | 0 | 0 | 0 | 0 | 296.3059 | 0 | 0 | 0 | 0 | 296.5445 | 0.00022661 | 0 | 0 | 0.00045321 | 296.7035 | 0.00057158 | 0 | 0 | 0.0011432 | 296.9421 | 0.001089 | 0 | 0 | 0.0021781 | 297.1807 | 0.0016065 | 0 | 0 | 0.003213 | 297.3397 | 0.0019515 | 0 | 0 | 0.003903 | 297.5783 | 0.0024689 | 0 | 0 | 0.0049379 | 297.8169 | 0.0029864 | 0 | 0 | 0.0059728 | 297.8964 | 0.0031589 | 0 | 0 | 0.0063178 | 298.135 | 0.0036764 | 0 | 0 | 0.0073527 | 298.3735 | 0.0041938 | 0 | 0 | 0.0083876 | 298.5326 | 0.0045388 | 0 | 0 | 0.0090776 | 298.7711 | 0.0050562 | 0 | 0 | 0.010112 | 298.9302 | 0.0054012 | 0 | 0 | 0.010802 | 299.0892 | 0.0057462 | 0 | 0 | 0.011492
2017-12-21 12:00 | 267.5802 | 0.79755 |  | 280.9765 | 0 | 0 | 0 | 0 | 288.8722 | 0 | 0 | 0 | 0 | 295.3324 | 0 | 0 | 0 | 0 | 295.5716 | 0 | 0 | 0 | 0 | 295.7311 | 0 | 0 | 0 | 0 | 295.9704 | 0 | 0 | 0 | 0 | 296.2097 | 0 | 0 | 0 | 0 | 296.4489 | 1.9397e-05 | 0 | 0 | 3.8794e-05 | 296.768 | 0.00071135 | 0 | 0 | 0.0014227 | 297.0072 | 0.0012303 | 0 | 0 | 0.0024606 | 297.1667 | 0.0015763 | 0 | 0 | 0.0031526 | 297.406 | 0.0020953 | 0 | 0 | 0.0041905 | 297.5655 | 0.0024412 | 0 | 0 | 0.0048825 | 297.8048 | 0.0029602 | 0 | 0 | 0.0059204 | 298.044 | 0.0034792 | 0 | 0 | 0.0069583 | 298.2036 | 0.0038251 | 0 | 0 | 0.0076503 | 298.4428 | 0.0043441 | 0 | 0 | 0.0086882 | 298.6821 | 0.0048631 | 0 | 0 | 0.0097261 | 298.7618 | 0.0050361 | 0 | 0 | 0.010072 | 299.0011 | 0.005555 | 0 | 0 | 0.01111 | 299.2404 | 0.006074 | 0 | 0 | 0.012148 | 299.3999 | 0.00642 | 0 | 0 | 0.01284 | 299.6391 | 0.0069389 | 0 | 0 | 0.013878 | 299.7986 | 0.0072849 | 0 | 0 | 0.01457 | 299.9582 | 0.0076309 | 0 | 0 | 0.015262
2017-12-21 13:00 | 267.56 | 0.79749 |  | 280.9553 | 0 | 0 | 0 | 0 | 288.8505 | 0 | 0 | 0 | 0 | 295.3101 | 0 | 0 | 0 | 0 | 295.5494 | 0 | 0 | 0 | 0 | 295.7089 | 0 | 0 | 0 | 0 | 295.9481 | 0 | 0 | 0 | 0 | 296.1874 | 0 | 0 | 0 | 0 | 296.4266 | 0 | 0 | 0 | 0 | 296.7456 | 0.00066284 | 0 | 0 | 0.0013257 | 296.9848 | 0.0011818 | 0 | 0 | 0.0023635 | 297.1443 | 0.0015277 | 0 | 0 | 0.0030554 | 297.3836 | 0.0020466 | 0 | 0 | 0.0040933 | 297.5431 | 0.0023926 | 0 | 0 | 0.0047852 | 297.7823 | 0.0029115 | 0 | 0 | 0.005823 | 298.0216 | 0.0034304 | 0 | 0 | 0.0068609 | 298.1811 | 0.0037764 | 0 | 0 | 0.0075528 | 298.4203 | 0.0042953 | 0 | 0 | 0.0085906 | 298.6596 | 0.0048143 | 0 | 0 | 0.0096285 | 298.7393 | 0.0049872 | 0 | 0 | 0.0099745 | 298.9786 | 0.0055062 | 0 | 0 | 0.011012 | 299.2178 | 0.0060251 | 0 | 0 | 0.01205 | 299.3773 | 0.006371 | 0 | 0 | 0.012742 | 299.6166 | 0.00689 | 0 | 0 | 0.01378 | 299.7761 | 0.0072359 | 0 | 0 | 0.014472 | 299.9356 | 0.0075819 | 0 | 0 | 0.015164
2017-12-21 14:00 | 271.7265 | 0.80991 |  | 285.3304 | 0 | 0 | 0 | 0 | 293.3485 | 0 | 0 | 0 | 0 | 299.9087 | 0.0075237 | 0 | 0 | 0.015047 | 300.1517 | 0.0080507 | 0 | 0 | 0.016101 | 300.3137 | 0.008402 | 0 | 0 | 0.016804 | 300.5567 | 0.008929 | 0 | 0 | 0.017858 | 300.7996 | 0.009456 | 0 | 0 | 0.018912 | 301.0426 | 0.0099831 | 0 | 0 | 0.019966 | 301.3666 | 0.010686 | 0 | 0 | 0.021371 | 301.6095 | 0.011213 | 0 | 0 | 0.022425 | 301.7715 | 0.011564 | 0 | 0 | 0.023128 | 302.0145 | 0.012091 | 0 | 0 | 0.024182 | 302.1765 | 0.012442 | 0 | 0 | 0.024885 | 302.4194 | 0.012969 | 0 | 0 | 0.025939 | 302.6624 | 0.013496 | 0 | 0 | 0.026993 | 302.8244 | 0.013848 | 0 | 0 | 0.027696 | 303.0674 | 0.014375 | 0 | 0 | 0.02875 | 303.3103 | 0.014902 | 0 | 0 | 0.029804 | 303.3913 | 0.015077 | 0 | 0 | 0.030155 | 303.6343 | 0.015604 | 0 | 0 | 0.031209 | 303.8773 | 0.016131 | 0 | 0 | 0.032263 | 304.0393 | 0.016483 | 0 | 0 | 0.032966 | 304.2822 | 0.01701 | 0 | 0 | 0.03402 | 304.4442 | 0.017361 | 0 | 0 | 0.034722 | 304.6062 | 0.017712 | 0 | 0 | 0.035425
2017-12-21 15:00 | 275.4186 | 0.82091 |  | 289.2073 | 0 | 0 | 0 | 0 | 297.3343 | 0.0019398 | 0 | 0 | 0.0038796 | 303.9837 | 0.016362 | 0 | 0 | 0.032725 | 304.23 | 0.016897 | 0 | 0 | 0.033793 | 304.3942 | 0.017253 | 0 | 0 | 0.034505 | 304.6405 | 0.017787 | 0 | 0 | 0.035574 | 304.8867 | 0.018321 | 0 | 0 | 0.036642 | 305.133 | 0.018855 | 0 | 0 | 0.03771 | 305.4614 | 0.019567 | 0 | 0 | 0.039135 | 305.7076 | 0.020102 | 0 | 0 | 0.040203 | 305.8718 | 0.020458 | 0 | 0 | 0.040915 | 306.1181 | 0.020992 | 0 | 0 | 0.041984 | 306.2823 | 0.021348 | 0 | 0 | 0.042696 | 306.5286 | 0.021882 | 0 | 0 | 0.043764 | 306.7748 | 0.022416 | 0 | 0 | 0.044832 | 306.939 | 0.022772 | 0 | 0 | 0.045545 | 307.1853 | 0.023307 | 0 | 0 | 0.046613 | 307.4316 | 0.023841 | 0 | 0 | 0.047681 | 307.5136 | 0.024019 | 0 | 0 | 0.048037 | 307.7599 | 0.024553 | 0 | 0 | 0.049106 | 308.0062 | 0.025087 | 0 | 0 | 0.050174 | 308.1704 | 0.025443 | 0 | 0 | 0.050886 | 308.4167 | 0.025977 | 0 | 0 | 0.051955 | 308.5808 | 0.026333 | 0 | 0 | 0.052667 | 308.745 | 0.02669 | 0 | 0 | 0.053379
2017-12-21 16:00 | 277.9455 | 0.82844 |  | 291.8607 | 0 | 0 | 0 | 0 | 300.0623 | 0.0078568 | 0 | 0 | 0.015714 | 306.7727 | 0.022412 | 0 | 0 | 0.044823 | 307.0212 | 0.022951 | 0 | 0 | 0.045901 | 307.1869 | 0.02331 | 0 | 0 | 0.04662 | 307.4355 | 0.023849 | 0 | 0 | 0.047698 | 307.684 | 0.024388 | 0 | 0 | 0.048776 | 307.9325 | 0.024927 | 0 | 0 | 0.049855 | 308.2639 | 0.025646 | 0 | 0 | 0.051292 | 308.5124 | 0.026185 | 0 | 0 | 0.05237 | 308.6781 | 0.026545 | 0 | 0 | 0.053089 | 308.9267 | 0.027084 | 0 | 0 | 0.054167 | 309.0924 | 0.027443 | 0 | 0 | 0.054886 | 309.3409 | 0.027982 | 0 | 0 | 0.055964 | 309.5894 | 0.028521 | 0 | 0 | 0.057042 | 309.7551 | 0.02888 | 0 | 0 | 0.057761 | 310.0036 | 0.02942 | 0 | 0 | 0.058839 | 310.2522 | 0.029959 | 0 | 0 | 0.059917 | 310.335 | 0.030138 | 0 | 0 | 0.060277 | 310.5836 | 0.030677 | 0 | 0 | 0.061355 | 310.8321 | 0.031216 | 0 | 0 | 0.062433 | 310.9978 | 0.031576 | 0 | 0 | 0.063152 | 311.2463 | 0.032115 | 0 | 0 | 0.06423 | 311.412 | 0.032474 | 0 | 0 | 0.064949 | 311.5777 | 0.032834 | 0 | 0 | 0.065667
2017-12-21 17:00 | 288.593 | 0.86018 |  | 303.0413 | 0.014318 | 0 | 0 | 0.028637 | 311.5571 | 0.032789 | 0 | 0 | 0.065578 | 318.5246 | 0.047901 | 0 | 0 | 0.095803 | 318.7826 | 0.048461 | 0 | 0 | 0.096922 | 318.9546 | 0.048834 | 0 | 0 | 0.097669 | 319.2127 | 0.049394 | 0 | 0 | 0.098788 | 319.4707 | 0.049954 | 0 | 0 | 0.099907 | 319.7288 | 0.050513 | 0 | 0 | 0.10103 | 320.0729 | 0.05126 | 0 | 0 | 0.10252 | 320.3309 | 0.051819 | 0 | 0 | 0.10364 | 320.503 | 0.052193 | 0 | 0 | 0.10439 | 320.761 | 0.052752 | 0 | 0 | 0.1055 | 320.9331 | 0.053125 | 0 | 0 | 0.10625 | 321.1911 | 0.053685 | 0 | 0 | 0.10737 | 321.4492 | 0.054245 | 0 | 0 | 0.10849 | 321.6212 | 0.054618 | 0 | 0 | 0.10924 | 321.8793 | 0.055178 | 0 | 0 | 0.11036 | 322.1373 | 0.055737 | 0 | 0 | 0.11147 | 322.2233 | 0.055924 | 0 | 0 | 0.11185 | 322.4814 | 0.056484 | 0 | 0 | 0.11297 | 322.7394 | 0.057043 | 0 | 0 | 0.11409 | 322.9115 | 0.057417 | 0 | 0 | 0.11483 | 323.1695 | 0.057976 | 0 | 0 | 0.11595 | 323.3416 | 0.058349 | 0 | 0 | 0.1167 | 323.5136 | 0.058723 | 0 | 0 | 0.11745
2017-12-21 18:00 | 291.803 | 0.86975 |  | 306.412 | 0.021629 | 0 | 0 | 0.043259 | 315.0225 | 0.040306 | 0 | 0 | 0.080611 | 322.0675 | 0.055586 | 0 | 0 | 0.11117 | 322.3284 | 0.056152 | 0 | 0 | 0.1123 | 322.5024 | 0.056529 | 0 | 0 | 0.11306 | 322.7633 | 0.057095 | 0 | 0 | 0.11419 | 323.0242 | 0.057661 | 0 | 0 | 0.11532 | 323.2851 | 0.058227 | 0 | 0 | 0.11645 | 323.633 | 0.058982 | 0 | 0 | 0.11796 | 323.894 | 0.059548 | 0 | 0 | 0.1191 | 324.0679 | 0.059925 | 0 | 0 | 0.11985 | 324.3288 | 0.060491 | 0 | 0 | 0.12098 | 324.5028 | 0.060868 | 0 | 0 | 0.12174 | 324.7637 | 0.061434 | 0 | 0 | 0.12287 | 325.0246 | 0.062 | 0 | 0 | 0.124 | 325.1986 | 0.062377 | 0 | 0 | 0.12475 | 325.4595 | 0.062943 | 0 | 0 | 0.12589 | 325.7204 | 0.063509 | 0 | 0 | 0.12702 | 325.8074 | 0.063698 | 0 | 0 | 0.1274 | 326.0683 | 0.064264 | 0 | 0 | 0.12853 | 326.3293 | 0.06483 | 0 | 0 | 0.12966 | 326.5032 | 0.065207 | 0 | 0 | 0.13041 | 326.7641 | 0.065773 | 0 | 0 | 0.13155 | 326.9381 | 0.06615 | 0 | 0 | 0.1323 | 327.112 | 0.066528 | 0 | 0 | 0.13306
2017-12-21 19:00 | 296.4093 | 0.88348 |  | 311.249 | 0.032121 | 0 | 0 | 0.064241 | 319.9954 | 0.051092 | 0 | 0 | 0.10218 | 327.1515 | 0.066613 | 0 | 0 | 0.13323 | 327.4166 | 0.067188 | 0 | 0 | 0.13438 | 327.5933 | 0.067571 | 0 | 0 | 0.13514 | 327.8583 | 0.068146 | 0 | 0 | 0.13629 | 328.1234 | 0.068721 | 0 | 0 | 0.13744 | 328.3884 | 0.069296 | 0 | 0 | 0.13859 | 328.7418 | 0.070063 | 0 | 0 | 0.14013 | 329.0068 | 0.070637 | 0 | 0 | 0.14127 | 329.1835 | 0.071021 | 0 | 0 | 0.14204 | 329.4486 | 0.071596 | 0 | 0 | 0.14319 | 329.6253 | 0.071979 | 0 | 0 | 0.14396 | 329.8903 | 0.072554 | 0 | 0 | 0.14511 | 330.1554 | 0.073129 | 0 | 0 | 0.14626 | 330.3321 | 0.073512 | 0 | 0 | 0.14702 | 330.5971 | 0.074087 | 0 | 0 | 0.14817 | 330.8622 | 0.074662 | 0 | 0 | 0.14932 | 330.9505 | 0.074853 | 0 | 0 | 0.14971 | 331.2155 | 0.075428 | 0 | 0 | 0.15086 | 331.4806 | 0.076003 | 0 | 0 | 0.15201 | 331.6573 | 0.076386 | 0 | 0 | 0.15277 | 331.9223 | 0.076961 | 0 | 0 | 0.15392 | 332.099 | 0.077344 | 0 | 0 | 0.15469 | 332.2757 | 0.077728 | 0 | 0 | 0.15546
2017-12-21 20:00 | 286.3388 | 0.85346 |  | 300.6742 | 0.009184 | 0 | 0 | 0.018368 | 309.1235 | 0.02751 | 0 | 0 | 0.055021 | 316.0365 | 0.042505 | 0 | 0 | 0.08501 | 316.2926 | 0.04306 | 0 | 0 | 0.08612 | 316.4632 | 0.04343 | 0 | 0 | 0.086861 | 316.7193 | 0.043986 | 0 | 0 | 0.087972 | 316.9753 | 0.044541 | 0 | 0 | 0.089082 | 317.2314 | 0.045096 | 0 | 0 | 0.090193 | 317.5727 | 0.045837 | 0 | 0 | 0.091674 | 317.8288 | 0.046392 | 0 | 0 | 0.092785 | 317.9995 | 0.046763 | 0 | 0 | 0.093525 | 318.2555 | 0.047318 | 0 | 0 | 0.094636 | 318.4262 | 0.047688 | 0 | 0 | 0.095376 | 318.6822 | 0.048243 | 0 | 0 | 0.096487 | 318.9383 | 0.048799 | 0 | 0 | 0.097598 | 319.109 | 0.049169 | 0 | 0 | 0.098338 | 319.365 | 0.049724 | 0 | 0 | 0.099449 | 319.6211 | 0.05028 | 0 | 0 | 0.10056 | 319.7064 | 0.050465 | 0 | 0 | 0.10093 | 319.9624 | 0.05102 | 0 | 0 | 0.10204 | 320.2185 | 0.051576 | 0 | 0 | 0.10315 | 320.3892 | 0.051946 | 0 | 0 | 0.10389 | 320.6452 | 0.052501 | 0 | 0 | 0.105 | 320.8159 | 0.052871 | 0 | 0 | 0.10574 | 320.9866 | 0.053242 | 0 | 0 | 0.10648
2017-12-21 21:00 | 296.1886 | 0.88282 |  | 311.0172 | 0.031618 | 0 | 0 | 0.063236 | 319.7571 | 0.050575 | 0 | 0 | 0.10115 | 326.9079 | 0.066085 | 0 | 0 | 0.13217 | 327.1728 | 0.066659 | 0 | 0 | 0.13332 | 327.3494 | 0.067042 | 0 | 0 | 0.13408 | 327.6142 | 0.067617 | 0 | 0 | 0.13523 | 327.879 | 0.068191 | 0 | 0 | 0.13638 | 328.1439 | 0.068766 | 0 | 0 | 0.13753 | 328.497 | 0.069532 | 0 | 0 | 0.13906 | 328.7619 | 0.070106 | 0 | 0 | 0.14021 | 328.9384 | 0.070489 | 0 | 0 | 0.14098 | 329.2033 | 0.071064 | 0 | 0 | 0.14213 | 329.3798 | 0.071447 | 0 | 0 | 0.14289 | 329.6447 | 0.072021 | 0 | 0 | 0.14404 | 329.9095 | 0.072595 | 0 | 0 | 0.14519 | 330.0861 | 0.072978 | 0 | 0 | 0.14596 | 330.3509 | 0.073553 | 0 | 0 | 0.14711 | 330.6158 | 0.074127 | 0 | 0 | 0.14825 | 330.7041 | 0.074319 | 0 | 0 | 0.14864 | 330.9689 | 0.074893 | 0 | 0 | 0.14979 | 331.2338 | 0.075468 | 0 | 0 | 0.15094 | 331.4103 | 0.075851 | 0 | 0 | 0.1517 | 331.6752 | 0.076425 | 0 | 0 | 0.15285 | 331.8517 | 0.076808 | 0 | 0 | 0.15362 | 332.0283 | 0.077191 | 0 | 0 | 0.15438
2017-12-21 22:00 | 293.1643 | 0.8738 |  | 307.8414 | 0.02473 | 0 | 0 | 0.049459 | 316.4921 | 0.043493 | 0 | 0 | 0.086986 | 323.5699 | 0.058845 | 0 | 0 | 0.11769 | 323.8321 | 0.059413 | 0 | 0 | 0.11883 | 324.0068 | 0.059792 | 0 | 0 | 0.11958 | 324.269 | 0.060361 | 0 | 0 | 0.12072 | 324.5311 | 0.06093 | 0 | 0 | 0.12186 | 324.7933 | 0.061498 | 0 | 0 | 0.123 | 325.1428 | 0.062256 | 0 | 0 | 0.12451 | 325.4049 | 0.062825 | 0 | 0 | 0.12565 | 325.5797 | 0.063204 | 0 | 0 | 0.12641 | 325.8418 | 0.063773 | 0 | 0 | 0.12755 | 326.0166 | 0.064152 | 0 | 0 | 0.1283 | 326.2787 | 0.06472 | 0 | 0 | 0.12944 | 326.5409 | 0.065289 | 0 | 0 | 0.13058 | 326.7156 | 0.065668 | 0 | 0 | 0.13134 | 326.9778 | 0.066236 | 0 | 0 | 0.13247 | 327.2399 | 0.066805 | 0 | 0 | 0.13361 | 327.3273 | 0.066995 | 0 | 0 | 0.13399 | 327.5894 | 0.067563 | 0 | 0 | 0.13513 | 327.8516 | 0.068132 | 0 | 0 | 0.13626 | 328.0263 | 0.068511 | 0 | 0 | 0.13702 | 328.2885 | 0.069079 | 0 | 0 | 0.13816 | 328.4632 | 0.069458 | 0 | 0 | 0.13892 | 328.638 | 0.069837 | 0 | 0 | 0.13967
2017-12-21 23:00 | 295.2052 | 0.87989 |  | 309.9846 | 0.029378 | 0 | 0 | 0.058756 | 318.6955 | 0.048272 | 0 | 0 | 0.096544 | 325.8226 | 0.063731 | 0 | 0 | 0.12746 | 326.0865 | 0.064303 | 0 | 0 | 0.12861 | 326.2625 | 0.064685 | 0 | 0 | 0.12937 | 326.5265 | 0.065258 | 0 | 0 | 0.13052 | 326.7905 | 0.06583 | 0 | 0 | 0.13166 | 327.0544 | 0.066403 | 0 | 0 | 0.13281 | 327.4064 | 0.067166 | 0 | 0 | 0.13433 | 327.6703 | 0.067739 | 0 | 0 | 0.13548 | 327.8463 | 0.06812 | 0 | 0 | 0.13624 | 328.1103 | 0.068693 | 0 | 0 | 0.13739 | 328.2863 | 0.069075 | 0 | 0 | 0.13815 | 328.5502 | 0.069647 | 0 | 0 | 0.13929 | 328.8142 | 0.07022 | 0 | 0 | 0.14044 | 328.9902 | 0.070601 | 0 | 0 | 0.1412 | 329.2541 | 0.071174 | 0 | 0 | 0.14235 | 329.5181 | 0.071746 | 0 | 0 | 0.14349 | 329.6061 | 0.071937 | 0 | 0 | 0.14387 | 329.8701 | 0.07251 | 0 | 0 | 0.14502 | 330.134 | 0.073082 | 0 | 0 | 0.14616 | 330.31 | 0.073464 | 0 | 0 | 0.14693 | 330.574 | 0.074037 | 0 | 0 | 0.14807 | 330.75 | 0.074418 | 0 | 0 | 0.14884 | 330.9259 | 0.0748 | 0 | 0 | 0.1496
2017-12-22 | 301.7924 | 0.89952 |  | 316.9016 | 0.044381 | 0 | 0 | 0.088762 | 325.8068 | 0.063697 | 0 | 0 | 0.12739 | 333.093 | 0.0795 | 0 | 0 | 0.159 | 333.3628 | 0.080086 | 0 | 0 | 0.16017 | 333.5427 | 0.080476 | 0 | 0 | 0.16095 | 333.8126 | 0.081061 | 0 | 0 | 0.16212 | 334.0825 | 0.081646 | 0 | 0 | 0.16329 | 334.3523 | 0.082232 | 0 | 0 | 0.16446 | 334.7121 | 0.083012 | 0 | 0 | 0.16602 | 334.982 | 0.083598 | 0 | 0 | 0.1672 | 335.1619 | 0.083988 | 0 | 0 | 0.16798 | 335.4317 | 0.084573 | 0 | 0 | 0.16915 | 335.6116 | 0.084963 | 0 | 0 | 0.16993 | 335.8815 | 0.085549 | 0 | 0 | 0.1711 | 336.1514 | 0.086134 | 0 | 0 | 0.17227 | 336.3313 | 0.086524 | 0 | 0 | 0.17305 | 336.6011 | 0.087109 | 0 | 0 | 0.17422 | 336.871 | 0.087695 | 0 | 0 | 0.17539 | 336.9609 | 0.08789 | 0 | 0 | 0.17578 | 337.2308 | 0.088475 | 0 | 0 | 0.17695 | 337.5006 | 0.089061 | 0 | 0 | 0.17812 | 337.6805 | 0.089451 | 0 | 0 | 0.1789 | 337.9504 | 0.090036 | 0 | 0 | 0.18007 | 338.1303 | 0.090426 | 0 | 0 | 0.18085 | 338.3102 | 0.090816 | 0 | 0 | 0.18163
2017-12-22 01:00 | 292.8167 | 0.87277 |  | 307.4765 | 0.023938 | 0 | 0 | 0.047876 | 316.1169 | 0.042679 | 0 | 0 | 0.085358 | 323.1863 | 0.058013 | 0 | 0 | 0.11603 | 323.4481 | 0.058581 | 0 | 0 | 0.11716 | 323.6227 | 0.058959 | 0 | 0 | 0.11792 | 323.8845 | 0.059527 | 0 | 0 | 0.11905 | 324.1464 | 0.060095 | 0 | 0 | 0.12019 | 324.4082 | 0.060663 | 0 | 0 | 0.12133 | 324.7573 | 0.06142 | 0 | 0 | 0.12284 | 325.0191 | 0.061988 | 0 | 0 | 0.12398 | 325.1937 | 0.062367 | 0 | 0 | 0.12473 | 325.4555 | 0.062935 | 0 | 0 | 0.12587 | 325.6301 | 0.063313 | 0 | 0 | 0.12663 | 325.8919 | 0.063881 | 0 | 0 | 0.12776 | 326.1537 | 0.064449 | 0 | 0 | 0.1289 | 326.3283 | 0.064828 | 0 | 0 | 0.12966 | 326.5901 | 0.065396 | 0 | 0 | 0.13079 | 326.8519 | 0.065963 | 0 | 0 | 0.13193 | 326.9392 | 0.066153 | 0 | 0 | 0.13231 | 327.201 | 0.066721 | 0 | 0 | 0.13344 | 327.4629 | 0.067289 | 0 | 0 | 0.13458 | 327.6374 | 0.067667 | 0 | 0 | 0.13533 | 327.8993 | 0.068235 | 0 | 0 | 0.13647 | 328.0738 | 0.068614 | 0 | 0 | 0.13723 | 328.2484 | 0.068992 | 0 | 0 | 0.13798
2017-12-22 02:00 | 292.7295 | 0.87251 |  | 307.3849 | 0.023739 | 0 | 0 | 0.047479 | 316.0227 | 0.042475 | 0 | 0 | 0.08495 | 323.0901 | 0.057804 | 0 | 0 | 0.11561 | 323.3518 | 0.058372 | 0 | 0 | 0.11674 | 323.5263 | 0.05875 | 0 | 0 | 0.1175 | 323.7881 | 0.059318 | 0 | 0 | 0.11864 | 324.0498 | 0.059886 | 0 | 0 | 0.11977 | 324.3116 | 0.060453 | 0 | 0 | 0.12091 | 324.6606 | 0.06121 | 0 | 0 | 0.12242 | 324.9223 | 0.061778 | 0 | 0 | 0.12356 | 325.0968 | 0.062157 | 0 | 0 | 0.12431 | 325.3586 | 0.062724 | 0 | 0 | 0.12545 | 325.5331 | 0.063103 | 0 | 0 | 0.12621 | 325.7948 | 0.063671 | 0 | 0 | 0.12734 | 326.0566 | 0.064238 | 0 | 0 | 0.12848 | 326.2311 | 0.064617 | 0 | 0 | 0.12923 | 326.4928 | 0.065185 | 0 | 0 | 0.13037 | 326.7546 | 0.065752 | 0 | 0 | 0.1315 | 326.8418 | 0.065942 | 0 | 0 | 0.13188 | 327.1036 | 0.066509 | 0 | 0 | 0.13302 | 327.3654 | 0.067077 | 0 | 0 | 0.13415 | 327.5399 | 0.067456 | 0 | 0 | 0.13491 | 327.8016 | 0.068023 | 0 | 0 | 0.13605 | 327.9761 | 0.068402 | 0 | 0 | 0.1368 | 328.1506 | 0.06878 | 0 | 0 | 0.13756
2017-12-22 03:00 | 296.7268 | 0.88442 |  | 311.5824 | 0.032844 | 0 | 0 | 0.065688 | 320.3382 | 0.051835 | 0 | 0 | 0.10367 | 327.502 | 0.067373 | 0 | 0 | 0.13475 | 327.7673 | 0.067949 | 0 | 0 | 0.1359 | 327.9442 | 0.068333 | 0 | 0 | 0.13667 | 328.2095 | 0.068908 | 0 | 0 | 0.13782 | 328.4749 | 0.069484 | 0 | 0 | 0.13897 | 328.7402 | 0.070059 | 0 | 0 | 0.14012 | 329.094 | 0.070826 | 0 | 0 | 0.14165 | 329.3593 | 0.071402 | 0 | 0 | 0.1428 | 329.5362 | 0.071786 | 0 | 0 | 0.14357 | 329.8015 | 0.072361 | 0 | 0 | 0.14472 | 329.9784 | 0.072745 | 0 | 0 | 0.14549 | 330.2437 | 0.07332 | 0 | 0 | 0.14664 | 330.509 | 0.073896 | 0 | 0 | 0.14779 | 330.6859 | 0.074279 | 0 | 0 | 0.14856 | 330.9512 | 0.074855 | 0 | 0 | 0.14971 | 331.2166 | 0.07543 | 0 | 0 | 0.15086 | 331.305 | 0.075622 | 0 | 0 | 0.15124 | 331.5703 | 0.076198 | 0 | 0 | 0.1524 | 331.8357 | 0.076773 | 0 | 0 | 0.15355 | 332.0125 | 0.077157 | 0 | 0 | 0.15431 | 332.2779 | 0.077732 | 0 | 0 | 0.15546 | 332.4548 | 0.078116 | 0 | 0 | 0.15623 | 332.6316 | 0.0785 | 0 | 0 | 0.157
2017-12-22 04:00 | 307.1076 | 0.91536 |  | 322.4828 | 0.056487 | 0 | 0 | 0.11297 | 331.5449 | 0.076143 | 0 | 0 | 0.15229 | 338.9594 | 0.092225 | 0 | 0 | 0.18445 | 339.234 | 0.09282 | 0 | 0 | 0.18564 | 339.4171 | 0.093217 | 0 | 0 | 0.18643 | 339.6917 | 0.093813 | 0 | 0 | 0.18763 | 339.9663 | 0.094408 | 0 | 0 | 0.18882 | 340.2409 | 0.095004 | 0 | 0 | 0.19001 | 340.607 | 0.095798 | 0 | 0 | 0.1916 | 340.8816 | 0.096394 | 0 | 0 | 0.19279 | 341.0647 | 0.096791 | 0 | 0 | 0.19358 | 341.3393 | 0.097387 | 0 | 0 | 0.19477 | 341.5224 | 0.097784 | 0 | 0 | 0.19557 | 341.797 | 0.098379 | 0 | 0 | 0.19676 | 342.0716 | 0.098975 | 0 | 0 | 0.19795 | 342.2547 | 0.099372 | 0 | 0 | 0.19874 | 342.5293 | 0.099968 | 0 | 0 | 0.19994 | 342.8039 | 0.10056 | 0 | 0 | 0.20113 | 342.8954 | 0.10076 | 0 | 0 | 0.20152 | 343.17 | 0.10136 | 0 | 0 | 0.20271 | 343.4447 | 0.10195 | 0 | 0 | 0.20391 | 343.6277 | 0.10235 | 0 | 0 | 0.2047 | 343.9023 | 0.10295 | 0 | 0 | 0.20589 | 344.0854 | 0.10334 | 0 | 0 | 0.20669 | 344.2685 | 0.10374 | 0 | 0 | 0.20748
2017-12-22 05:00 | 305.937 | 0.91188 |  | 321.2536 | 0.053821 | 0 | 0 | 0.10764 | 330.2812 | 0.073402 | 0 | 0 | 0.1468 | 337.6674 | 0.089422 | 0 | 0 | 0.17884 | 337.9409 | 0.090016 | 0 | 0 | 0.18003 | 338.1233 | 0.090411 | 0 | 0 | 0.18082 | 338.3969 | 0.091004 | 0 | 0 | 0.18201 | 338.6704 | 0.091598 | 0 | 0 | 0.1832 | 338.944 | 0.092191 | 0 | 0 | 0.18438 | 339.3088 | 0.092982 | 0 | 0 | 0.18596 | 339.5823 | 0.093576 | 0 | 0 | 0.18715 | 339.7647 | 0.093971 | 0 | 0 | 0.18794 | 340.0383 | 0.094565 | 0 | 0 | 0.18913 | 340.2206 | 0.09496 | 0 | 0 | 0.18992 | 340.4942 | 0.095554 | 0 | 0 | 0.19111 | 340.7678 | 0.096147 | 0 | 0 | 0.19229 | 340.9501 | 0.096542 | 0 | 0 | 0.19308 | 341.2237 | 0.097136 | 0 | 0 | 0.19427 | 341.4973 | 0.097729 | 0 | 0 | 0.19546 | 341.5884 | 0.097927 | 0 | 0 | 0.19585 | 341.862 | 0.09852 | 0 | 0 | 0.19704 | 342.1356 | 0.099114 | 0 | 0 | 0.19823 | 342.3179 | 0.099509 | 0 | 0 | 0.19902 | 342.5915 | 0.1001 | 0 | 0 | 0.20021 | 342.7739 | 0.1005 | 0 | 0 | 0.201 | 342.9563 | 0.10089 | 0 | 0 | 0.20179
2017-12-22 06:00 | 311.8723 | 0.92957 |  | 327.4861 | 0.067339 | 0 | 0 | 0.13468 | 336.6888 | 0.0873 | 0 | 0 | 0.1746 | 344.2183 | 0.10363 | 0 | 0 | 0.20726 | 344.4971 | 0.10424 | 0 | 0 | 0.20847 | 344.683 | 0.10464 | 0 | 0 | 0.20928 | 344.9619 | 0.10524 | 0 | 0 | 0.21049 | 345.2408 | 0.10585 | 0 | 0 | 0.2117 | 345.5196 | 0.10645 | 0 | 0 | 0.21291 | 345.8915 | 0.10726 | 0 | 0 | 0.21452 | 346.1703 | 0.10787 | 0 | 0 | 0.21573 | 346.3563 | 0.10827 | 0 | 0 | 0.21654 | 346.6351 | 0.10887 | 0 | 0 | 0.21775 | 346.821 | 0.10928 | 0 | 0 | 0.21855 | 347.0999 | 0.10988 | 0 | 0 | 0.21976 | 347.3788 | 0.11049 | 0 | 0 | 0.22097 | 347.5647 | 0.11089 | 0 | 0 | 0.22178 | 347.8436 | 0.11149 | 0 | 0 | 0.22299 | 348.1224 | 0.1121 | 0 | 0 | 0.2242 | 348.2154 | 0.1123 | 0 | 0 | 0.2246 | 348.4943 | 0.11291 | 0 | 0 | 0.22581 | 348.7731 | 0.11351 | 0 | 0 | 0.22702 | 348.959 | 0.11391 | 0 | 0 | 0.22783 | 349.2379 | 0.11452 | 0 | 0 | 0.22904 | 349.4238 | 0.11492 | 0 | 0 | 0.22984 | 349.6097 | 0.11533 | 0 | 0 | 0.23065
2017-12-22 07:00 | 315.6854 | 0.94093 |  | 331.4901 | 0.076024 | 0 | 0 | 0.15205 | 340.8053 | 0.096228 | 0 | 0 | 0.19246 | 348.4268 | 0.11276 | 0 | 0 | 0.22552 | 348.7091 | 0.11337 | 0 | 0 | 0.22674 | 348.8973 | 0.11378 | 0 | 0 | 0.22756 | 349.1796 | 0.11439 | 0 | 0 | 0.22878 | 349.4619 | 0.115 | 0 | 0 | 0.23001 | 349.7441 | 0.11562 | 0 | 0 | 0.23123 | 350.1205 | 0.11643 | 0 | 0 | 0.23287 | 350.4028 | 0.11705 | 0 | 0 | 0.23409 | 350.591 | 0.11745 | 0 | 0 | 0.23491 | 350.8732 | 0.11807 | 0 | 0 | 0.23613 | 351.0614 | 0.11847 | 0 | 0 | 0.23695 | 351.3437 | 0.11909 | 0 | 0 | 0.23817 | 351.626 | 0.1197 | 0 | 0 | 0.2394 | 351.8142 | 0.12011 | 0 | 0 | 0.24021 | 352.0965 | 0.12072 | 0 | 0 | 0.24144 | 352.3787 | 0.12133 | 0 | 0 | 0.24266 | 352.4728 | 0.12154 | 0 | 0 | 0.24307 | 352.7551 | 0.12215 | 0 | 0 | 0.24429 | 353.0374 | 0.12276 | 0 | 0 | 0.24552 | 353.2256 | 0.12317 | 0 | 0 | 0.24634 | 353.5079 | 0.12378 | 0 | 0 | 0.24756 | 353.696 | 0.12419 | 0 | 0 | 0.24838 | 353.8842 | 0.1246 | 0 | 0 | 0.24919
2017-12-22 08:00 | 314.2291 | 0.93659 |  | 329.9609 | 0.072707 | 0 | 0 | 0.14541 | 339.2332 | 0.092818 | 0 | 0 | 0.18564 | 346.8196 | 0.10927 | 0 | 0 | 0.21855 | 347.1005 | 0.10988 | 0 | 0 | 0.21977 | 347.2879 | 0.11029 | 0 | 0 | 0.22058 | 347.5688 | 0.1109 | 0 | 0 | 0.2218 | 347.8498 | 0.11151 | 0 | 0 | 0.22302 | 348.1308 | 0.11212 | 0 | 0 | 0.22423 | 348.5054 | 0.11293 | 0 | 0 | 0.22586 | 348.7864 | 0.11354 | 0 | 0 | 0.22708 | 348.9737 | 0.11395 | 0 | 0 | 0.22789 | 349.2547 | 0.11456 | 0 | 0 | 0.22911 | 349.442 | 0.11496 | 0 | 0 | 0.22992 | 349.723 | 0.11557 | 0 | 0 | 0.23114 | 350.004 | 0.11618 | 0 | 0 | 0.23236 | 350.1913 | 0.11659 | 0 | 0 | 0.23317 | 350.4723 | 0.1172 | 0 | 0 | 0.23439 | 350.7532 | 0.11781 | 0 | 0 | 0.23561 | 350.8469 | 0.11801 | 0 | 0 | 0.23602 | 351.1279 | 0.11862 | 0 | 0 | 0.23724 | 351.4089 | 0.11923 | 0 | 0 | 0.23845 | 351.5962 | 0.11963 | 0 | 0 | 0.23927 | 351.8772 | 0.12024 | 0 | 0 | 0.24049 | 352.0645 | 0.12065 | 0 | 0 | 0.2413 | 352.2518 | 0.12106 | 0 | 0 | 0.24211
2017-12-22 09:00 | 316.7073 | 0.94398 |  | 332.5632 | 0.078351 | 0 | 0 | 0.1567 | 341.9086 | 0.098621 | 0 | 0 | 0.19724 | 349.5548 | 0.11521 | 0 | 0 | 0.23041 | 349.838 | 0.11582 | 0 | 0 | 0.23164 | 350.0268 | 0.11623 | 0 | 0 | 0.23246 | 350.31 | 0.11684 | 0 | 0 | 0.23369 | 350.5931 | 0.11746 | 0 | 0 | 0.23492 | 350.8763 | 0.11807 | 0 | 0 | 0.23614 | 351.2539 | 0.11889 | 0 | 0 | 0.23778 | 351.5371 | 0.11951 | 0 | 0 | 0.23901 | 351.7259 | 0.11992 | 0 | 0 | 0.23983 | 352.0091 | 0.12053 | 0 | 0 | 0.24106 | 352.1979 | 0.12094 | 0 | 0 | 0.24188 | 352.4811 | 0.12155 | 0 | 0 | 0.24311 | 352.7643 | 0.12217 | 0 | 0 | 0.24433 | 352.9531 | 0.12258 | 0 | 0 | 0.24515 | 353.2363 | 0.12319 | 0 | 0 | 0.24638 | 353.5195 | 0.12381 | 0 | 0 | 0.24761 | 353.6139 | 0.12401 | 0 | 0 | 0.24802 | 353.8971 | 0.12462 | 0 | 0 | 0.24925 | 354.1803 | 0.12524 | 0 | 0 | 0.25048 | 354.3691 | 0.12565 | 0 | 0 | 0.2513 | 354.6522 | 0.12626 | 0 | 0 | 0.25252 | 354.841 | 0.12667 | 0 | 0 | 0.25334 | 355.0298 | 0.12708 | 0 | 0 | 0.25416
2017-12-22 10:00 | 315.7582 | 0.94115 |  | 331.5666 | 0.07619 | 0 | 0 | 0.15238 | 340.884 | 0.096399 | 0 | 0 | 0.1928 | 348.5073 | 0.11293 | 0 | 0 | 0.22587 | 348.7896 | 0.11355 | 0 | 0 | 0.22709 | 348.9778 | 0.11395 | 0 | 0 | 0.22791 | 349.2602 | 0.11457 | 0 | 0 | 0.22913 | 349.5425 | 0.11518 | 0 | 0 | 0.23036 | 349.8249 | 0.11579 | 0 | 0 | 0.23158 | 350.2013 | 0.11661 | 0 | 0 | 0.23322 | 350.4837 | 0.11722 | 0 | 0 | 0.23444 | 350.6719 | 0.11763 | 0 | 0 | 0.23526 | 350.9543 | 0.11824 | 0 | 0 | 0.23648 | 351.1425 | 0.11865 | 0 | 0 | 0.2373 | 351.4248 | 0.11926 | 0 | 0 | 0.23852 | 351.7072 | 0.11987 | 0 | 0 | 0.23975 | 351.8954 | 0.12028 | 0 | 0 | 0.24057 | 352.1777 | 0.1209 | 0 | 0 | 0.24179 | 352.4601 | 0.12151 | 0 | 0 | 0.24302 | 352.5542 | 0.12171 | 0 | 0 | 0.24342 | 352.8366 | 0.12232 | 0 | 0 | 0.24465 | 353.1189 | 0.12294 | 0 | 0 | 0.24587 | 353.3071 | 0.12334 | 0 | 0 | 0.24669 | 353.5895 | 0.12396 | 0 | 0 | 0.24791 | 353.7777 | 0.12437 | 0 | 0 | 0.24873 | 353.9659 | 0.12477 | 0 | 0 | 0.24955
2017-12-22 11:00 | 312.5306 | 0.93153 |  | 328.1774 | 0.068838 | 0 | 0 | 0.13768 | 337.3995 | 0.088841 | 0 | 0 | 0.17768 | 344.9449 | 0.10521 | 0 | 0 | 0.21041 | 345.2244 | 0.10581 | 0 | 0 | 0.21163 | 345.4107 | 0.10622 | 0 | 0 | 0.21243 | 345.6901 | 0.10682 | 0 | 0 | 0.21365 | 345.9696 | 0.10743 | 0 | 0 | 0.21486 | 346.249 | 0.10804 | 0 | 0 | 0.21607 | 346.6217 | 0.10884 | 0 | 0 | 0.21769 | 346.9011 | 0.10945 | 0 | 0 | 0.2189 | 347.0874 | 0.10985 | 0 | 0 | 0.21971 | 347.3669 | 0.11046 | 0 | 0 | 0.22092 | 347.5532 | 0.11086 | 0 | 0 | 0.22173 | 347.8326 | 0.11147 | 0 | 0 | 0.22294 | 348.1121 | 0.11208 | 0 | 0 | 0.22415 | 348.2984 | 0.11248 | 0 | 0 | 0.22496 | 348.5779 | 0.11309 | 0 | 0 | 0.22617 | 348.8573 | 0.11369 | 0 | 0 | 0.22739 | 348.9505 | 0.1139 | 0 | 0 | 0.22779 | 349.2299 | 0.1145 | 0 | 0 | 0.229 | 349.5094 | 0.11511 | 0 | 0 | 0.23022 | 349.6957 | 0.11551 | 0 | 0 | 0.23102 | 349.9752 | 0.11612 | 0 | 0 | 0.23224 | 350.1615 | 0.11652 | 0 | 0 | 0.23304 | 350.3478 | 0.11693 | 0 | 0 | 0.23385
2017-12-22 12:00 | 305.8622 | 0.91165 |  | 321.1751 | 0.053651 | 0 | 0 | 0.1073 | 330.2005 | 0.073227 | 0 | 0 | 0.14645 | 337.5849 | 0.089243 | 0 | 0 | 0.17849 | 337.8584 | 0.089836 | 0 | 0 | 0.17967 | 338.0407 | 0.090232 | 0 | 0 | 0.18046 | 338.3142 | 0.090825 | 0 | 0 | 0.18165 | 338.5877 | 0.091418 | 0 | 0 | 0.18284 | 338.8612 | 0.092012 | 0 | 0 | 0.18402 | 339.2259 | 0.092803 | 0 | 0 | 0.18561 | 339.4994 | 0.093396 | 0 | 0 | 0.18679 | 339.6817 | 0.093791 | 0 | 0 | 0.18758 | 339.9552 | 0.094384 | 0 | 0 | 0.18877 | 340.1375 | 0.09478 | 0 | 0 | 0.18956 | 340.411 | 0.095373 | 0 | 0 | 0.19075 | 340.6845 | 0.095966 | 0 | 0 | 0.19193 | 340.8668 | 0.096362 | 0 | 0 | 0.19272 | 341.1403 | 0.096955 | 0 | 0 | 0.19391 | 341.4138 | 0.097548 | 0 | 0 | 0.1951 | 341.505 | 0.097746 | 0 | 0 | 0.19549 | 341.7785 | 0.098339 | 0 | 0 | 0.19668 | 342.052 | 0.098932 | 0 | 0 | 0.19786 | 342.2343 | 0.099328 | 0 | 0 | 0.19866 | 342.5078 | 0.099921 | 0 | 0 | 0.19984 | 342.6901 | 0.10032 | 0 | 0 | 0.20063 | 342.8725 | 0.10071 | 0 | 0 | 0.20142
2017-12-22 13:00 | 300.989 | 0.89713 |  | 316.0579 | 0.042551 | 0 | 0 | 0.085102 | 324.9394 | 0.061815 | 0 | 0 | 0.12363 | 332.2062 | 0.077577 | 0 | 0 | 0.15515 | 332.4753 | 0.078161 | 0 | 0 | 0.15632 | 332.6547 | 0.07855 | 0 | 0 | 0.1571 | 332.9239 | 0.079134 | 0 | 0 | 0.15827 | 333.193 | 0.079717 | 0 | 0 | 0.15943 | 333.4621 | 0.080301 | 0 | 0 | 0.1606 | 333.821 | 0.081079 | 0 | 0 | 0.16216 | 334.0901 | 0.081663 | 0 | 0 | 0.16333 | 334.2696 | 0.082052 | 0 | 0 | 0.1641 | 334.5387 | 0.082636 | 0 | 0 | 0.16527 | 334.7181 | 0.083025 | 0 | 0 | 0.16605 | 334.9873 | 0.083609 | 0 | 0 | 0.16722 | 335.2564 | 0.084193 | 0 | 0 | 0.16839 | 335.4358 | 0.084582 | 0 | 0 | 0.16916 | 335.705 | 0.085166 | 0 | 0 | 0.17033 | 335.9741 | 0.085749 | 0 | 0 | 0.1715 | 336.0638 | 0.085944 | 0 | 0 | 0.17189 | 336.333 | 0.086528 | 0 | 0 | 0.17306 | 336.6021 | 0.087112 | 0 | 0 | 0.17422 | 336.7815 | 0.087501 | 0 | 0 | 0.175 | 337.0507 | 0.088085 | 0 | 0 | 0.17617 | 337.2301 | 0.088474 | 0 | 0 | 0.17695 | 337.4095 | 0.088863 | 0 | 0 | 0.17773
2017-12-22 14:00 | 295.2363 | 0.87998 |  | 310.0172 | 0.029449 | 0 | 0 | 0.058898 | 318.729 | 0.048345 | 0 | 0 | 0.09669 | 325.8568 | 0.063805 | 0 | 0 | 0.12761 | 326.1208 | 0.064378 | 0 | 0 | 0.12876 | 326.2968 | 0.064759 | 0 | 0 | 0.12952 | 326.5608 | 0.065332 | 0 | 0 | 0.13066 | 326.8248 | 0.065905 | 0 | 0 | 0.13181 | 327.0888 | 0.066477 | 0 | 0 | 0.13295 | 327.4408 | 0.067241 | 0 | 0 | 0.13448 | 327.7048 | 0.067813 | 0 | 0 | 0.13563 | 327.8808 | 0.068195 | 0 | 0 | 0.13639 | 328.1448 | 0.068768 | 0 | 0 | 0.13754 | 328.3208 | 0.069149 | 0 | 0 | 0.1383 | 328.5848 | 0.069722 | 0 | 0 | 0.13944 | 328.8488 | 0.070295 | 0 | 0 | 0.14059 | 329.0248 | 0.070676 | 0 | 0 | 0.14135 | 329.2888 | 0.071249 | 0 | 0 | 0.1425 | 329.5528 | 0.071822 | 0 | 0 | 0.14364 | 329.6408 | 0.072012 | 0 | 0 | 0.14402 | 329.9048 | 0.072585 | 0 | 0 | 0.14517 | 330.1687 | 0.073158 | 0 | 0 | 0.14632 | 330.3447 | 0.073539 | 0 | 0 | 0.14708 | 330.6087 | 0.074112 | 0 | 0 | 0.14822 | 330.7847 | 0.074494 | 0 | 0 | 0.14899 | 330.9607 | 0.074875 | 0 | 0 | 0.14975
2017-12-22 15:00 | 286.4927 | 0.85392 |  | 300.8359 | 0.0095347 | 0 | 0 | 0.019069 | 309.2897 | 0.027871 | 0 | 0 | 0.055742 | 316.2064 | 0.042873 | 0 | 0 | 0.085747 | 316.4626 | 0.043429 | 0 | 0 | 0.086858 | 316.6334 | 0.043799 | 0 | 0 | 0.087599 | 316.8896 | 0.044355 | 0 | 0 | 0.08871 | 317.1457 | 0.044911 | 0 | 0 | 0.089822 | 317.4019 | 0.045466 | 0 | 0 | 0.090933 | 317.7435 | 0.046207 | 0 | 0 | 0.092415 | 317.9997 | 0.046763 | 0 | 0 | 0.093526 | 318.1704 | 0.047133 | 0 | 0 | 0.094267 | 318.4266 | 0.047689 | 0 | 0 | 0.095378 | 318.5974 | 0.048059 | 0 | 0 | 0.096119 | 318.8536 | 0.048615 | 0 | 0 | 0.09723 | 319.1098 | 0.049171 | 0 | 0 | 0.098341 | 319.2805 | 0.049541 | 0 | 0 | 0.099082 | 319.5367 | 0.050097 | 0 | 0 | 0.10019 | 319.7929 | 0.050652 | 0 | 0 | 0.1013 | 319.8783 | 0.050838 | 0 | 0 | 0.10168 | 320.1345 | 0.051393 | 0 | 0 | 0.10279 | 320.3906 | 0.051949 | 0 | 0 | 0.1039 | 320.5614 | 0.052319 | 0 | 0 | 0.10464 | 320.8176 | 0.052875 | 0 | 0 | 0.10575 | 320.9884 | 0.053245 | 0 | 0 | 0.10649 | 321.1592 | 0.053616 | 0 | 0 | 0.10723
2017-12-22 16:00 | 278.0614 | 0.82879 |  | 291.9824 | 0 | 0 | 0 | 0 | 300.1875 | 0.0081282 | 0 | 0 | 0.016256 | 306.9006 | 0.022689 | 0 | 0 | 0.045378 | 307.1493 | 0.023228 | 0 | 0 | 0.046457 | 307.315 | 0.023588 | 0 | 0 | 0.047176 | 307.5637 | 0.024127 | 0 | 0 | 0.048254 | 307.8123 | 0.024667 | 0 | 0 | 0.049333 | 308.0609 | 0.025206 | 0 | 0 | 0.050412 | 308.3925 | 0.025925 | 0 | 0 | 0.05185 | 308.6411 | 0.026464 | 0 | 0 | 0.052928 | 308.8069 | 0.026824 | 0 | 0 | 0.053647 | 309.0555 | 0.027363 | 0 | 0 | 0.054726 | 309.2213 | 0.027723 | 0 | 0 | 0.055445 | 309.4699 | 0.028262 | 0 | 0 | 0.056524 | 309.7185 | 0.028801 | 0 | 0 | 0.057602 | 309.8843 | 0.029161 | 0 | 0 | 0.058321 | 310.1329 | 0.0297 | 0 | 0 | 0.0594 | 310.3816 | 0.030239 | 0 | 0 | 0.060478 | 310.4644 | 0.030419 | 0 | 0 | 0.060838 | 310.7131 | 0.030958 | 0 | 0 | 0.061917 | 310.9617 | 0.031498 | 0 | 0 | 0.062995 | 311.1275 | 0.031857 | 0 | 0 | 0.063714 | 311.3761 | 0.032396 | 0 | 0 | 0.064793 | 311.5419 | 0.032756 | 0 | 0 | 0.065512 | 311.7076 | 0.033115 | 0 | 0 | 0.066231
2017-12-22 17:00 | 268.7879 | 0.80115 |  | 282.2447 | 0 | 0 | 0 | 0 | 290.1761 | 0 | 0 | 0 | 0 | 296.6654 | 0.00048891 | 0 | 0 | 0.00097783 | 296.9058 | 0.0010102 | 0 | 0 | 0.0020204 | 297.066 | 0.0013578 | 0 | 0 | 0.0027155 | 297.3063 | 0.0018791 | 0 | 0 | 0.0037581 | 297.5467 | 0.0024004 | 0 | 0 | 0.0048008 | 297.787 | 0.0029217 | 0 | 0 | 0.0058434 | 298.1075 | 0.0036168 | 0 | 0 | 0.0072335 | 298.3478 | 0.0041381 | 0 | 0 | 0.0082761 | 298.5081 | 0.0044856 | 0 | 0 | 0.0089712 | 298.7484 | 0.0050069 | 0 | 0 | 0.010014 | 298.9086 | 0.0053545 | 0 | 0 | 0.010709 | 299.149 | 0.0058758 | 0 | 0 | 0.011752 | 299.3893 | 0.0063971 | 0 | 0 | 0.012794 | 299.5495 | 0.0067446 | 0 | 0 | 0.013489 | 299.7899 | 0.0072659 | 0 | 0 | 0.014532 | 300.0302 | 0.0077872 | 0 | 0 | 0.015574 | 300.1104 | 0.007961 | 0 | 0 | 0.015922 | 300.3507 | 0.0084823 | 0 | 0 | 0.016965 | 300.591 | 0.0090036 | 0 | 0 | 0.018007 | 300.7513 | 0.0093511 | 0 | 0 | 0.018702 | 300.9916 | 0.0098725 | 0 | 0 | 0.019745 | 301.1518 | 0.01022 | 0 | 0 | 0.02044 | 301.3121 | 0.010568 | 0 | 0 | 0.021135
2017-12-22 18:00 | 278.5321 | 0.83019 |  | 292.4768 | 0 | 0 | 0 | 0 | 300.6957 | 0.0092305 | 0 | 0 | 0.018461 | 307.4202 | 0.023816 | 0 | 0 | 0.047632 | 307.6693 | 0.024356 | 0 | 0 | 0.048713 | 307.8353 | 0.024716 | 0 | 0 | 0.049433 | 308.0844 | 0.025257 | 0 | 0 | 0.050513 | 308.3334 | 0.025797 | 0 | 0 | 0.051594 | 308.5825 | 0.026337 | 0 | 0 | 0.052674 | 308.9146 | 0.027057 | 0 | 0 | 0.054115 | 309.1636 | 0.027598 | 0 | 0 | 0.055195 | 309.3297 | 0.027958 | 0 | 0 | 0.055915 | 309.5787 | 0.028498 | 0 | 0 | 0.056996 | 309.7448 | 0.028858 | 0 | 0 | 0.057716 | 309.9938 | 0.029398 | 0 | 0 | 0.058796 | 310.2429 | 0.029938 | 0 | 0 | 0.059877 | 310.4089 | 0.030299 | 0 | 0 | 0.060597 | 310.658 | 0.030839 | 0 | 0 | 0.061678 | 310.907 | 0.031379 | 0 | 0 | 0.062758 | 310.9901 | 0.031559 | 0 | 0 | 0.063118 | 311.2391 | 0.032099 | 0 | 0 | 0.064199 | 311.4882 | 0.032639 | 0 | 0 | 0.065279 | 311.6542 | 0.033 | 0 | 0 | 0.065999 | 311.9033 | 0.03354 | 0 | 0 | 0.06708 | 312.0693 | 0.0339 | 0 | 0 | 0.0678 | 312.2353 | 0.03426 | 0 | 0 | 0.06852
2017-12-22 19:00 | 283.2192 | 0.84416 |  | 297.3985 | 0.0020789 | 0 | 0 | 0.0041579 | 305.7557 | 0.020206 | 0 | 0 | 0.040411 | 312.5934 | 0.035037 | 0 | 0 | 0.070073 | 312.8467 | 0.035586 | 0 | 0 | 0.071172 | 313.0155 | 0.035952 | 0 | 0 | 0.071904 | 313.2687 | 0.036502 | 0 | 0 | 0.073003 | 313.522 | 0.037051 | 0 | 0 | 0.074102 | 313.7752 | 0.0376 | 0 | 0 | 0.0752 | 314.1129 | 0.038333 | 0 | 0 | 0.076665 | 314.3661 | 0.038882 | 0 | 0 | 0.077764 | 314.535 | 0.039248 | 0 | 0 | 0.078496 | 314.7882 | 0.039797 | 0 | 0 | 0.079595 | 314.9571 | 0.040164 | 0 | 0 | 0.080327 | 315.2103 | 0.040713 | 0 | 0 | 0.081426 | 315.4636 | 0.041262 | 0 | 0 | 0.082524 | 315.6324 | 0.041628 | 0 | 0 | 0.083257 | 315.8856 | 0.042178 | 0 | 0 | 0.084355 | 316.1389 | 0.042727 | 0 | 0 | 0.085454 | 316.2233 | 0.04291 | 0 | 0 | 0.08582 | 316.4766 | 0.043459 | 0 | 0 | 0.086919 | 316.7298 | 0.044009 | 0 | 0 | 0.088017 | 316.8986 | 0.044375 | 0 | 0 | 0.08875 | 317.1519 | 0.044924 | 0 | 0 | 0.089848 | 317.3207 | 0.04529 | 0 | 0 | 0.090581 | 317.4895 | 0.045656 | 0 | 0 | 0.091313
2017-12-22 20:00 | 283.5846 | 0.84525 |  | 297.7822 | 0.0029112 | 0 | 0 | 0.0058224 | 306.1502 | 0.021061 | 0 | 0 | 0.042123 | 312.9967 | 0.035912 | 0 | 0 | 0.071823 | 313.2503 | 0.036462 | 0 | 0 | 0.072923 | 313.4193 | 0.036828 | 0 | 0 | 0.073656 | 313.6729 | 0.037378 | 0 | 0 | 0.074756 | 313.9265 | 0.037928 | 0 | 0 | 0.075856 | 314.1801 | 0.038478 | 0 | 0 | 0.076956 | 314.5182 | 0.039212 | 0 | 0 | 0.078423 | 314.7717 | 0.039762 | 0 | 0 | 0.079523 | 314.9408 | 0.040128 | 0 | 0 | 0.080256 | 315.1944 | 0.040678 | 0 | 0 | 0.081356 | 315.3634 | 0.041045 | 0 | 0 | 0.08209 | 315.617 | 0.041595 | 0 | 0 | 0.08319 | 315.8706 | 0.042145 | 0 | 0 | 0.08429 | 316.0396 | 0.042512 | 0 | 0 | 0.085023 | 316.2932 | 0.043062 | 0 | 0 | 0.086123 | 316.5468 | 0.043612 | 0 | 0 | 0.087223 | 316.6313 | 0.043795 | 0 | 0 | 0.08759 | 316.8849 | 0.044345 | 0 | 0 | 0.08869 | 317.1384 | 0.044895 | 0 | 0 | 0.08979 | 317.3075 | 0.045262 | 0 | 0 | 0.090523 | 317.5611 | 0.045812 | 0 | 0 | 0.091623 | 317.7301 | 0.046178 | 0 | 0 | 0.092357 | 317.8992 | 0.046545 | 0 | 0 | 0.09309
2017-12-22 21:00 | 285.2702 | 0.85028 |  | 299.5522 | 0.0067503 | 0 | 0 | 0.013501 | 307.9699 | 0.025008 | 0 | 0 | 0.050017 | 314.8572 | 0.039947 | 0 | 0 | 0.079894 | 315.1122 | 0.0405 | 0 | 0 | 0.081 | 315.2823 | 0.040869 | 0 | 0 | 0.081738 | 315.5374 | 0.041422 | 0 | 0 | 0.082844 | 315.7925 | 0.041975 | 0 | 0 | 0.083951 | 316.0475 | 0.042529 | 0 | 0 | 0.085057 | 316.3876 | 0.043266 | 0 | 0 | 0.086533 | 316.6427 | 0.04382 | 0 | 0 | 0.087639 | 316.8128 | 0.044189 | 0 | 0 | 0.088377 | 317.0679 | 0.044742 | 0 | 0 | 0.089484 | 317.2379 | 0.045111 | 0 | 0 | 0.090221 | 317.493 | 0.045664 | 0 | 0 | 0.091328 | 317.7481 | 0.046217 | 0 | 0 | 0.092434 | 317.9181 | 0.046586 | 0 | 0 | 0.093172 | 318.1732 | 0.047139 | 0 | 0 | 0.094279 | 318.4283 | 0.047693 | 0 | 0 | 0.095385 | 318.5133 | 0.047877 | 0 | 0 | 0.095754 | 318.7684 | 0.04843 | 0 | 0 | 0.096861 | 319.0235 | 0.048984 | 0 | 0 | 0.097967 | 319.1936 | 0.049352 | 0 | 0 | 0.098705 | 319.4486 | 0.049906 | 0 | 0 | 0.099811 | 319.6187 | 0.050275 | 0 | 0 | 0.10055 | 319.7888 | 0.050643 | 0 | 0 | 0.10129
2017-12-22 22:00 | 291.4265 | 0.86863 |  | 306.0167 | 0.020772 | 0 | 0 | 0.041544 | 314.6161 | 0.039424 | 0 | 0 | 0.078848 | 321.6519 | 0.054685 | 0 | 0 | 0.10937 | 321.9125 | 0.05525 | 0 | 0 | 0.1105 | 322.0863 | 0.055627 | 0 | 0 | 0.11125 | 322.3468 | 0.056192 | 0 | 0 | 0.11238 | 322.6074 | 0.056757 | 0 | 0 | 0.11351 | 322.868 | 0.057322 | 0 | 0 | 0.11464 | 323.2155 | 0.058076 | 0 | 0 | 0.11615 | 323.4761 | 0.058641 | 0 | 0 | 0.11728 | 323.6498 | 0.059018 | 0 | 0 | 0.11804 | 323.9104 | 0.059583 | 0 | 0 | 0.11917 | 324.0841 | 0.05996 | 0 | 0 | 0.11992 | 324.3447 | 0.060525 | 0 | 0 | 0.12105 | 324.6053 | 0.06109 | 0 | 0 | 0.12218 | 324.779 | 0.061467 | 0 | 0 | 0.12293 | 325.0396 | 0.062032 | 0 | 0 | 0.12406 | 325.3002 | 0.062598 | 0 | 0 | 0.1252 | 325.387 | 0.062786 | 0 | 0 | 0.12557 | 325.6476 | 0.063351 | 0 | 0 | 0.1267 | 325.9082 | 0.063917 | 0 | 0 | 0.12783 | 326.0819 | 0.064293 | 0 | 0 | 0.12859 | 326.3425 | 0.064859 | 0 | 0 | 0.12972 | 326.5162 | 0.065235 | 0 | 0 | 0.13047 | 326.69 | 0.065612 | 0 | 0 | 0.13122
2017-12-22 23:00 | 289.5962 | 0.86317 |  | 304.0948 | 0.016603 | 0 | 0 | 0.033206 | 312.6402 | 0.035138 | 0 | 0 | 0.070276 | 319.6318 | 0.050303 | 0 | 0 | 0.10061 | 319.8908 | 0.050865 | 0 | 0 | 0.10173 | 320.0634 | 0.051239 | 0 | 0 | 0.10248 | 320.3224 | 0.051801 | 0 | 0 | 0.1036 | 320.5813 | 0.052363 | 0 | 0 | 0.10473 | 320.8403 | 0.052924 | 0 | 0 | 0.10585 | 321.1855 | 0.053673 | 0 | 0 | 0.10735 | 321.4445 | 0.054235 | 0 | 0 | 0.10847 | 321.6171 | 0.054609 | 0 | 0 | 0.10922 | 321.8761 | 0.055171 | 0 | 0 | 0.11034 | 322.0487 | 0.055545 | 0 | 0 | 0.11109 | 322.3077 | 0.056107 | 0 | 0 | 0.11221 | 322.5666 | 0.056669 | 0 | 0 | 0.11334 | 322.7392 | 0.057043 | 0 | 0 | 0.11409 | 322.9982 | 0.057605 | 0 | 0 | 0.11521 | 323.2571 | 0.058166 | 0 | 0 | 0.11633 | 323.3435 | 0.058354 | 0 | 0 | 0.11671 | 323.6024 | 0.058915 | 0 | 0 | 0.11783 | 323.8614 | 0.059477 | 0 | 0 | 0.11895 | 324.034 | 0.059851 | 0 | 0 | 0.1197 | 324.2929 | 0.060413 | 0 | 0 | 0.12083 | 324.4656 | 0.060787 | 0 | 0 | 0.12157 | 324.6382 | 0.061162 | 0 | 0 | 0.12232
2017-12-23 | 292.2047 | 0.87094 |  | 306.8339 | 0.022544 | 0 | 0 | 0.045089 | 315.4562 | 0.041246 | 0 | 0 | 0.082492 | 322.5109 | 0.056548 | 0 | 0 | 0.1131 | 322.7722 | 0.057114 | 0 | 0 | 0.11423 | 322.9463 | 0.057492 | 0 | 0 | 0.11498 | 323.2076 | 0.058059 | 0 | 0 | 0.11612 | 323.4689 | 0.058626 | 0 | 0 | 0.11725 | 323.7302 | 0.059192 | 0 | 0 | 0.11838 | 324.0786 | 0.059948 | 0 | 0 | 0.1199 | 324.3399 | 0.060515 | 0 | 0 | 0.12103 | 324.514 | 0.060893 | 0 | 0 | 0.12179 | 324.7753 | 0.061459 | 0 | 0 | 0.12292 | 324.9495 | 0.061837 | 0 | 0 | 0.12367 | 325.2108 | 0.062404 | 0 | 0 | 0.12481 | 325.4721 | 0.062971 | 0 | 0 | 0.12594 | 325.6463 | 0.063348 | 0 | 0 | 0.1267 | 325.9076 | 0.063915 | 0 | 0 | 0.12783 | 326.1688 | 0.064482 | 0 | 0 | 0.12896 | 326.2559 | 0.064671 | 0 | 0 | 0.12934 | 326.5172 | 0.065237 | 0 | 0 | 0.13047 | 326.7785 | 0.065804 | 0 | 0 | 0.13161 | 326.9527 | 0.066182 | 0 | 0 | 0.13236 | 327.214 | 0.066749 | 0 | 0 | 0.1335 | 327.3882 | 0.067127 | 0 | 0 | 0.13425 | 327.5624 | 0.067504 | 0 | 0 | 0.13501
2017-12-23 01:00 | 292.6362 | 0.87223 |  | 307.2869 | 0.023527 | 0 | 0 | 0.047054 | 315.922 | 0.042256 | 0 | 0 | 0.084513 | 322.9871 | 0.057581 | 0 | 0 | 0.11516 | 323.2487 | 0.058148 | 0 | 0 | 0.1163 | 323.4232 | 0.058527 | 0 | 0 | 0.11705 | 323.6848 | 0.059094 | 0 | 0 | 0.11819 | 323.9465 | 0.059662 | 0 | 0 | 0.11932 | 324.2082 | 0.060229 | 0 | 0 | 0.12046 | 324.5571 | 0.060986 | 0 | 0 | 0.12197 | 324.8187 | 0.061553 | 0 | 0 | 0.12311 | 324.9932 | 0.061932 | 0 | 0 | 0.12386 | 325.2549 | 0.062499 | 0 | 0 | 0.125 | 325.4293 | 0.062878 | 0 | 0 | 0.12576 | 325.691 | 0.063445 | 0 | 0 | 0.12689 | 325.9526 | 0.064013 | 0 | 0 | 0.12803 | 326.1271 | 0.064391 | 0 | 0 | 0.12878 | 326.3888 | 0.064959 | 0 | 0 | 0.12992 | 326.6504 | 0.065526 | 0 | 0 | 0.13105 | 326.7377 | 0.065716 | 0 | 0 | 0.13143 | 326.9993 | 0.066283 | 0 | 0 | 0.13257 | 327.261 | 0.066851 | 0 | 0 | 0.1337 | 327.4354 | 0.067229 | 0 | 0 | 0.13446 | 327.6971 | 0.067797 | 0 | 0 | 0.13559 | 327.8716 | 0.068175 | 0 | 0 | 0.13635 | 328.046 | 0.068553 | 0 | 0 | 0.13711
2017-12-23 02:00 | 295.5615 | 0.88095 |  | 310.3587 | 0.03019 | 0 | 0 | 0.060379 | 319.0801 | 0.049106 | 0 | 0 | 0.098213 | 326.2158 | 0.064584 | 0 | 0 | 0.12917 | 326.4801 | 0.065157 | 0 | 0 | 0.13031 | 326.6563 | 0.065539 | 0 | 0 | 0.13108 | 326.9206 | 0.066112 | 0 | 0 | 0.13222 | 327.1849 | 0.066686 | 0 | 0 | 0.13337 | 327.4491 | 0.067259 | 0 | 0 | 0.13452 | 327.8015 | 0.068023 | 0 | 0 | 0.13605 | 328.0658 | 0.068596 | 0 | 0 | 0.13719 | 328.242 | 0.068979 | 0 | 0 | 0.13796 | 328.5063 | 0.069552 | 0 | 0 | 0.1391 | 328.6825 | 0.069934 | 0 | 0 | 0.13987 | 328.9468 | 0.070507 | 0 | 0 | 0.14101 | 329.211 | 0.07108 | 0 | 0 | 0.14216 | 329.3872 | 0.071463 | 0 | 0 | 0.14293 | 329.6515 | 0.072036 | 0 | 0 | 0.14407 | 329.9158 | 0.072609 | 0 | 0 | 0.14522 | 330.0039 | 0.0728 | 0 | 0 | 0.1456 | 330.2682 | 0.073373 | 0 | 0 | 0.14675 | 330.5325 | 0.073947 | 0 | 0 | 0.14789 | 330.7087 | 0.074329 | 0 | 0 | 0.14866 | 330.9729 | 0.074902 | 0 | 0 | 0.1498 | 331.1491 | 0.075284 | 0 | 0 | 0.15057 | 331.3253 | 0.075666 | 0 | 0 | 0.15133
2017-12-23 03:00 | 296.4103 | 0.88348 |  | 311.25 | 0.032123 | 0 | 0 | 0.064246 | 319.9964 | 0.051094 | 0 | 0 | 0.10219 | 327.1526 | 0.066616 | 0 | 0 | 0.13323 | 327.4176 | 0.067191 | 0 | 0 | 0.13438 | 327.5943 | 0.067574 | 0 | 0 | 0.13515 | 327.8594 | 0.068149 | 0 | 0 | 0.1363 | 328.1244 | 0.068724 | 0 | 0 | 0.13745 | 328.3895 | 0.069298 | 0 | 0 | 0.1386 | 328.7429 | 0.070065 | 0 | 0 | 0.14013 | 329.0079 | 0.07064 | 0 | 0 | 0.14128 | 329.1846 | 0.071023 | 0 | 0 | 0.14205 | 329.4496 | 0.071598 | 0 | 0 | 0.1432 | 329.6263 | 0.071981 | 0 | 0 | 0.14396 | 329.8914 | 0.072556 | 0 | 0 | 0.14511 | 330.1564 | 0.073131 | 0 | 0 | 0.14626 | 330.3331 | 0.073514 | 0 | 0 | 0.14703 | 330.5982 | 0.074089 | 0 | 0 | 0.14818 | 330.8632 | 0.074664 | 0 | 0 | 0.14933 | 330.9516 | 0.074856 | 0 | 0 | 0.14971 | 331.2166 | 0.07543 | 0 | 0 | 0.15086 | 331.4817 | 0.076005 | 0 | 0 | 0.15201 | 331.6583 | 0.076389 | 0 | 0 | 0.15278 | 331.9234 | 0.076963 | 0 | 0 | 0.15393 | 332.1001 | 0.077347 | 0 | 0 | 0.15469 | 332.2768 | 0.07773 | 0 | 0 | 0.15546
2017-12-23 04:00 | 294.1134 | 0.87663 |  | 308.8381 | 0.026891 | 0 | 0 | 0.053783 | 317.5167 | 0.045715 | 0 | 0 | 0.091431 | 324.6175 | 0.061117 | 0 | 0 | 0.12223 | 324.8805 | 0.061687 | 0 | 0 | 0.12337 | 325.0558 | 0.062068 | 0 | 0 | 0.12414 | 325.3188 | 0.062638 | 0 | 0 | 0.12528 | 325.5818 | 0.063209 | 0 | 0 | 0.12642 | 325.8448 | 0.063779 | 0 | 0 | 0.12756 | 326.1954 | 0.06454 | 0 | 0 | 0.12908 | 326.4584 | 0.06511 | 0 | 0 | 0.13022 | 326.6337 | 0.06549 | 0 | 0 | 0.13098 | 326.8967 | 0.066061 | 0 | 0 | 0.13212 | 327.0721 | 0.066441 | 0 | 0 | 0.13288 | 327.335 | 0.067011 | 0 | 0 | 0.13402 | 327.598 | 0.067582 | 0 | 0 | 0.13516 | 327.7734 | 0.067962 | 0 | 0 | 0.13592 | 328.0363 | 0.068532 | 0 | 0 | 0.13706 | 328.2993 | 0.069103 | 0 | 0 | 0.13821 | 328.387 | 0.069293 | 0 | 0 | 0.13859 | 328.65 | 0.069863 | 0 | 0 | 0.13973 | 328.913 | 0.070434 | 0 | 0 | 0.14087 | 329.0883 | 0.070814 | 0 | 0 | 0.14163 | 329.3513 | 0.071385 | 0 | 0 | 0.14277 | 329.5266 | 0.071765 | 0 | 0 | 0.14353 | 329.702 | 0.072145 | 0 | 0 | 0.14429
2017-12-23 05:00 | 296.4905 | 0.88372 |  | 311.3342 | 0.032305 | 0 | 0 | 0.064611 | 320.083 | 0.051282 | 0 | 0 | 0.10256 | 327.2411 | 0.066808 | 0 | 0 | 0.13362 | 327.5062 | 0.067383 | 0 | 0 | 0.13477 | 327.683 | 0.067766 | 0 | 0 | 0.13553 | 327.9481 | 0.068341 | 0 | 0 | 0.13668 | 328.2132 | 0.068916 | 0 | 0 | 0.13783 | 328.4783 | 0.069491 | 0 | 0 | 0.13898 | 328.8318 | 0.070258 | 0 | 0 | 0.14052 | 329.0969 | 0.070833 | 0 | 0 | 0.14167 | 329.2737 | 0.071216 | 0 | 0 | 0.14243 | 329.5388 | 0.071791 | 0 | 0 | 0.14358 | 329.7155 | 0.072175 | 0 | 0 | 0.14435 | 329.9807 | 0.07275 | 0 | 0 | 0.1455 | 330.2458 | 0.073325 | 0 | 0 | 0.14665 | 330.4225 | 0.073708 | 0 | 0 | 0.14742 | 330.6876 | 0.074283 | 0 | 0 | 0.14857 | 330.9527 | 0.074858 | 0 | 0 | 0.14972 | 331.0411 | 0.07505 | 0 | 0 | 0.1501 | 331.3062 | 0.075625 | 0 | 0 | 0.15125 | 331.5713 | 0.0762 | 0 | 0 | 0.1524 | 331.7481 | 0.076583 | 0 | 0 | 0.15317 | 332.0132 | 0.077158 | 0 | 0 | 0.15432 | 332.19 | 0.077542 | 0 | 0 | 0.15508 | 332.3667 | 0.077925 | 0 | 0 | 0.15585
2017-12-23 06:00 | 297.2884 | 0.8861 |  | 312.1721 | 0.034123 | 0 | 0 | 0.068246 | 320.9444 | 0.05315 | 0 | 0 | 0.1063 | 328.1218 | 0.068718 | 0 | 0 | 0.13744 | 328.3876 | 0.069294 | 0 | 0 | 0.13859 | 328.5649 | 0.069679 | 0 | 0 | 0.13936 | 328.8307 | 0.070255 | 0 | 0 | 0.14051 | 329.0965 | 0.070832 | 0 | 0 | 0.14166 | 329.3623 | 0.071409 | 0 | 0 | 0.14282 | 329.7168 | 0.072177 | 0 | 0 | 0.14435 | 329.9826 | 0.072754 | 0 | 0 | 0.14551 | 330.1598 | 0.073138 | 0 | 0 | 0.14628 | 330.4257 | 0.073715 | 0 | 0 | 0.14743 | 330.6029 | 0.074099 | 0 | 0 | 0.1482 | 330.8687 | 0.074676 | 0 | 0 | 0.14935 | 331.1345 | 0.075252 | 0 | 0 | 0.1505 | 331.3118 | 0.075637 | 0 | 0 | 0.15127 | 331.5776 | 0.076213 | 0 | 0 | 0.15243 | 331.8434 | 0.07679 | 0 | 0 | 0.15358 | 331.932 | 0.076982 | 0 | 0 | 0.15396 | 332.1979 | 0.077559 | 0 | 0 | 0.15512 | 332.4637 | 0.078135 | 0 | 0 | 0.15627 | 332.6409 | 0.07852 | 0 | 0 | 0.15704 | 332.9067 | 0.079096 | 0 | 0 | 0.15819 | 333.084 | 0.079481 | 0 | 0 | 0.15896 | 333.2612 | 0.079865 | 0 | 0 | 0.15973
2017-12-23 07:00 | 297.1881 | 0.8858 |  | 312.0667 | 0.033894 | 0 | 0 | 0.067789 | 320.8361 | 0.052915 | 0 | 0 | 0.10583 | 328.0111 | 0.068478 | 0 | 0 | 0.13696 | 328.2768 | 0.069054 | 0 | 0 | 0.13811 | 328.454 | 0.069438 | 0 | 0 | 0.13888 | 328.7197 | 0.070015 | 0 | 0 | 0.14003 | 328.9855 | 0.070591 | 0 | 0 | 0.14118 | 329.2512 | 0.071168 | 0 | 0 | 0.14234 | 329.6055 | 0.071936 | 0 | 0 | 0.14387 | 329.8713 | 0.072512 | 0 | 0 | 0.14502 | 330.0484 | 0.072897 | 0 | 0 | 0.14579 | 330.3142 | 0.073473 | 0 | 0 | 0.14695 | 330.4913 | 0.073857 | 0 | 0 | 0.14771 | 330.7571 | 0.074434 | 0 | 0 | 0.14887 | 331.0228 | 0.07501 | 0 | 0 | 0.15002 | 331.2 | 0.075394 | 0 | 0 | 0.15079 | 331.4657 | 0.075971 | 0 | 0 | 0.15194 | 331.7315 | 0.076547 | 0 | 0 | 0.15309 | 331.82 | 0.076739 | 0 | 0 | 0.15348 | 332.0858 | 0.077316 | 0 | 0 | 0.15463 | 332.3515 | 0.077892 | 0 | 0 | 0.15578 | 332.5287 | 0.078276 | 0 | 0 | 0.15655 | 332.7944 | 0.078853 | 0 | 0 | 0.15771 | 332.9716 | 0.079237 | 0 | 0 | 0.15847 | 333.1487 | 0.079621 | 0 | 0 | 0.15924
2017-12-23 08:00 | 289.5212 | 0.86295 |  | 304.016 | 0.016432 | 0 | 0 | 0.032865 | 312.5592 | 0.034963 | 0 | 0 | 0.069925 | 319.5491 | 0.050124 | 0 | 0 | 0.10025 | 319.8079 | 0.050685 | 0 | 0 | 0.10137 | 319.9805 | 0.051059 | 0 | 0 | 0.10212 | 320.2394 | 0.051621 | 0 | 0 | 0.10324 | 320.4983 | 0.052182 | 0 | 0 | 0.10436 | 320.7572 | 0.052744 | 0 | 0 | 0.10549 | 321.1024 | 0.053493 | 0 | 0 | 0.10699 | 321.3612 | 0.054054 | 0 | 0 | 0.10811 | 321.5338 | 0.054429 | 0 | 0 | 0.10886 | 321.7927 | 0.05499 | 0 | 0 | 0.10998 | 321.9653 | 0.055364 | 0 | 0 | 0.11073 | 322.2242 | 0.055926 | 0 | 0 | 0.11185 | 322.4831 | 0.056487 | 0 | 0 | 0.11297 | 322.6557 | 0.056862 | 0 | 0 | 0.11372 | 322.9145 | 0.057423 | 0 | 0 | 0.11485 | 323.1734 | 0.057985 | 0 | 0 | 0.11597 | 323.2597 | 0.058172 | 0 | 0 | 0.11634 | 323.5186 | 0.058734 | 0 | 0 | 0.11747 | 323.7775 | 0.059295 | 0 | 0 | 0.11859 | 323.9501 | 0.059669 | 0 | 0 | 0.11934 | 324.209 | 0.060231 | 0 | 0 | 0.12046 | 324.3816 | 0.060605 | 0 | 0 | 0.12121 | 324.5541 | 0.06098 | 0 | 0 | 0.12196
2017-12-23 09:00 | 275.8897 | 0.82232 |  | 289.702 | 0 | 0 | 0 | 0 | 297.8429 | 0.003043 | 0 | 0 | 0.0060859 | 304.5037 | 0.01749 | 0 | 0 | 0.03498 | 304.7504 | 0.018025 | 0 | 0 | 0.03605 | 304.9149 | 0.018382 | 0 | 0 | 0.036764 | 305.1615 | 0.018917 | 0 | 0 | 0.037834 | 305.4082 | 0.019452 | 0 | 0 | 0.038904 | 305.6549 | 0.019987 | 0 | 0 | 0.039974 | 305.9839 | 0.020701 | 0 | 0 | 0.041401 | 306.2306 | 0.021236 | 0 | 0 | 0.042471 | 306.395 | 0.021592 | 0 | 0 | 0.043185 | 306.6417 | 0.022128 | 0 | 0 | 0.044255 | 306.8062 | 0.022484 | 0 | 0 | 0.044968 | 307.0529 | 0.023019 | 0 | 0 | 0.046039 | 307.2996 | 0.023554 | 0 | 0 | 0.047109 | 307.464 | 0.023911 | 0 | 0 | 0.047822 | 307.7107 | 0.024446 | 0 | 0 | 0.048892 | 307.9574 | 0.024981 | 0 | 0 | 0.049963 | 308.0397 | 0.02516 | 0 | 0 | 0.050319 | 308.2864 | 0.025695 | 0 | 0 | 0.051389 | 308.533 | 0.02623 | 0 | 0 | 0.05246 | 308.6975 | 0.026587 | 0 | 0 | 0.053173 | 308.9442 | 0.027122 | 0 | 0 | 0.054243 | 309.1087 | 0.027478 | 0 | 0 | 0.054957 | 309.2731 | 0.027835 | 0 | 0 | 0.05567
2017-12-23 10:00 | 283.7688 | 0.8458 |  | 297.9756 | 0.0033307 | 0 | 0 | 0.0066615 | 306.349 | 0.021493 | 0 | 0 | 0.042985 | 313.2 | 0.036353 | 0 | 0 | 0.072705 | 313.4538 | 0.036903 | 0 | 0 | 0.073806 | 313.6229 | 0.03727 | 0 | 0 | 0.07454 | 313.8767 | 0.03782 | 0 | 0 | 0.07564 | 314.1304 | 0.03837 | 0 | 0 | 0.076741 | 314.3841 | 0.038921 | 0 | 0 | 0.077842 | 314.7225 | 0.039655 | 0 | 0 | 0.079309 | 314.9762 | 0.040205 | 0 | 0 | 0.08041 | 315.1454 | 0.040572 | 0 | 0 | 0.081144 | 315.3991 | 0.041122 | 0 | 0 | 0.082245 | 315.5683 | 0.041489 | 0 | 0 | 0.082978 | 315.822 | 0.04204 | 0 | 0 | 0.084079 | 316.0758 | 0.04259 | 0 | 0 | 0.08518 | 316.2449 | 0.042957 | 0 | 0 | 0.085914 | 316.4987 | 0.043507 | 0 | 0 | 0.087014 | 316.7524 | 0.044058 | 0 | 0 | 0.088115 | 316.837 | 0.044241 | 0 | 0 | 0.088482 | 317.0907 | 0.044791 | 0 | 0 | 0.089583 | 317.3445 | 0.045342 | 0 | 0 | 0.090684 | 317.5136 | 0.045709 | 0 | 0 | 0.091417 | 317.7674 | 0.046259 | 0 | 0 | 0.092518 | 317.9365 | 0.046626 | 0 | 0 | 0.093252 | 318.1057 | 0.046993 | 0 | 0 | 0.093986
2017-12-23 11:00 | 283.7999 | 0.84589 |  | 298.0082 | 0.0034015 | 0 | 0 | 0.0068029 | 306.3826 | 0.021565 | 0 | 0 | 0.043131 | 313.2343 | 0.036427 | 0 | 0 | 0.072854 | 313.4881 | 0.036977 | 0 | 0 | 0.073954 | 313.6572 | 0.037344 | 0 | 0 | 0.074688 | 313.911 | 0.037895 | 0 | 0 | 0.075789 | 314.1648 | 0.038445 | 0 | 0 | 0.07689 | 314.4185 | 0.038995 | 0 | 0 | 0.077991 | 314.7569 | 0.039729 | 0 | 0 | 0.079459 | 315.0107 | 0.04028 | 0 | 0 | 0.08056 | 315.1798 | 0.040647 | 0 | 0 | 0.081293 | 315.4336 | 0.041197 | 0 | 0 | 0.082394 | 315.6028 | 0.041564 | 0 | 0 | 0.083128 | 315.8566 | 0.042115 | 0 | 0 | 0.084229 | 316.1103 | 0.042665 | 0 | 0 | 0.08533 | 316.2795 | 0.043032 | 0 | 0 | 0.086064 | 316.5333 | 0.043582 | 0 | 0 | 0.087165 | 316.787 | 0.044133 | 0 | 0 | 0.088265 | 316.8716 | 0.044316 | 0 | 0 | 0.088632 | 317.1254 | 0.044867 | 0 | 0 | 0.089733 | 317.3792 | 0.045417 | 0 | 0 | 0.090834 | 317.5483 | 0.045784 | 0 | 0 | 0.091568 | 317.8021 | 0.046334 | 0 | 0 | 0.092669 | 317.9713 | 0.046701 | 0 | 0 | 0.093403 | 318.1405 | 0.047068 | 0 | 0 | 0.094137
2017-12-23 12:00 | 278.6025 | 0.8304 |  | 292.5507 | 0 | 0 | 0 | 0 | 300.7717 | 0.0093954 | 0 | 0 | 0.018791 | 307.4979 | 0.023985 | 0 | 0 | 0.047969 | 307.747 | 0.024525 | 0 | 0 | 0.04905 | 307.9131 | 0.024885 | 0 | 0 | 0.04977 | 308.1622 | 0.025426 | 0 | 0 | 0.050851 | 308.4114 | 0.025966 | 0 | 0 | 0.051932 | 308.6605 | 0.026506 | 0 | 0 | 0.053012 | 308.9926 | 0.027227 | 0 | 0 | 0.054453 | 309.2418 | 0.027767 | 0 | 0 | 0.055534 | 309.4078 | 0.028127 | 0 | 0 | 0.056254 | 309.657 | 0.028668 | 0 | 0 | 0.057335 | 309.823 | 0.029028 | 0 | 0 | 0.058056 | 310.0722 | 0.029568 | 0 | 0 | 0.059136 | 310.3213 | 0.030108 | 0 | 0 | 0.060217 | 310.4874 | 0.030469 | 0 | 0 | 0.060937 | 310.7365 | 0.031009 | 0 | 0 | 0.062018 | 310.9856 | 0.031549 | 0 | 0 | 0.063099 | 311.0686 | 0.03173 | 0 | 0 | 0.063459 | 311.3178 | 0.03227 | 0 | 0 | 0.06454 | 311.5669 | 0.03281 | 0 | 0 | 0.06562 | 311.733 | 0.03317 | 0 | 0 | 0.066341 | 311.9821 | 0.033711 | 0 | 0 | 0.067422 | 312.1482 | 0.034071 | 0 | 0 | 0.068142 | 312.3142 | 0.034431 | 0 | 0 | 0.068862
2017-12-23 13:00 | 283.437 | 0.84481 |  | 297.6272 | 0.002575 | 0 | 0 | 0.00515 | 305.9908 | 0.020716 | 0 | 0 | 0.041431 | 312.8338 | 0.035558 | 0 | 0 | 0.071116 | 313.0872 | 0.036108 | 0 | 0 | 0.072216 | 313.2562 | 0.036474 | 0 | 0 | 0.072949 | 313.5096 | 0.037024 | 0 | 0 | 0.074048 | 313.7631 | 0.037574 | 0 | 0 | 0.075148 | 314.0165 | 0.038123 | 0 | 0 | 0.076247 | 314.3545 | 0.038856 | 0 | 0 | 0.077713 | 314.6079 | 0.039406 | 0 | 0 | 0.078812 | 314.7769 | 0.039773 | 0 | 0 | 0.079545 | 315.0303 | 0.040322 | 0 | 0 | 0.080645 | 315.1993 | 0.040689 | 0 | 0 | 0.081378 | 315.4527 | 0.041239 | 0 | 0 | 0.082477 | 315.7062 | 0.041788 | 0 | 0 | 0.083577 | 315.8751 | 0.042155 | 0 | 0 | 0.08431 | 316.1286 | 0.042704 | 0 | 0 | 0.085409 | 316.382 | 0.043254 | 0 | 0 | 0.086508 | 316.4665 | 0.043437 | 0 | 0 | 0.086875 | 316.7199 | 0.043987 | 0 | 0 | 0.087974 | 316.9734 | 0.044537 | 0 | 0 | 0.089074 | 317.1423 | 0.044903 | 0 | 0 | 0.089807 | 317.3958 | 0.045453 | 0 | 0 | 0.090906 | 317.5647 | 0.04582 | 0 | 0 | 0.091639 | 317.7337 | 0.046186 | 0 | 0 | 0.092372
2017-12-23 14:00 | 288.2021 | 0.85901 |  | 302.6309 | 0.013428 | 0 | 0 | 0.026856 | 311.1351 | 0.031874 | 0 | 0 | 0.063748 | 318.0932 | 0.046966 | 0 | 0 | 0.093931 | 318.3509 | 0.047525 | 0 | 0 | 0.095049 | 318.5227 | 0.047897 | 0 | 0 | 0.095795 | 318.7804 | 0.048456 | 0 | 0 | 0.096913 | 319.0381 | 0.049015 | 0 | 0 | 0.09803 | 319.2958 | 0.049574 | 0 | 0 | 0.099148 | 319.6394 | 0.050319 | 0 | 0 | 0.10064 | 319.8971 | 0.050878 | 0 | 0 | 0.10176 | 320.0689 | 0.051251 | 0 | 0 | 0.1025 | 320.3266 | 0.05181 | 0 | 0 | 0.10362 | 320.4984 | 0.052183 | 0 | 0 | 0.10437 | 320.7561 | 0.052742 | 0 | 0 | 0.10548 | 321.0138 | 0.053301 | 0 | 0 | 0.1066 | 321.1856 | 0.053673 | 0 | 0 | 0.10735 | 321.4433 | 0.054232 | 0 | 0 | 0.10846 | 321.701 | 0.054791 | 0 | 0 | 0.10958 | 321.7869 | 0.054977 | 0 | 0 | 0.10995 | 322.0446 | 0.055536 | 0 | 0 | 0.11107 | 322.3023 | 0.056095 | 0 | 0 | 0.11219 | 322.4741 | 0.056468 | 0 | 0 | 0.11294 | 322.7318 | 0.057027 | 0 | 0 | 0.11405 | 322.9037 | 0.0574 | 0 | 0 | 0.1148 | 323.0755 | 0.057772 | 0 | 0 | 0.11554
2017-12-23 15:00 | 288.2998 | 0.85931 |  | 302.7335 | 0.013651 | 0 | 0 | 0.027301 | 311.2406 | 0.032103 | 0 | 0 | 0.064205 | 318.201 | 0.0472 | 0 | 0 | 0.094399 | 318.4588 | 0.047759 | 0 | 0 | 0.095517 | 318.6306 | 0.048132 | 0 | 0 | 0.096263 | 318.8884 | 0.048691 | 0 | 0 | 0.097381 | 319.1462 | 0.04925 | 0 | 0 | 0.0985 | 319.404 | 0.049809 | 0 | 0 | 0.099618 | 319.7477 | 0.050554 | 0 | 0 | 0.10111 | 320.0055 | 0.051114 | 0 | 0 | 0.10223 | 320.1774 | 0.051486 | 0 | 0 | 0.10297 | 320.4352 | 0.052046 | 0 | 0 | 0.10409 | 320.607 | 0.052418 | 0 | 0 | 0.10484 | 320.8648 | 0.052977 | 0 | 0 | 0.10595 | 321.1226 | 0.053537 | 0 | 0 | 0.10707 | 321.2945 | 0.053909 | 0 | 0 | 0.10782 | 321.5523 | 0.054469 | 0 | 0 | 0.10894 | 321.8101 | 0.055028 | 0 | 0 | 0.11006 | 321.896 | 0.055214 | 0 | 0 | 0.11043 | 322.1538 | 0.055773 | 0 | 0 | 0.11155 | 322.4116 | 0.056332 | 0 | 0 | 0.11266 | 322.5835 | 0.056705 | 0 | 0 | 0.11341 | 322.8412 | 0.057264 | 0 | 0 | 0.11453 | 323.0131 | 0.057637 | 0 | 0 | 0.11527 | 323.185 | 0.05801 | 0 | 0 | 0.11602
2017-12-23 16:00 | 285.8575 | 0.85203 |  | 300.1689 | 0.008088 | 0 | 0 | 0.016176 | 308.604 | 0.026384 | 0 | 0 | 0.052767 | 315.5054 | 0.041353 | 0 | 0 | 0.082706 | 315.761 | 0.041907 | 0 | 0 | 0.083814 | 315.9314 | 0.042277 | 0 | 0 | 0.084554 | 316.187 | 0.042831 | 0 | 0 | 0.085663 | 316.4426 | 0.043386 | 0 | 0 | 0.086771 | 316.6982 | 0.04394 | 0 | 0 | 0.08788 | 317.039 | 0.044679 | 0 | 0 | 0.089359 | 317.2946 | 0.045234 | 0 | 0 | 0.090467 | 317.465 | 0.045603 | 0 | 0 | 0.091207 | 317.7207 | 0.046158 | 0 | 0 | 0.092315 | 317.8911 | 0.046527 | 0 | 0 | 0.093055 | 318.1467 | 0.047082 | 0 | 0 | 0.094164 | 318.4023 | 0.047636 | 0 | 0 | 0.095272 | 318.5727 | 0.048006 | 0 | 0 | 0.096012 | 318.8283 | 0.04856 | 0 | 0 | 0.09712 | 319.0839 | 0.049115 | 0 | 0 | 0.098229 | 319.1691 | 0.049299 | 0 | 0 | 0.098599 | 319.4247 | 0.049854 | 0 | 0 | 0.099708 | 319.6803 | 0.050408 | 0 | 0 | 0.10082 | 319.8507 | 0.050778 | 0 | 0 | 0.10156 | 320.1063 | 0.051332 | 0 | 0 | 0.10266 | 320.2767 | 0.051702 | 0 | 0 | 0.1034 | 320.4471 | 0.052071 | 0 | 0 | 0.10414
2017-12-23 17:00 | 296.9712 | 0.88515 |  | 311.839 | 0.0334 | 0 | 0 | 0.066801 | 320.602 | 0.052407 | 0 | 0 | 0.10481 | 327.7717 | 0.067959 | 0 | 0 | 0.13592 | 328.0373 | 0.068534 | 0 | 0 | 0.13707 | 328.2143 | 0.068918 | 0 | 0 | 0.13784 | 328.4798 | 0.069494 | 0 | 0 | 0.13899 | 328.7454 | 0.07007 | 0 | 0 | 0.14014 | 329.0109 | 0.070646 | 0 | 0 | 0.14129 | 329.365 | 0.071414 | 0 | 0 | 0.14283 | 329.6305 | 0.07199 | 0 | 0 | 0.14398 | 329.8076 | 0.072374 | 0 | 0 | 0.14475 | 330.0731 | 0.07295 | 0 | 0 | 0.1459 | 330.2502 | 0.073334 | 0 | 0 | 0.14667 | 330.5157 | 0.07391 | 0 | 0 | 0.14782 | 330.7812 | 0.074486 | 0 | 0 | 0.14897 | 330.9583 | 0.07487 | 0 | 0 | 0.14974 | 331.2238 | 0.075446 | 0 | 0 | 0.15089 | 331.4894 | 0.076022 | 0 | 0 | 0.15204 | 331.5779 | 0.076214 | 0 | 0 | 0.15243 | 331.8434 | 0.07679 | 0 | 0 | 0.15358 | 332.109 | 0.077366 | 0 | 0 | 0.15473 | 332.286 | 0.07775 | 0 | 0 | 0.1555 | 332.5515 | 0.078326 | 0 | 0 | 0.15665 | 332.7286 | 0.07871 | 0 | 0 | 0.15742 | 332.9056 | 0.079094 | 0 | 0 | 0.15819
2017-12-23 18:00 | 296.446 | 0.88359 |  | 311.2875 | 0.032204 | 0 | 0 | 0.064408 | 320.035 | 0.051178 | 0 | 0 | 0.10236 | 327.192 | 0.066701 | 0 | 0 | 0.1334 | 327.4571 | 0.067276 | 0 | 0 | 0.13455 | 327.6338 | 0.067659 | 0 | 0 | 0.13532 | 327.8989 | 0.068234 | 0 | 0 | 0.13647 | 328.164 | 0.068809 | 0 | 0 | 0.13762 | 328.4291 | 0.069384 | 0 | 0 | 0.13877 | 328.7825 | 0.070151 | 0 | 0 | 0.1403 | 329.0476 | 0.070726 | 0 | 0 | 0.14145 | 329.2243 | 0.071109 | 0 | 0 | 0.14222 | 329.4894 | 0.071684 | 0 | 0 | 0.14337 | 329.6661 | 0.072067 | 0 | 0 | 0.14413 | 329.9312 | 0.072642 | 0 | 0 | 0.14528 | 330.1962 | 0.073217 | 0 | 0 | 0.14643 | 330.3729 | 0.073601 | 0 | 0 | 0.1472 | 330.638 | 0.074176 | 0 | 0 | 0.14835 | 330.9031 | 0.07475 | 0 | 0 | 0.1495 | 330.9915 | 0.074942 | 0 | 0 | 0.14988 | 331.2565 | 0.075517 | 0 | 0 | 0.15103 | 331.5216 | 0.076092 | 0 | 0 | 0.15218 | 331.6983 | 0.076475 | 0 | 0 | 0.15295 | 331.9634 | 0.07705 | 0 | 0 | 0.1541 | 332.1401 | 0.077434 | 0 | 0 | 0.15487 | 332.3168 | 0.077817 | 0 | 0 | 0.15563
2017-12-23 19:00 | 299.5234 | 0.89276 |  | 314.5189 | 0.039213 | 0 | 0 | 0.078426 | 323.3572 | 0.058383 | 0 | 0 | 0.11677 | 330.5886 | 0.074068 | 0 | 0 | 0.14814 | 330.8564 | 0.074649 | 0 | 0 | 0.1493 | 331.035 | 0.075036 | 0 | 0 | 0.15007 | 331.3028 | 0.075617 | 0 | 0 | 0.15123 | 331.5706 | 0.076198 | 0 | 0 | 0.1524 | 331.8384 | 0.076779 | 0 | 0 | 0.15356 | 332.1955 | 0.077554 | 0 | 0 | 0.15511 | 332.4634 | 0.078135 | 0 | 0 | 0.15627 | 332.6419 | 0.078522 | 0 | 0 | 0.15704 | 332.9098 | 0.079103 | 0 | 0 | 0.15821 | 333.0883 | 0.07949 | 0 | 0 | 0.15898 | 333.3561 | 0.080071 | 0 | 0 | 0.16014 | 333.624 | 0.080652 | 0 | 0 | 0.1613 | 333.8025 | 0.081039 | 0 | 0 | 0.16208 | 334.0703 | 0.08162 | 0 | 0 | 0.16324 | 334.3382 | 0.082201 | 0 | 0 | 0.1644 | 334.4274 | 0.082395 | 0 | 0 | 0.16479 | 334.6953 | 0.082976 | 0 | 0 | 0.16595 | 334.9631 | 0.083557 | 0 | 0 | 0.16711 | 335.1417 | 0.083944 | 0 | 0 | 0.16789 | 335.4095 | 0.084525 | 0 | 0 | 0.16905 | 335.588 | 0.084912 | 0 | 0 | 0.16982 | 335.7666 | 0.085299 | 0 | 0 | 0.1706
2017-12-23 20:00 | 296.6612 | 0.88423 |  | 311.5135 | 0.032694 | 0 | 0 | 0.065389 | 320.2673 | 0.051682 | 0 | 0 | 0.10336 | 327.4296 | 0.067216 | 0 | 0 | 0.13443 | 327.6949 | 0.067792 | 0 | 0 | 0.13558 | 327.8717 | 0.068175 | 0 | 0 | 0.13635 | 328.137 | 0.068751 | 0 | 0 | 0.1375 | 328.4022 | 0.069326 | 0 | 0 | 0.13865 | 328.6675 | 0.069901 | 0 | 0 | 0.1398 | 329.0212 | 0.070669 | 0 | 0 | 0.14134 | 329.2865 | 0.071244 | 0 | 0 | 0.14249 | 329.4633 | 0.071628 | 0 | 0 | 0.14326 | 329.7286 | 0.072203 | 0 | 0 | 0.14441 | 329.9054 | 0.072587 | 0 | 0 | 0.14517 | 330.1707 | 0.073162 | 0 | 0 | 0.14632 | 330.436 | 0.073737 | 0 | 0 | 0.14747 | 330.6128 | 0.074121 | 0 | 0 | 0.14824 | 330.8781 | 0.074696 | 0 | 0 | 0.14939 | 331.1434 | 0.075272 | 0 | 0 | 0.15054 | 331.2318 | 0.075463 | 0 | 0 | 0.15093 | 331.497 | 0.076039 | 0 | 0 | 0.15208 | 331.7623 | 0.076614 | 0 | 0 | 0.15323 | 331.9392 | 0.076998 | 0 | 0 | 0.154 | 332.2044 | 0.077573 | 0 | 0 | 0.15515 | 332.3813 | 0.077957 | 0 | 0 | 0.15591 | 332.5581 | 0.07834 | 0 | 0 | 0.15668
2017-12-23 21:00 | 296.632 | 0.88414 |  | 311.4828 | 0.032628 | 0 | 0 | 0.065256 | 320.2358 | 0.051613 | 0 | 0 | 0.10323 | 327.3973 | 0.067146 | 0 | 0 | 0.13429 | 327.6626 | 0.067722 | 0 | 0 | 0.13544 | 327.8394 | 0.068105 | 0 | 0 | 0.13621 | 328.1047 | 0.068681 | 0 | 0 | 0.13736 | 328.3699 | 0.069256 | 0 | 0 | 0.13851 | 328.6351 | 0.069831 | 0 | 0 | 0.13966 | 328.9888 | 0.070598 | 0 | 0 | 0.1412 | 329.254 | 0.071174 | 0 | 0 | 0.14235 | 329.4309 | 0.071557 | 0 | 0 | 0.14311 | 329.6961 | 0.072132 | 0 | 0 | 0.14426 | 329.8729 | 0.072516 | 0 | 0 | 0.14503 | 330.1382 | 0.073091 | 0 | 0 | 0.14618 | 330.4034 | 0.073667 | 0 | 0 | 0.14733 | 330.5802 | 0.07405 | 0 | 0 | 0.1481 | 330.8455 | 0.074626 | 0 | 0 | 0.14925 | 331.1107 | 0.075201 | 0 | 0 | 0.1504 | 331.1991 | 0.075393 | 0 | 0 | 0.15079 | 331.4644 | 0.075968 | 0 | 0 | 0.15194 | 331.7296 | 0.076543 | 0 | 0 | 0.15309 | 331.9065 | 0.076927 | 0 | 0 | 0.15385 | 332.1717 | 0.077502 | 0 | 0 | 0.155 | 332.3485 | 0.077886 | 0 | 0 | 0.15577 | 332.5254 | 0.078269 | 0 | 0 | 0.15654
2017-12-23 22:00 | 300.4754 | 0.8956 |  | 315.5186 | 0.041382 | 0 | 0 | 0.082763 | 324.385 | 0.060613 | 0 | 0 | 0.12123 | 331.6393 | 0.076347 | 0 | 0 | 0.15269 | 331.908 | 0.07693 | 0 | 0 | 0.15386 | 332.0871 | 0.077319 | 0 | 0 | 0.15464 | 332.3558 | 0.077901 | 0 | 0 | 0.1558 | 332.6245 | 0.078484 | 0 | 0 | 0.15697 | 332.8932 | 0.079067 | 0 | 0 | 0.15813 | 333.2514 | 0.079844 | 0 | 0 | 0.15969 | 333.5201 | 0.080427 | 0 | 0 | 0.16085 | 333.6992 | 0.080815 | 0 | 0 | 0.16163 | 333.9679 | 0.081398 | 0 | 0 | 0.1628 | 334.147 | 0.081787 | 0 | 0 | 0.16357 | 334.4157 | 0.082369 | 0 | 0 | 0.16474 | 334.6844 | 0.082952 | 0 | 0 | 0.1659 | 334.8635 | 0.083341 | 0 | 0 | 0.16668 | 335.1322 | 0.083923 | 0 | 0 | 0.16785 | 335.4009 | 0.084506 | 0 | 0 | 0.16901 | 335.4904 | 0.0847 | 0 | 0 | 0.1694 | 335.7591 | 0.085283 | 0 | 0 | 0.17057 | 336.0278 | 0.085866 | 0 | 0 | 0.17173 | 336.2069 | 0.086254 | 0 | 0 | 0.17251 | 336.4756 | 0.086837 | 0 | 0 | 0.17367 | 336.6547 | 0.087226 | 0 | 0 | 0.17445 | 336.8338 | 0.087614 | 0 | 0 | 0.17523
2017-12-23 23:00 | 296.8863 | 0.8849 |  | 311.7498 | 0.033207 | 0 | 0 | 0.066414 | 320.5103 | 0.052209 | 0 | 0 | 0.10442 | 327.678 | 0.067755 | 0 | 0 | 0.13551 | 327.9435 | 0.068331 | 0 | 0 | 0.13666 | 328.1205 | 0.068715 | 0 | 0 | 0.13743 | 328.3859 | 0.069291 | 0 | 0 | 0.13858 | 328.6514 | 0.069867 | 0 | 0 | 0.13973 | 328.9169 | 0.070442 | 0 | 0 | 0.14088 | 329.2708 | 0.07121 | 0 | 0 | 0.14242 | 329.5363 | 0.071786 | 0 | 0 | 0.14357 | 329.7133 | 0.07217 | 0 | 0 | 0.14434 | 329.9788 | 0.072746 | 0 | 0 | 0.14549 | 330.1557 | 0.073129 | 0 | 0 | 0.14626 | 330.4212 | 0.073705 | 0 | 0 | 0.14741 | 330.6867 | 0.074281 | 0 | 0 | 0.14856 | 330.8637 | 0.074665 | 0 | 0 | 0.14933 | 331.1291 | 0.075241 | 0 | 0 | 0.15048 | 331.3946 | 0.075817 | 0 | 0 | 0.15163 | 331.4831 | 0.076008 | 0 | 0 | 0.15202 | 331.7486 | 0.076584 | 0 | 0 | 0.15317 | 332.014 | 0.07716 | 0 | 0 | 0.15432 | 332.191 | 0.077544 | 0 | 0 | 0.15509 | 332.4565 | 0.07812 | 0 | 0 | 0.15624 | 332.6335 | 0.078504 | 0 | 0 | 0.15701 | 332.8104 | 0.078887 | 0 | 0 | 0.15777
2017-12-24 | 299.8896 | 0.89385 |  | 314.9035 | 0.040047 | 0 | 0 | 0.080094 | 323.7526 | 0.059241 | 0 | 0 | 0.11848 | 330.9928 | 0.074945 | 0 | 0 | 0.14989 | 331.2609 | 0.075527 | 0 | 0 | 0.15105 | 331.4397 | 0.075914 | 0 | 0 | 0.15183 | 331.7078 | 0.076496 | 0 | 0 | 0.15299 | 331.976 | 0.077078 | 0 | 0 | 0.15416 | 332.2442 | 0.077659 | 0 | 0 | 0.15532 | 332.6017 | 0.078435 | 0 | 0 | 0.15687 | 332.8699 | 0.079016 | 0 | 0 | 0.15803 | 333.0486 | 0.079404 | 0 | 0 | 0.15881 | 333.3168 | 0.079986 | 0 | 0 | 0.15997 | 333.4955 | 0.080373 | 0 | 0 | 0.16075 | 333.7637 | 0.080955 | 0 | 0 | 0.16191 | 334.0319 | 0.081537 | 0 | 0 | 0.16307 | 334.2106 | 0.081924 | 0 | 0 | 0.16385 | 334.4788 | 0.082506 | 0 | 0 | 0.16501 | 334.7469 | 0.083088 | 0 | 0 | 0.16618 | 334.8363 | 0.083282 | 0 | 0 | 0.16656 | 335.1045 | 0.083863 | 0 | 0 | 0.16773 | 335.3726 | 0.084445 | 0 | 0 | 0.16889 | 335.5514 | 0.084833 | 0 | 0 | 0.16967 | 335.8196 | 0.085414 | 0 | 0 | 0.17083 | 335.9983 | 0.085802 | 0 | 0 | 0.1716 | 336.1771 | 0.08619 | 0 | 0 | 0.17238
2017-12-24 01:00 | 293.04 | 0.87343 |  | 307.7109 | 0.024447 | 0 | 0 | 0.048893 | 316.3579 | 0.043202 | 0 | 0 | 0.086404 | 323.4328 | 0.058547 | 0 | 0 | 0.11709 | 323.6948 | 0.059116 | 0 | 0 | 0.11823 | 323.8695 | 0.059495 | 0 | 0 | 0.11899 | 324.1315 | 0.060063 | 0 | 0 | 0.12013 | 324.3935 | 0.060631 | 0 | 0 | 0.12126 | 324.6556 | 0.0612 | 0 | 0 | 0.1224 | 325.0049 | 0.061957 | 0 | 0 | 0.12391 | 325.267 | 0.062526 | 0 | 0 | 0.12505 | 325.4417 | 0.062905 | 0 | 0 | 0.12581 | 325.7037 | 0.063473 | 0 | 0 | 0.12695 | 325.8784 | 0.063852 | 0 | 0 | 0.1277 | 326.1404 | 0.06442 | 0 | 0 | 0.12884 | 326.4024 | 0.064989 | 0 | 0 | 0.12998 | 326.5771 | 0.065367 | 0 | 0 | 0.13073 | 326.8392 | 0.065936 | 0 | 0 | 0.13187 | 327.1012 | 0.066504 | 0 | 0 | 0.13301 | 327.1885 | 0.066694 | 0 | 0 | 0.13339 | 327.4506 | 0.067262 | 0 | 0 | 0.13452 | 327.7126 | 0.06783 | 0 | 0 | 0.13566 | 327.8873 | 0.068209 | 0 | 0 | 0.13642 | 328.1493 | 0.068777 | 0 | 0 | 0.13755 | 328.324 | 0.069156 | 0 | 0 | 0.13831 | 328.4987 | 0.069535 | 0 | 0 | 0.13907
2017-12-24 02:00 | 289.0848 | 0.86165 |  | 303.5578 | 0.015438 | 0 | 0 | 0.030877 | 312.0881 | 0.033941 | 0 | 0 | 0.067881 | 319.0674 | 0.049079 | 0 | 0 | 0.098158 | 319.3259 | 0.04964 | 0 | 0 | 0.099279 | 319.4982 | 0.050013 | 0 | 0 | 0.10003 | 319.7567 | 0.050574 | 0 | 0 | 0.10115 | 320.0152 | 0.051135 | 0 | 0 | 0.10227 | 320.2737 | 0.051695 | 0 | 0 | 0.10339 | 320.6184 | 0.052443 | 0 | 0 | 0.10489 | 320.8769 | 0.053004 | 0 | 0 | 0.10601 | 321.0492 | 0.053377 | 0 | 0 | 0.10675 | 321.3077 | 0.053938 | 0 | 0 | 0.10788 | 321.48 | 0.054312 | 0 | 0 | 0.10862 | 321.7385 | 0.054872 | 0 | 0 | 0.10974 | 321.997 | 0.055433 | 0 | 0 | 0.11087 | 322.1693 | 0.055807 | 0 | 0 | 0.11161 | 322.4278 | 0.056368 | 0 | 0 | 0.11274 | 322.6863 | 0.056928 | 0 | 0 | 0.11386 | 322.7725 | 0.057115 | 0 | 0 | 0.11423 | 323.031 | 0.057676 | 0 | 0 | 0.11535 | 323.2895 | 0.058236 | 0 | 0 | 0.11647 | 323.4618 | 0.05861 | 0 | 0 | 0.11722 | 323.7203 | 0.059171 | 0 | 0 | 0.11834 | 323.8926 | 0.059545 | 0 | 0 | 0.11909 | 324.0649 | 0.059919 | 0 | 0 | 0.11984
2017-12-24 03:00 | 284.1406 | 0.84691 |  | 298.366 | 0.0041775 | 0 | 0 | 0.0083551 | 306.7504 | 0.022363 | 0 | 0 | 0.044727 | 313.6104 | 0.037243 | 0 | 0 | 0.074485 | 313.8645 | 0.037794 | 0 | 0 | 0.075587 | 314.0338 | 0.038161 | 0 | 0 | 0.076322 | 314.2879 | 0.038712 | 0 | 0 | 0.077424 | 314.542 | 0.039263 | 0 | 0 | 0.078526 | 314.7961 | 0.039814 | 0 | 0 | 0.079629 | 315.1348 | 0.040549 | 0 | 0 | 0.081098 | 315.3889 | 0.0411 | 0 | 0 | 0.0822 | 315.5583 | 0.041468 | 0 | 0 | 0.082935 | 315.8123 | 0.042019 | 0 | 0 | 0.084037 | 315.9817 | 0.042386 | 0 | 0 | 0.084772 | 316.2358 | 0.042937 | 0 | 0 | 0.085874 | 316.4899 | 0.043488 | 0 | 0 | 0.086976 | 316.6593 | 0.043856 | 0 | 0 | 0.087711 | 316.9133 | 0.044407 | 0 | 0 | 0.088813 | 317.1674 | 0.044958 | 0 | 0 | 0.089915 | 317.2521 | 0.045141 | 0 | 0 | 0.090283 | 317.5062 | 0.045693 | 0 | 0 | 0.091385 | 317.7602 | 0.046244 | 0 | 0 | 0.092487 | 317.9296 | 0.046611 | 0 | 0 | 0.093222 | 318.1837 | 0.047162 | 0 | 0 | 0.094324 | 318.3531 | 0.047529 | 0 | 0 | 0.095059 | 318.5225 | 0.047897 | 0 | 0 | 0.095794
2017-12-24 04:00 | 278.6763 | 0.83062 |  | 292.6281 | 0 | 0 | 0 | 0 | 300.8513 | 0.009568 | 0 | 0 | 0.019136 | 307.5793 | 0.024161 | 0 | 0 | 0.048322 | 307.8285 | 0.024702 | 0 | 0 | 0.049403 | 307.9946 | 0.025062 | 0 | 0 | 0.050124 | 308.2438 | 0.025602 | 0 | 0 | 0.051205 | 308.493 | 0.026143 | 0 | 0 | 0.052286 | 308.7422 | 0.026683 | 0 | 0 | 0.053367 | 309.0744 | 0.027404 | 0 | 0 | 0.054808 | 309.3236 | 0.027945 | 0 | 0 | 0.055889 | 309.4897 | 0.028305 | 0 | 0 | 0.05661 | 309.7389 | 0.028845 | 0 | 0 | 0.057691 | 309.905 | 0.029206 | 0 | 0 | 0.058411 | 310.1542 | 0.029746 | 0 | 0 | 0.059492 | 310.4034 | 0.030287 | 0 | 0 | 0.060573 | 310.5695 | 0.030647 | 0 | 0 | 0.061294 | 310.8187 | 0.031187 | 0 | 0 | 0.062375 | 311.0679 | 0.031728 | 0 | 0 | 0.063456 | 311.151 | 0.031908 | 0 | 0 | 0.063816 | 311.4002 | 0.032449 | 0 | 0 | 0.064897 | 311.6493 | 0.032989 | 0 | 0 | 0.065978 | 311.8155 | 0.033349 | 0 | 0 | 0.066699 | 312.0647 | 0.03389 | 0 | 0 | 0.06778 | 312.2308 | 0.03425 | 0 | 0 | 0.0685 | 312.3969 | 0.034611 | 0 | 0 | 0.069221
2017-12-24 05:00 | 275.6151 | 0.8215 |  | 289.4137 | 0 | 0 | 0 | 0 | 297.5465 | 0.0024001 | 0 | 0 | 0.0048002 | 304.2007 | 0.016833 | 0 | 0 | 0.033666 | 304.4471 | 0.017367 | 0 | 0 | 0.034735 | 304.6114 | 0.017724 | 0 | 0 | 0.035448 | 304.8579 | 0.018258 | 0 | 0 | 0.036517 | 305.1043 | 0.018793 | 0 | 0 | 0.037586 | 305.3508 | 0.019327 | 0 | 0 | 0.038655 | 305.6794 | 0.02004 | 0 | 0 | 0.04008 | 305.9258 | 0.020575 | 0 | 0 | 0.04115 | 306.0901 | 0.020931 | 0 | 0 | 0.041862 | 306.3366 | 0.021466 | 0 | 0 | 0.042931 | 306.5009 | 0.021822 | 0 | 0 | 0.043644 | 306.7473 | 0.022357 | 0 | 0 | 0.044713 | 306.9938 | 0.022891 | 0 | 0 | 0.045782 | 307.1581 | 0.023247 | 0 | 0 | 0.046495 | 307.4045 | 0.023782 | 0 | 0 | 0.047564 | 307.651 | 0.024317 | 0 | 0 | 0.048633 | 307.7331 | 0.024495 | 0 | 0 | 0.04899 | 307.9796 | 0.025029 | 0 | 0 | 0.050059 | 308.226 | 0.025564 | 0 | 0 | 0.051128 | 308.3903 | 0.02592 | 0 | 0 | 0.05184 | 308.6368 | 0.026455 | 0 | 0 | 0.05291 | 308.8011 | 0.026811 | 0 | 0 | 0.053622 | 308.9654 | 0.027168 | 0 | 0 | 0.054335
2017-12-24 06:00 | 279.1921 | 0.83216 |  | 293.1697 | 0 | 0 | 0 | 0 | 301.4081 | 0.010776 | 0 | 0 | 0.021552 | 308.1486 | 0.025396 | 0 | 0 | 0.050792 | 308.3982 | 0.025937 | 0 | 0 | 0.051875 | 308.5647 | 0.026298 | 0 | 0 | 0.052597 | 308.8143 | 0.02684 | 0 | 0 | 0.05368 | 309.064 | 0.027381 | 0 | 0 | 0.054763 | 309.3136 | 0.027923 | 0 | 0 | 0.055846 | 309.6465 | 0.028645 | 0 | 0 | 0.05729 | 309.8961 | 0.029186 | 0 | 0 | 0.058373 | 310.0626 | 0.029547 | 0 | 0 | 0.059095 | 310.3122 | 0.030089 | 0 | 0 | 0.060178 | 310.4786 | 0.03045 | 0 | 0 | 0.0609 | 310.7283 | 0.030991 | 0 | 0 | 0.061983 | 310.9779 | 0.031533 | 0 | 0 | 0.063066 | 311.1444 | 0.031894 | 0 | 0 | 0.063788 | 311.394 | 0.032435 | 0 | 0 | 0.064871 | 311.6437 | 0.032977 | 0 | 0 | 0.065953 | 311.7269 | 0.033157 | 0 | 0 | 0.066314 | 311.9765 | 0.033699 | 0 | 0 | 0.067397 | 312.2262 | 0.03424 | 0 | 0 | 0.06848 | 312.3926 | 0.034601 | 0 | 0 | 0.069202 | 312.6423 | 0.035143 | 0 | 0 | 0.070285 | 312.8087 | 0.035504 | 0 | 0 | 0.071007 | 312.9751 | 0.035865 | 0 | 0 | 0.071729
2017-12-24 07:00 | 279.6729 | 0.83359 |  | 293.6747 | 0 | 0 | 0 | 0 | 301.9272 | 0.011902 | 0 | 0 | 0.023804 | 308.6793 | 0.026547 | 0 | 0 | 0.053094 | 308.9294 | 0.02709 | 0 | 0 | 0.054179 | 309.0961 | 0.027451 | 0 | 0 | 0.054902 | 309.3462 | 0.027994 | 0 | 0 | 0.055987 | 309.5963 | 0.028536 | 0 | 0 | 0.057072 | 309.8464 | 0.029078 | 0 | 0 | 0.058157 | 310.1798 | 0.029802 | 0 | 0 | 0.059603 | 310.4299 | 0.030344 | 0 | 0 | 0.060688 | 310.5966 | 0.030706 | 0 | 0 | 0.061411 | 310.8467 | 0.031248 | 0 | 0 | 0.062496 | 311.0134 | 0.03161 | 0 | 0 | 0.063219 | 311.2635 | 0.032152 | 0 | 0 | 0.064304 | 311.5136 | 0.032695 | 0 | 0 | 0.065389 | 311.6803 | 0.033056 | 0 | 0 | 0.066112 | 311.9304 | 0.033599 | 0 | 0 | 0.067197 | 312.1804 | 0.034141 | 0 | 0 | 0.068282 | 312.2638 | 0.034322 | 0 | 0 | 0.068644 | 312.5139 | 0.034864 | 0 | 0 | 0.069728 | 312.764 | 0.035407 | 0 | 0 | 0.070813 | 312.9307 | 0.035768 | 0 | 0 | 0.071537 | 313.1807 | 0.036311 | 0 | 0 | 0.072621 | 313.3475 | 0.036672 | 0 | 0 | 0.073345 | 313.5142 | 0.037034 | 0 | 0 | 0.074068
2017-12-24 08:00 | 271.5337 | 0.80933 |  | 285.1279 | 0 | 0 | 0 | 0 | 293.1403 | 0 | 0 | 0 | 0 | 299.6959 | 0.0070621 | 0 | 0 | 0.014124 | 299.9387 | 0.0075887 | 0 | 0 | 0.015177 | 300.1006 | 0.0079398 | 0 | 0 | 0.01588 | 300.3434 | 0.0084664 | 0 | 0 | 0.016933 | 300.5862 | 0.0089931 | 0 | 0 | 0.017986 | 300.829 | 0.0095197 | 0 | 0 | 0.019039 | 301.1527 | 0.010222 | 0 | 0 | 0.020444 | 301.3955 | 0.010748 | 0 | 0 | 0.021497 | 301.5574 | 0.0111 | 0 | 0 | 0.022199 | 301.8002 | 0.011626 | 0 | 0 | 0.023252 | 301.962 | 0.011977 | 0 | 0 | 0.023955 | 302.2048 | 0.012504 | 0 | 0 | 0.025008 | 302.4476 | 0.013031 | 0 | 0 | 0.026061 | 302.6095 | 0.013382 | 0 | 0 | 0.026763 | 302.8523 | 0.013908 | 0 | 0 | 0.027817 | 303.0951 | 0.014435 | 0 | 0 | 0.02887 | 303.176 | 0.01461 | 0 | 0 | 0.029221 | 303.4188 | 0.015137 | 0 | 0 | 0.030274 | 303.6616 | 0.015664 | 0 | 0 | 0.031327 | 303.8235 | 0.016015 | 0 | 0 | 0.03203 | 304.0663 | 0.016541 | 0 | 0 | 0.033083 | 304.2282 | 0.016893 | 0 | 0 | 0.033785 | 304.39 | 0.017244 | 0 | 0 | 0.034487
2017-12-24 09:00 | 273.1227 | 0.81407 |  | 286.7965 | 0 | 0 | 0 | 0 | 294.8558 | 0 | 0 | 0 | 0 | 301.4498 | 0.010866 | 0 | 0 | 0.021732 | 301.694 | 0.011396 | 0 | 0 | 0.022792 | 301.8568 | 0.011749 | 0 | 0 | 0.023498 | 302.101 | 0.012279 | 0 | 0 | 0.024558 | 302.3453 | 0.012809 | 0 | 0 | 0.025617 | 302.5895 | 0.013338 | 0 | 0 | 0.026676 | 302.9151 | 0.014045 | 0 | 0 | 0.028089 | 303.1593 | 0.014574 | 0 | 0 | 0.029148 | 303.3221 | 0.014927 | 0 | 0 | 0.029855 | 303.5664 | 0.015457 | 0 | 0 | 0.030914 | 303.7292 | 0.01581 | 0 | 0 | 0.03162 | 303.9734 | 0.01634 | 0 | 0 | 0.03268 | 304.2176 | 0.01687 | 0 | 0 | 0.033739 | 304.3804 | 0.017223 | 0 | 0 | 0.034446 | 304.6247 | 0.017753 | 0 | 0 | 0.035505 | 304.8689 | 0.018282 | 0 | 0 | 0.036564 | 304.9503 | 0.018459 | 0 | 0 | 0.036918 | 305.1945 | 0.018989 | 0 | 0 | 0.037977 | 305.4387 | 0.019518 | 0 | 0 | 0.039036 | 305.6015 | 0.019871 | 0 | 0 | 0.039743 | 305.8458 | 0.020401 | 0 | 0 | 0.040802 | 306.0086 | 0.020754 | 0 | 0 | 0.041508 | 306.1714 | 0.021107 | 0 | 0 | 0.042215
2017-12-24 10:00 | 276.674 | 0.82465 |  | 290.5256 | 0 | 0 | 0 | 0 | 298.6896 | 0.0048795 | 0 | 0 | 0.0097589 | 305.3693 | 0.019368 | 0 | 0 | 0.038735 | 305.6167 | 0.019904 | 0 | 0 | 0.039809 | 305.7817 | 0.020262 | 0 | 0 | 0.040524 | 306.0291 | 0.020799 | 0 | 0 | 0.041597 | 306.2765 | 0.021335 | 0 | 0 | 0.042671 | 306.5239 | 0.021872 | 0 | 0 | 0.043744 | 306.8537 | 0.022587 | 0 | 0 | 0.045175 | 307.1011 | 0.023124 | 0 | 0 | 0.046248 | 307.266 | 0.023482 | 0 | 0 | 0.046963 | 307.5134 | 0.024018 | 0 | 0 | 0.048037 | 307.6784 | 0.024376 | 0 | 0 | 0.048752 | 307.9258 | 0.024913 | 0 | 0 | 0.049825 | 308.1732 | 0.025449 | 0 | 0 | 0.050898 | 308.3381 | 0.025807 | 0 | 0 | 0.051614 | 308.5855 | 0.026344 | 0 | 0 | 0.052687 | 308.8329 | 0.02688 | 0 | 0 | 0.05376 | 308.9153 | 0.027059 | 0 | 0 | 0.054118 | 309.1627 | 0.027596 | 0 | 0 | 0.055191 | 309.4101 | 0.028132 | 0 | 0 | 0.056264 | 309.5751 | 0.02849 | 0 | 0 | 0.05698 | 309.8225 | 0.029027 | 0 | 0 | 0.058053 | 309.9874 | 0.029384 | 0 | 0 | 0.058769 | 310.1523 | 0.029742 | 0 | 0 | 0.059484
2017-12-24 11:00 | 277.6247 | 0.82749 |  | 291.5239 | 0 | 0 | 0 | 0 | 299.716 | 0.0071057 | 0 | 0 | 0.014211 | 306.4187 | 0.021644 | 0 | 0 | 0.043287 | 306.6669 | 0.022182 | 0 | 0 | 0.044364 | 306.8324 | 0.022541 | 0 | 0 | 0.045082 | 307.0807 | 0.02308 | 0 | 0 | 0.046159 | 307.3289 | 0.023618 | 0 | 0 | 0.047236 | 307.5772 | 0.024156 | 0 | 0 | 0.048313 | 307.9082 | 0.024874 | 0 | 0 | 0.049749 | 308.1564 | 0.025413 | 0 | 0 | 0.050826 | 308.3219 | 0.025772 | 0 | 0 | 0.051544 | 308.5701 | 0.02631 | 0 | 0 | 0.052621 | 308.7356 | 0.026669 | 0 | 0 | 0.053338 | 308.9839 | 0.027208 | 0 | 0 | 0.054415 | 309.2321 | 0.027746 | 0 | 0 | 0.055492 | 309.3976 | 0.028105 | 0 | 0 | 0.05621 | 309.6459 | 0.028644 | 0 | 0 | 0.057287 | 309.8941 | 0.029182 | 0 | 0 | 0.058364 | 309.9769 | 0.029361 | 0 | 0 | 0.058723 | 310.2251 | 0.0299 | 0 | 0 | 0.0598 | 310.4734 | 0.030438 | 0 | 0 | 0.060877 | 310.6389 | 0.030797 | 0 | 0 | 0.061595 | 310.8871 | 0.031336 | 0 | 0 | 0.062672 | 311.0526 | 0.031695 | 0 | 0 | 0.063389 | 311.2181 | 0.032054 | 0 | 0 | 0.064107
2017-12-24 12:00 | 271.5684 | 0.80944 |  | 285.1644 | 0 | 0 | 0 | 0 | 293.1778 | 0 | 0 | 0 | 0 | 299.7342 | 0.0071452 | 0 | 0 | 0.01429 | 299.9771 | 0.0076719 | 0 | 0 | 0.015344 | 300.1389 | 0.008023 | 0 | 0 | 0.016046 | 300.3818 | 0.0085497 | 0 | 0 | 0.017099 | 300.6246 | 0.0090764 | 0 | 0 | 0.018153 | 300.8674 | 0.0096031 | 0 | 0 | 0.019206 | 301.1912 | 0.010305 | 0 | 0 | 0.020611 | 301.434 | 0.010832 | 0 | 0 | 0.021664 | 301.5959 | 0.011183 | 0 | 0 | 0.022366 | 301.8388 | 0.01171 | 0 | 0 | 0.02342 | 302.0007 | 0.012061 | 0 | 0 | 0.024122 | 302.2435 | 0.012588 | 0 | 0 | 0.025176 | 302.4863 | 0.013114 | 0 | 0 | 0.026229 | 302.6482 | 0.013466 | 0 | 0 | 0.026931 | 302.891 | 0.013992 | 0 | 0 | 0.027985 | 303.1339 | 0.014519 | 0 | 0 | 0.029038 | 303.2148 | 0.014695 | 0 | 0 | 0.029389 | 303.4576 | 0.015221 | 0 | 0 | 0.030443 | 303.7005 | 0.015748 | 0 | 0 | 0.031496 | 303.8624 | 0.016099 | 0 | 0 | 0.032198 | 304.1052 | 0.016626 | 0 | 0 | 0.033252 | 304.2671 | 0.016977 | 0 | 0 | 0.033954 | 304.429 | 0.017328 | 0 | 0 | 0.034656
2017-12-24 13:00 | 275.8911 | 0.82232 |  | 289.7035 | 0 | 0 | 0 | 0 | 297.8445 | 0.0030464 | 0 | 0 | 0.0060928 | 304.5053 | 0.017494 | 0 | 0 | 0.034987 | 304.752 | 0.018029 | 0 | 0 | 0.036057 | 304.9165 | 0.018385 | 0 | 0 | 0.036771 | 305.1632 | 0.018921 | 0 | 0 | 0.037841 | 305.4099 | 0.019456 | 0 | 0 | 0.038911 | 305.6566 | 0.019991 | 0 | 0 | 0.039981 | 305.9855 | 0.020704 | 0 | 0 | 0.041408 | 306.2322 | 0.021239 | 0 | 0 | 0.042478 | 306.3966 | 0.021596 | 0 | 0 | 0.043192 | 306.6433 | 0.022131 | 0 | 0 | 0.044262 | 306.8078 | 0.022488 | 0 | 0 | 0.044976 | 307.0545 | 0.023023 | 0 | 0 | 0.046046 | 307.3012 | 0.023558 | 0 | 0 | 0.047116 | 307.4657 | 0.023915 | 0 | 0 | 0.047829 | 307.7124 | 0.02445 | 0 | 0 | 0.048899 | 307.9591 | 0.024985 | 0 | 0 | 0.04997 | 308.0413 | 0.025163 | 0 | 0 | 0.050326 | 308.288 | 0.025698 | 0 | 0 | 0.051397 | 308.5347 | 0.026233 | 0 | 0 | 0.052467 | 308.6991 | 0.02659 | 0 | 0 | 0.05318 | 308.9458 | 0.027125 | 0 | 0 | 0.05425 | 309.1103 | 0.027482 | 0 | 0 | 0.054964 | 309.2748 | 0.027839 | 0 | 0 | 0.055677
2017-12-24 14:00 | 287.5052 | 0.85694 |  | 301.8991 | 0.011841 | 0 | 0 | 0.023682 | 310.3828 | 0.030242 | 0 | 0 | 0.060484 | 317.324 | 0.045297 | 0 | 0 | 0.090595 | 317.5811 | 0.045855 | 0 | 0 | 0.09171 | 317.7524 | 0.046227 | 0 | 0 | 0.092453 | 318.0095 | 0.046784 | 0 | 0 | 0.093569 | 318.2666 | 0.047342 | 0 | 0 | 0.094684 | 318.5237 | 0.0479 | 0 | 0 | 0.095799 | 318.8665 | 0.048643 | 0 | 0 | 0.097286 | 319.1235 | 0.049201 | 0 | 0 | 0.098401 | 319.2949 | 0.049572 | 0 | 0 | 0.099145 | 319.552 | 0.05013 | 0 | 0 | 0.10026 | 319.7234 | 0.050502 | 0 | 0 | 0.101 | 319.9805 | 0.051059 | 0 | 0 | 0.10212 | 320.2376 | 0.051617 | 0 | 0 | 0.10323 | 320.409 | 0.051989 | 0 | 0 | 0.10398 | 320.666 | 0.052546 | 0 | 0 | 0.10509 | 320.9231 | 0.053104 | 0 | 0 | 0.10621 | 321.0088 | 0.05329 | 0 | 0 | 0.10658 | 321.2659 | 0.053847 | 0 | 0 | 0.10769 | 321.523 | 0.054405 | 0 | 0 | 0.10881 | 321.6944 | 0.054777 | 0 | 0 | 0.10955 | 321.9514 | 0.055334 | 0 | 0 | 0.11067 | 322.1228 | 0.055706 | 0 | 0 | 0.11141 | 322.2942 | 0.056078 | 0 | 0 | 0.11216
2017-12-24 15:00 | 294.1367 | 0.8767 |  | 308.8626 | 0.026945 | 0 | 0 | 0.053889 | 317.542 | 0.04577 | 0 | 0 | 0.09154 | 324.6433 | 0.061173 | 0 | 0 | 0.12235 | 324.9063 | 0.061743 | 0 | 0 | 0.12349 | 325.0816 | 0.062124 | 0 | 0 | 0.12425 | 325.3446 | 0.062694 | 0 | 0 | 0.12539 | 325.6076 | 0.063265 | 0 | 0 | 0.12653 | 325.8707 | 0.063835 | 0 | 0 | 0.12767 | 326.2213 | 0.064596 | 0 | 0 | 0.12919 | 326.4843 | 0.065166 | 0 | 0 | 0.13033 | 326.6597 | 0.065547 | 0 | 0 | 0.13109 | 326.9227 | 0.066117 | 0 | 0 | 0.13223 | 327.098 | 0.066497 | 0 | 0 | 0.13299 | 327.3611 | 0.067068 | 0 | 0 | 0.13414 | 327.6241 | 0.067638 | 0 | 0 | 0.13528 | 327.7994 | 0.068019 | 0 | 0 | 0.13604 | 328.0624 | 0.068589 | 0 | 0 | 0.13718 | 328.3254 | 0.069159 | 0 | 0 | 0.13832 | 328.4131 | 0.06935 | 0 | 0 | 0.1387 | 328.6761 | 0.06992 | 0 | 0 | 0.13984 | 328.9391 | 0.070491 | 0 | 0 | 0.14098 | 329.1145 | 0.070871 | 0 | 0 | 0.14174 | 329.3775 | 0.071441 | 0 | 0 | 0.14288 | 329.5528 | 0.071822 | 0 | 0 | 0.14364 | 329.7281 | 0.072202 | 0 | 0 | 0.1444
2017-12-24 16:00 | 295.2305 | 0.87996 |  | 310.0111 | 0.029436 | 0 | 0 | 0.058871 | 318.7227 | 0.048331 | 0 | 0 | 0.096662 | 325.8504 | 0.063791 | 0 | 0 | 0.12758 | 326.1144 | 0.064364 | 0 | 0 | 0.12873 | 326.2904 | 0.064746 | 0 | 0 | 0.12949 | 326.5544 | 0.065318 | 0 | 0 | 0.13064 | 326.8184 | 0.065891 | 0 | 0 | 0.13178 | 327.0824 | 0.066463 | 0 | 0 | 0.13293 | 327.4344 | 0.067227 | 0 | 0 | 0.13445 | 327.6984 | 0.067799 | 0 | 0 | 0.1356 | 327.8743 | 0.068181 | 0 | 0 | 0.13636 | 328.1383 | 0.068754 | 0 | 0 | 0.13751 | 328.3143 | 0.069135 | 0 | 0 | 0.13827 | 328.5783 | 0.069708 | 0 | 0 | 0.13942 | 328.8423 | 0.070281 | 0 | 0 | 0.14056 | 329.0183 | 0.070662 | 0 | 0 | 0.14132 | 329.2823 | 0.071235 | 0 | 0 | 0.14247 | 329.5463 | 0.071808 | 0 | 0 | 0.14362 | 329.6343 | 0.071998 | 0 | 0 | 0.144 | 329.8983 | 0.072571 | 0 | 0 | 0.14514 | 330.1623 | 0.073144 | 0 | 0 | 0.14629 | 330.3382 | 0.073525 | 0 | 0 | 0.14705 | 330.6022 | 0.074098 | 0 | 0 | 0.1482 | 330.7782 | 0.07448 | 0 | 0 | 0.14896 | 330.9542 | 0.074861 | 0 | 0 | 0.14972
2017-12-24 17:00 | 297.3377 | 0.88624 |  | 312.2239 | 0.034235 | 0 | 0 | 0.06847 | 320.9977 | 0.053266 | 0 | 0 | 0.10653 | 328.1763 | 0.068836 | 0 | 0 | 0.13767 | 328.4421 | 0.069413 | 0 | 0 | 0.13883 | 328.6194 | 0.069797 | 0 | 0 | 0.13959 | 328.8853 | 0.070374 | 0 | 0 | 0.14075 | 329.1511 | 0.07095 | 0 | 0 | 0.1419 | 329.417 | 0.071527 | 0 | 0 | 0.14305 | 329.7715 | 0.072296 | 0 | 0 | 0.14459 | 330.0374 | 0.072873 | 0 | 0 | 0.14575 | 330.2146 | 0.073257 | 0 | 0 | 0.14651 | 330.4805 | 0.073834 | 0 | 0 | 0.14767 | 330.6578 | 0.074218 | 0 | 0 | 0.14844 | 330.9236 | 0.074795 | 0 | 0 | 0.14959 | 331.1895 | 0.075372 | 0 | 0 | 0.15074 | 331.3668 | 0.075756 | 0 | 0 | 0.15151 | 331.6326 | 0.076333 | 0 | 0 | 0.15267 | 331.8985 | 0.076909 | 0 | 0 | 0.15382 | 331.9871 | 0.077102 | 0 | 0 | 0.1542 | 332.253 | 0.077678 | 0 | 0 | 0.15536 | 332.5189 | 0.078255 | 0 | 0 | 0.15651 | 332.6961 | 0.07864 | 0 | 0 | 0.15728 | 332.962 | 0.079216 | 0 | 0 | 0.15843 | 333.1392 | 0.079601 | 0 | 0 | 0.1592 | 333.3165 | 0.079985 | 0 | 0 | 0.15997
2017-12-24 18:00 | 300.4405 | 0.89549 |  | 315.4819 | 0.041302 | 0 | 0 | 0.082604 | 324.3473 | 0.060531 | 0 | 0 | 0.12106 | 331.6008 | 0.076264 | 0 | 0 | 0.15253 | 331.8695 | 0.076846 | 0 | 0 | 0.15369 | 332.0485 | 0.077235 | 0 | 0 | 0.15447 | 332.3172 | 0.077818 | 0 | 0 | 0.15564 | 332.5858 | 0.0784 | 0 | 0 | 0.1568 | 332.8545 | 0.078983 | 0 | 0 | 0.15797 | 333.2127 | 0.07976 | 0 | 0 | 0.15952 | 333.4813 | 0.080343 | 0 | 0 | 0.16069 | 333.6604 | 0.080731 | 0 | 0 | 0.16146 | 333.9291 | 0.081314 | 0 | 0 | 0.16263 | 334.1082 | 0.081702 | 0 | 0 | 0.1634 | 334.3768 | 0.082285 | 0 | 0 | 0.16457 | 334.6455 | 0.082868 | 0 | 0 | 0.16574 | 334.8246 | 0.083256 | 0 | 0 | 0.16651 | 335.0932 | 0.083839 | 0 | 0 | 0.16768 | 335.3619 | 0.084422 | 0 | 0 | 0.16884 | 335.4514 | 0.084616 | 0 | 0 | 0.16923 | 335.7201 | 0.085198 | 0 | 0 | 0.1704 | 335.9887 | 0.085781 | 0 | 0 | 0.17156 | 336.1678 | 0.08617 | 0 | 0 | 0.17234 | 336.4365 | 0.086752 | 0 | 0 | 0.1735 | 336.6156 | 0.087141 | 0 | 0 | 0.17428 | 336.7947 | 0.087529 | 0 | 0 | 0.17506
2017-12-24 19:00 | 300.943 | 0.89699 |  | 316.0096 | 0.042446 | 0 | 0 | 0.084893 | 324.8898 | 0.061708 | 0 | 0 | 0.12342 | 332.1554 | 0.077467 | 0 | 0 | 0.15493 | 332.4245 | 0.07805 | 0 | 0 | 0.1561 | 332.6039 | 0.07844 | 0 | 0 | 0.15688 | 332.873 | 0.079023 | 0 | 0 | 0.15805 | 333.1421 | 0.079607 | 0 | 0 | 0.15921 | 333.4112 | 0.080191 | 0 | 0 | 0.16038 | 333.77 | 0.080969 | 0 | 0 | 0.16194 | 334.0391 | 0.081552 | 0 | 0 | 0.1631 | 334.2185 | 0.081942 | 0 | 0 | 0.16388 | 334.4876 | 0.082525 | 0 | 0 | 0.16505 | 334.667 | 0.082914 | 0 | 0 | 0.16583 | 334.9361 | 0.083498 | 0 | 0 | 0.167 | 335.2052 | 0.084082 | 0 | 0 | 0.16816 | 335.3846 | 0.084471 | 0 | 0 | 0.16894 | 335.6537 | 0.085054 | 0 | 0 | 0.17011 | 335.9228 | 0.085638 | 0 | 0 | 0.17128 | 336.0125 | 0.085833 | 0 | 0 | 0.17167 | 336.2816 | 0.086416 | 0 | 0 | 0.17283 | 336.5507 | 0.087 | 0 | 0 | 0.174 | 336.7301 | 0.087389 | 0 | 0 | 0.17478 | 336.9992 | 0.087973 | 0 | 0 | 0.17595 | 337.1785 | 0.088362 | 0 | 0 | 0.17672 | 337.3579 | 0.088751 | 0 | 0 | 0.1775
2017-12-24 20:00 | 298.7878 | 0.89057 |  | 313.7466 | 0.037538 | 0 | 0 | 0.075076 | 322.5632 | 0.056661 | 0 | 0 | 0.11332 | 329.7768 | 0.072307 | 0 | 0 | 0.14461 | 330.0439 | 0.072887 | 0 | 0 | 0.14577 | 330.222 | 0.073273 | 0 | 0 | 0.14655 | 330.4892 | 0.073853 | 0 | 0 | 0.14771 | 330.7564 | 0.074432 | 0 | 0 | 0.14886 | 331.0236 | 0.075012 | 0 | 0 | 0.15002 | 331.3798 | 0.075784 | 0 | 0 | 0.15157 | 331.647 | 0.076364 | 0 | 0 | 0.15273 | 331.8251 | 0.07675 | 0 | 0 | 0.1535 | 332.0922 | 0.07733 | 0 | 0 | 0.15466 | 332.2703 | 0.077716 | 0 | 0 | 0.15543 | 332.5375 | 0.078296 | 0 | 0 | 0.15659 | 332.8047 | 0.078875 | 0 | 0 | 0.15775 | 332.9828 | 0.079261 | 0 | 0 | 0.15852 | 333.25 | 0.079841 | 0 | 0 | 0.15968 | 333.5171 | 0.08042 | 0 | 0 | 0.16084 | 333.6062 | 0.080613 | 0 | 0 | 0.16123 | 333.8734 | 0.081193 | 0 | 0 | 0.16239 | 334.1405 | 0.081772 | 0 | 0 | 0.16354 | 334.3187 | 0.082159 | 0 | 0 | 0.16432 | 334.5858 | 0.082738 | 0 | 0 | 0.16548 | 334.7639 | 0.083125 | 0 | 0 | 0.16625 | 334.942 | 0.083511 | 0 | 0 | 0.16702
2017-12-24 21:00 | 304.4372 | 0.9074 |  | 319.6787 | 0.050405 | 0 | 0 | 0.10081 | 328.662 | 0.06989 | 0 | 0 | 0.13978 | 336.012 | 0.085832 | 0 | 0 | 0.17166 | 336.2842 | 0.086422 | 0 | 0 | 0.17284 | 336.4657 | 0.086816 | 0 | 0 | 0.17363 | 336.738 | 0.087406 | 0 | 0 | 0.17481 | 337.0102 | 0.087997 | 0 | 0 | 0.17599 | 337.2824 | 0.088587 | 0 | 0 | 0.17717 | 337.6454 | 0.089374 | 0 | 0 | 0.17875 | 337.9176 | 0.089965 | 0 | 0 | 0.17993 | 338.0991 | 0.090358 | 0 | 0 | 0.18072 | 338.3713 | 0.090949 | 0 | 0 | 0.1819 | 338.5528 | 0.091343 | 0 | 0 | 0.18269 | 338.825 | 0.091933 | 0 | 0 | 0.18387 | 339.0972 | 0.092523 | 0 | 0 | 0.18505 | 339.2787 | 0.092917 | 0 | 0 | 0.18583 | 339.5509 | 0.093508 | 0 | 0 | 0.18702 | 339.8231 | 0.094098 | 0 | 0 | 0.1882 | 339.9139 | 0.094295 | 0 | 0 | 0.18859 | 340.1861 | 0.094885 | 0 | 0 | 0.18977 | 340.4583 | 0.095476 | 0 | 0 | 0.19095 | 340.6398 | 0.095869 | 0 | 0 | 0.19174 | 340.912 | 0.09646 | 0 | 0 | 0.19292 | 341.0935 | 0.096853 | 0 | 0 | 0.19371 | 341.275 | 0.097247 | 0 | 0 | 0.19449
2017-12-24 22:00 | 295.4312 | 0.88056 |  | 310.2219 | 0.029893 | 0 | 0 | 0.059786 | 318.9395 | 0.048801 | 0 | 0 | 0.097603 | 326.072 | 0.064272 | 0 | 0 | 0.12854 | 326.3362 | 0.064845 | 0 | 0 | 0.12969 | 326.5123 | 0.065227 | 0 | 0 | 0.13045 | 326.7765 | 0.0658 | 0 | 0 | 0.1316 | 327.0406 | 0.066373 | 0 | 0 | 0.13275 | 327.3048 | 0.066946 | 0 | 0 | 0.13389 | 327.657 | 0.06771 | 0 | 0 | 0.13542 | 327.9212 | 0.068283 | 0 | 0 | 0.13657 | 328.0973 | 0.068665 | 0 | 0 | 0.13733 | 328.3615 | 0.069238 | 0 | 0 | 0.13848 | 328.5376 | 0.06962 | 0 | 0 | 0.13924 | 328.8017 | 0.070193 | 0 | 0 | 0.14039 | 329.0659 | 0.070766 | 0 | 0 | 0.14153 | 329.242 | 0.071148 | 0 | 0 | 0.1423 | 329.5062 | 0.071721 | 0 | 0 | 0.14344 | 329.7704 | 0.072294 | 0 | 0 | 0.14459 | 329.8584 | 0.072485 | 0 | 0 | 0.14497 | 330.1226 | 0.073058 | 0 | 0 | 0.14612 | 330.3868 | 0.073631 | 0 | 0 | 0.14726 | 330.5629 | 0.074013 | 0 | 0 | 0.14803 | 330.827 | 0.074585 | 0 | 0 | 0.14917 | 331.0032 | 0.074967 | 0 | 0 | 0.14993 | 331.1793 | 0.075349 | 0 | 0 | 0.1507
2017-12-24 23:00 | 297.3621 | 0.88632 |  | 312.2494 | 0.034291 | 0 | 0 | 0.068581 | 321.0239 | 0.053323 | 0 | 0 | 0.10665 | 328.2031 | 0.068894 | 0 | 0 | 0.13779 | 328.469 | 0.069471 | 0 | 0 | 0.13894 | 328.6463 | 0.069855 | 0 | 0 | 0.13971 | 328.9122 | 0.070432 | 0 | 0 | 0.14086 | 329.1781 | 0.071009 | 0 | 0 | 0.14202 | 329.444 | 0.071586 | 0 | 0 | 0.14317 | 329.7985 | 0.072355 | 0 | 0 | 0.14471 | 330.0644 | 0.072931 | 0 | 0 | 0.14586 | 330.2416 | 0.073316 | 0 | 0 | 0.14663 | 330.5075 | 0.073892 | 0 | 0 | 0.14778 | 330.6848 | 0.074277 | 0 | 0 | 0.14855 | 330.9507 | 0.074854 | 0 | 0 | 0.14971 | 331.2166 | 0.07543 | 0 | 0 | 0.15086 | 331.3939 | 0.075815 | 0 | 0 | 0.15163 | 331.6597 | 0.076392 | 0 | 0 | 0.15278 | 331.9256 | 0.076968 | 0 | 0 | 0.15394 | 332.0143 | 0.077161 | 0 | 0 | 0.15432 | 332.2802 | 0.077737 | 0 | 0 | 0.15547 | 332.5461 | 0.078314 | 0 | 0 | 0.15663 | 332.7233 | 0.078699 | 0 | 0 | 0.1574 | 332.9892 | 0.079275 | 0 | 0 | 0.15855 | 333.1665 | 0.07966 | 0 | 0 | 0.15932 | 333.3438 | 0.080044 | 0 | 0 | 0.16009
2017-12-25 | 293.3682 | 0.87441 |  | 308.0556 | 0.025194 | 0 | 0 | 0.050388 | 316.7123 | 0.043971 | 0 | 0 | 0.087941 | 323.795 | 0.059333 | 0 | 0 | 0.11867 | 324.0574 | 0.059902 | 0 | 0 | 0.1198 | 324.2322 | 0.060281 | 0 | 0 | 0.12056 | 324.4946 | 0.06085 | 0 | 0 | 0.1217 | 324.7569 | 0.061419 | 0 | 0 | 0.12284 | 325.0192 | 0.061988 | 0 | 0 | 0.12398 | 325.369 | 0.062747 | 0 | 0 | 0.12549 | 325.6313 | 0.063316 | 0 | 0 | 0.12663 | 325.8062 | 0.063695 | 0 | 0 | 0.12739 | 326.0685 | 0.064264 | 0 | 0 | 0.12853 | 326.2434 | 0.064644 | 0 | 0 | 0.12929 | 326.5057 | 0.065213 | 0 | 0 | 0.13043 | 326.768 | 0.065782 | 0 | 0 | 0.13156 | 326.9429 | 0.066161 | 0 | 0 | 0.13232 | 327.2052 | 0.06673 | 0 | 0 | 0.13346 | 327.4676 | 0.067299 | 0 | 0 | 0.1346 | 327.555 | 0.067488 | 0 | 0 | 0.13498 | 327.8173 | 0.068057 | 0 | 0 | 0.13611 | 328.0797 | 0.068626 | 0 | 0 | 0.13725 | 328.2545 | 0.069006 | 0 | 0 | 0.13801 | 328.5169 | 0.069575 | 0 | 0 | 0.13915 | 328.6917 | 0.069954 | 0 | 0 | 0.13991 | 328.8666 | 0.070333 | 0 | 0 | 0.14067
2017-12-25 01:00 | 296.8545 | 0.8848 |  | 311.7164 | 0.033134 | 0 | 0 | 0.066269 | 320.4759 | 0.052134 | 0 | 0 | 0.10427 | 327.6429 | 0.067679 | 0 | 0 | 0.13536 | 327.9083 | 0.068255 | 0 | 0 | 0.13651 | 328.0853 | 0.068639 | 0 | 0 | 0.13728 | 328.3507 | 0.069214 | 0 | 0 | 0.13843 | 328.6161 | 0.06979 | 0 | 0 | 0.13958 | 328.8816 | 0.070366 | 0 | 0 | 0.14073 | 329.2355 | 0.071133 | 0 | 0 | 0.14227 | 329.5009 | 0.071709 | 0 | 0 | 0.14342 | 329.6779 | 0.072093 | 0 | 0 | 0.14419 | 329.9433 | 0.072669 | 0 | 0 | 0.14534 | 330.1203 | 0.073053 | 0 | 0 | 0.14611 | 330.3857 | 0.073628 | 0 | 0 | 0.14726 | 330.6512 | 0.074204 | 0 | 0 | 0.14841 | 330.8281 | 0.074588 | 0 | 0 | 0.14918 | 331.0936 | 0.075164 | 0 | 0 | 0.15033 | 331.359 | 0.075739 | 0 | 0 | 0.15148 | 331.4475 | 0.075931 | 0 | 0 | 0.15186 | 331.713 | 0.076507 | 0 | 0 | 0.15301 | 331.9784 | 0.077083 | 0 | 0 | 0.15417 | 332.1554 | 0.077467 | 0 | 0 | 0.15493 | 332.4208 | 0.078042 | 0 | 0 | 0.15608 | 332.5978 | 0.078426 | 0 | 0 | 0.15685 | 332.7747 | 0.07881 | 0 | 0 | 0.15762
2017-12-25 02:00 | 298.9477 | 0.89104 |  | 313.9145 | 0.037902 | 0 | 0 | 0.075804 | 322.7358 | 0.057036 | 0 | 0 | 0.11407 | 329.9533 | 0.07269 | 0 | 0 | 0.14538 | 330.2206 | 0.07327 | 0 | 0 | 0.14654 | 330.3988 | 0.073657 | 0 | 0 | 0.14731 | 330.6661 | 0.074236 | 0 | 0 | 0.14847 | 330.9334 | 0.074816 | 0 | 0 | 0.14963 | 331.2007 | 0.075396 | 0 | 0 | 0.15079 | 331.5571 | 0.076169 | 0 | 0 | 0.15234 | 331.8244 | 0.076749 | 0 | 0 | 0.1535 | 332.0027 | 0.077135 | 0 | 0 | 0.15427 | 332.27 | 0.077715 | 0 | 0 | 0.15543 | 332.4482 | 0.078102 | 0 | 0 | 0.1562 | 332.7155 | 0.078682 | 0 | 0 | 0.15736 | 332.9828 | 0.079261 | 0 | 0 | 0.15852 | 333.161 | 0.079648 | 0 | 0 | 0.1593 | 333.4283 | 0.080228 | 0 | 0 | 0.16046 | 333.6956 | 0.080807 | 0 | 0 | 0.16161 | 333.7847 | 0.081001 | 0 | 0 | 0.162 | 334.0521 | 0.081581 | 0 | 0 | 0.16316 | 334.3194 | 0.08216 | 0 | 0 | 0.16432 | 334.4976 | 0.082547 | 0 | 0 | 0.16509 | 334.7649 | 0.083127 | 0 | 0 | 0.16625 | 334.9431 | 0.083513 | 0 | 0 | 0.16703 | 335.1213 | 0.0839 | 0 | 0 | 0.1678
2017-12-25 03:00 | 302.6016 | 0.90193 |  | 317.7512 | 0.046224 | 0 | 0 | 0.092448 | 326.6804 | 0.065591 | 0 | 0 | 0.13118 | 333.986 | 0.081437 | 0 | 0 | 0.16287 | 334.2566 | 0.082024 | 0 | 0 | 0.16405 | 334.437 | 0.082416 | 0 | 0 | 0.16483 | 334.7076 | 0.083002 | 0 | 0 | 0.166 | 334.9782 | 0.083589 | 0 | 0 | 0.16718 | 335.2487 | 0.084176 | 0 | 0 | 0.16835 | 335.6095 | 0.084959 | 0 | 0 | 0.16992 | 335.8801 | 0.085546 | 0 | 0 | 0.17109 | 336.0605 | 0.085937 | 0 | 0 | 0.17187 | 336.3311 | 0.086524 | 0 | 0 | 0.17305 | 336.5115 | 0.086915 | 0 | 0 | 0.17383 | 336.782 | 0.087502 | 0 | 0 | 0.175 | 337.0526 | 0.088089 | 0 | 0 | 0.17618 | 337.233 | 0.08848 | 0 | 0 | 0.17696 | 337.5036 | 0.089067 | 0 | 0 | 0.17813 | 337.7742 | 0.089654 | 0 | 0 | 0.17931 | 337.8644 | 0.089849 | 0 | 0 | 0.1797 | 338.1349 | 0.090436 | 0 | 0 | 0.18087 | 338.4055 | 0.091023 | 0 | 0 | 0.18205 | 338.5859 | 0.091414 | 0 | 0 | 0.18283 | 338.8565 | 0.092001 | 0 | 0 | 0.184 | 339.0369 | 0.092393 | 0 | 0 | 0.18479 | 339.2173 | 0.092784 | 0 | 0 | 0.18557
2017-12-25 04:00 | 306.5583 | 0.91373 |  | 321.9061 | 0.055236 | 0 | 0 | 0.11047 | 330.952 | 0.074856 | 0 | 0 | 0.14971 | 338.3532 | 0.09091 | 0 | 0 | 0.18182 | 338.6273 | 0.091504 | 0 | 0 | 0.18301 | 338.81 | 0.091901 | 0 | 0 | 0.1838 | 339.0841 | 0.092495 | 0 | 0 | 0.18499 | 339.3583 | 0.09309 | 0 | 0 | 0.18618 | 339.6324 | 0.093684 | 0 | 0 | 0.18737 | 339.9979 | 0.094477 | 0 | 0 | 0.18895 | 340.272 | 0.095072 | 0 | 0 | 0.19014 | 340.4547 | 0.095468 | 0 | 0 | 0.19094 | 340.7288 | 0.096063 | 0 | 0 | 0.19213 | 340.9116 | 0.096459 | 0 | 0 | 0.19292 | 341.1857 | 0.097053 | 0 | 0 | 0.19411 | 341.4598 | 0.097648 | 0 | 0 | 0.1953 | 341.6426 | 0.098044 | 0 | 0 | 0.19609 | 341.9167 | 0.098639 | 0 | 0 | 0.19728 | 342.1908 | 0.099234 | 0 | 0 | 0.19847 | 342.2822 | 0.099432 | 0 | 0 | 0.19886 | 342.5563 | 0.10003 | 0 | 0 | 0.20005 | 342.8304 | 0.10062 | 0 | 0 | 0.20124 | 343.0132 | 0.10102 | 0 | 0 | 0.20203 | 343.2873 | 0.10161 | 0 | 0 | 0.20322 | 343.47 | 0.10201 | 0 | 0 | 0.20402 | 343.6528 | 0.1024 | 0 | 0 | 0.20481
2017-12-25 05:00 | 306.4573 | 0.91343 |  | 321.8 | 0.055006 | 0 | 0 | 0.11001 | 330.8429 | 0.07462 | 0 | 0 | 0.14924 | 338.2417 | 0.090668 | 0 | 0 | 0.18134 | 338.5157 | 0.091262 | 0 | 0 | 0.18252 | 338.6984 | 0.091659 | 0 | 0 | 0.18332 | 338.9724 | 0.092253 | 0 | 0 | 0.18451 | 339.2465 | 0.092847 | 0 | 0 | 0.18569 | 339.5205 | 0.093442 | 0 | 0 | 0.18688 | 339.8859 | 0.094234 | 0 | 0 | 0.18847 | 340.1599 | 0.094828 | 0 | 0 | 0.18966 | 340.3426 | 0.095225 | 0 | 0 | 0.19045 | 340.6166 | 0.095819 | 0 | 0 | 0.19164 | 340.7993 | 0.096215 | 0 | 0 | 0.19243 | 341.0733 | 0.09681 | 0 | 0 | 0.19362 | 341.3474 | 0.097404 | 0 | 0 | 0.19481 | 341.53 | 0.0978 | 0 | 0 | 0.1956 | 341.8041 | 0.098395 | 0 | 0 | 0.19679 | 342.0781 | 0.098989 | 0 | 0 | 0.19798 | 342.1694 | 0.099187 | 0 | 0 | 0.19837 | 342.4435 | 0.099782 | 0 | 0 | 0.19956 | 342.7175 | 0.10038 | 0 | 0 | 0.20075 | 342.9002 | 0.10077 | 0 | 0 | 0.20154 | 343.1742 | 0.10137 | 0 | 0 | 0.20273 | 343.3569 | 0.10176 | 0 | 0 | 0.20353 | 343.5396 | 0.10216 | 0 | 0 | 0.20432
2017-12-25 06:00 | 304.252 | 0.90685 |  | 319.4843 | 0.049983 | 0 | 0 | 0.099966 | 328.4621 | 0.069456 | 0 | 0 | 0.13891 | 335.8076 | 0.085388 | 0 | 0 | 0.17078 | 336.0797 | 0.085978 | 0 | 0 | 0.17196 | 336.2611 | 0.086372 | 0 | 0 | 0.17274 | 336.5331 | 0.086962 | 0 | 0 | 0.17392 | 336.8052 | 0.087552 | 0 | 0 | 0.1751 | 337.0772 | 0.088142 | 0 | 0 | 0.17628 | 337.44 | 0.088929 | 0 | 0 | 0.17786 | 337.712 | 0.089519 | 0 | 0 | 0.17904 | 337.8934 | 0.089912 | 0 | 0 | 0.17982 | 338.1655 | 0.090503 | 0 | 0 | 0.18101 | 338.3468 | 0.090896 | 0 | 0 | 0.18179 | 338.6189 | 0.091486 | 0 | 0 | 0.18297 | 338.8909 | 0.092076 | 0 | 0 | 0.18415 | 339.0723 | 0.092469 | 0 | 0 | 0.18494 | 339.3444 | 0.09306 | 0 | 0 | 0.18612 | 339.6164 | 0.09365 | 0 | 0 | 0.1873 | 339.7071 | 0.093846 | 0 | 0 | 0.18769 | 339.9792 | 0.094436 | 0 | 0 | 0.18887 | 340.2512 | 0.095027 | 0 | 0 | 0.19005 | 340.4326 | 0.09542 | 0 | 0 | 0.19084 | 340.7046 | 0.09601 | 0 | 0 | 0.19202 | 340.886 | 0.096403 | 0 | 0 | 0.19281 | 341.0674 | 0.096797 | 0 | 0 | 0.19359
2017-12-25 07:00 | 305.1385 | 0.9095 |  | 320.4151 | 0.052002 | 0 | 0 | 0.104 | 329.4191 | 0.071532 | 0 | 0 | 0.14306 | 336.7861 | 0.087511 | 0 | 0 | 0.17502 | 337.0589 | 0.088102 | 0 | 0 | 0.1762 | 337.2408 | 0.088497 | 0 | 0 | 0.17699 | 337.5136 | 0.089089 | 0 | 0 | 0.17818 | 337.7865 | 0.089681 | 0 | 0 | 0.17936 | 338.0593 | 0.090272 | 0 | 0 | 0.18054 | 338.4231 | 0.091061 | 0 | 0 | 0.18212 | 338.696 | 0.091653 | 0 | 0 | 0.18331 | 338.8779 | 0.092048 | 0 | 0 | 0.1841 | 339.1507 | 0.09264 | 0 | 0 | 0.18528 | 339.3326 | 0.093034 | 0 | 0 | 0.18607 | 339.6055 | 0.093626 | 0 | 0 | 0.18725 | 339.8783 | 0.094218 | 0 | 0 | 0.18844 | 340.0602 | 0.094612 | 0 | 0 | 0.18922 | 340.3331 | 0.095204 | 0 | 0 | 0.19041 | 340.6059 | 0.095796 | 0 | 0 | 0.19159 | 340.6969 | 0.095993 | 0 | 0 | 0.19199 | 340.9697 | 0.096585 | 0 | 0 | 0.19317 | 341.2426 | 0.097177 | 0 | 0 | 0.19435 | 341.4245 | 0.097571 | 0 | 0 | 0.19514 | 341.6973 | 0.098163 | 0 | 0 | 0.19633 | 341.8792 | 0.098558 | 0 | 0 | 0.19712 | 342.0611 | 0.098952 | 0 | 0 | 0.1979
2017-12-25 08:00 | 309 | 0.921 |  | 324.47 | 0.060797 | 0 | 0 | 0.12159 | 333.5879 | 0.080574 | 0 | 0 | 0.16115 | 341.0481 | 0.096755 | 0 | 0 | 0.19351 | 341.3244 | 0.097354 | 0 | 0 | 0.19471 | 341.5086 | 0.097754 | 0 | 0 | 0.19551 | 341.7849 | 0.098353 | 0 | 0 | 0.19671 | 342.0612 | 0.098952 | 0 | 0 | 0.1979 | 342.3375 | 0.099552 | 0 | 0 | 0.1991 | 342.7059 | 0.10035 | 0 | 0 | 0.2007 | 342.9822 | 0.10095 | 0 | 0 | 0.2019 | 343.1664 | 0.10135 | 0 | 0 | 0.2027 | 343.4427 | 0.10195 | 0 | 0 | 0.2039 | 343.6269 | 0.10235 | 0 | 0 | 0.2047 | 343.9032 | 0.10295 | 0 | 0 | 0.2059 | 344.1795 | 0.10355 | 0 | 0 | 0.20709 | 344.3637 | 0.10395 | 0 | 0 | 0.20789 | 344.64 | 0.10455 | 0 | 0 | 0.20909 | 344.9163 | 0.10515 | 0 | 0 | 0.21029 | 345.0084 | 0.10534 | 0 | 0 | 0.21069 | 345.2847 | 0.10594 | 0 | 0 | 0.21189 | 345.561 | 0.10654 | 0 | 0 | 0.21309 | 345.7452 | 0.10694 | 0 | 0 | 0.21389 | 346.0215 | 0.10754 | 0 | 0 | 0.21508 | 346.2057 | 0.10794 | 0 | 0 | 0.21588 | 346.3899 | 0.10834 | 0 | 0 | 0.21668
2017-12-25 09:00 | 309.013 | 0.92104 |  | 324.4836 | 0.060827 | 0 | 0 | 0.12165 | 333.6019 | 0.080604 | 0 | 0 | 0.16121 | 341.0624 | 0.096786 | 0 | 0 | 0.19357 | 341.3387 | 0.097385 | 0 | 0 | 0.19477 | 341.5229 | 0.097785 | 0 | 0 | 0.19557 | 341.7992 | 0.098384 | 0 | 0 | 0.19677 | 342.0755 | 0.098984 | 0 | 0 | 0.19797 | 342.3519 | 0.099583 | 0 | 0 | 0.19917 | 342.7203 | 0.10038 | 0 | 0 | 0.20076 | 342.9966 | 0.10098 | 0 | 0 | 0.20196 | 343.1808 | 0.10138 | 0 | 0 | 0.20276 | 343.4571 | 0.10198 | 0 | 0 | 0.20396 | 343.6413 | 0.10238 | 0 | 0 | 0.20476 | 343.9176 | 0.10298 | 0 | 0 | 0.20596 | 344.1939 | 0.10358 | 0 | 0 | 0.20716 | 344.3782 | 0.10398 | 0 | 0 | 0.20796 | 344.6545 | 0.10458 | 0 | 0 | 0.20915 | 344.9308 | 0.10518 | 0 | 0 | 0.21035 | 345.0229 | 0.10538 | 0 | 0 | 0.21075 | 345.2992 | 0.10598 | 0 | 0 | 0.21195 | 345.5755 | 0.10657 | 0 | 0 | 0.21315 | 345.7597 | 0.10697 | 0 | 0 | 0.21395 | 346.036 | 0.10757 | 0 | 0 | 0.21515 | 346.2202 | 0.10797 | 0 | 0 | 0.21595 | 346.4045 | 0.10837 | 0 | 0 | 0.21675
2017-12-25 10:00 | 306.1188 | 0.91242 |  | 321.4446 | 0.054235 | 0 | 0 | 0.10847 | 330.4775 | 0.073827 | 0 | 0 | 0.14765 | 337.8681 | 0.089858 | 0 | 0 | 0.17972 | 338.1418 | 0.090451 | 0 | 0 | 0.1809 | 338.3243 | 0.090847 | 0 | 0 | 0.18169 | 338.598 | 0.091441 | 0 | 0 | 0.18288 | 338.8718 | 0.092034 | 0 | 0 | 0.18407 | 339.1455 | 0.092628 | 0 | 0 | 0.18526 | 339.5104 | 0.09342 | 0 | 0 | 0.18684 | 339.7842 | 0.094014 | 0 | 0 | 0.18803 | 339.9667 | 0.094409 | 0 | 0 | 0.18882 | 340.2404 | 0.095003 | 0 | 0 | 0.19001 | 340.4229 | 0.095399 | 0 | 0 | 0.1908 | 340.6966 | 0.095993 | 0 | 0 | 0.19199 | 340.9703 | 0.096586 | 0 | 0 | 0.19317 | 341.1528 | 0.096982 | 0 | 0 | 0.19396 | 341.4265 | 0.097576 | 0 | 0 | 0.19515 | 341.7002 | 0.098169 | 0 | 0 | 0.19634 | 341.7915 | 0.098367 | 0 | 0 | 0.19673 | 342.0652 | 0.098961 | 0 | 0 | 0.19792 | 342.3389 | 0.099555 | 0 | 0 | 0.19911 | 342.5214 | 0.099951 | 0 | 0 | 0.1999 | 342.7951 | 0.10054 | 0 | 0 | 0.20109 | 342.9776 | 0.10094 | 0 | 0 | 0.20188 | 343.1601 | 0.10134 | 0 | 0 | 0.20267
2017-12-25 11:00 | 310.2834 | 0.92483 |  | 325.8177 | 0.06372 | 0 | 0 | 0.12744 | 334.9735 | 0.083579 | 0 | 0 | 0.16716 | 342.4646 | 0.099827 | 0 | 0 | 0.19965 | 342.7421 | 0.10043 | 0 | 0 | 0.20086 | 342.927 | 0.10083 | 0 | 0 | 0.20166 | 343.2045 | 0.10143 | 0 | 0 | 0.20286 | 343.4819 | 0.10203 | 0 | 0 | 0.20407 | 343.7594 | 0.10264 | 0 | 0 | 0.20527 | 344.1293 | 0.10344 | 0 | 0 | 0.20688 | 344.4067 | 0.10404 | 0 | 0 | 0.20808 | 344.5917 | 0.10444 | 0 | 0 | 0.20888 | 344.8692 | 0.10504 | 0 | 0 | 0.21009 | 345.0541 | 0.10544 | 0 | 0 | 0.21089 | 345.3316 | 0.10605 | 0 | 0 | 0.21209 | 345.609 | 0.10665 | 0 | 0 | 0.2133 | 345.794 | 0.10705 | 0 | 0 | 0.2141 | 346.0714 | 0.10765 | 0 | 0 | 0.2153 | 346.3489 | 0.10825 | 0 | 0 | 0.2165 | 346.4414 | 0.10845 | 0 | 0 | 0.21691 | 346.7188 | 0.10905 | 0 | 0 | 0.21811 | 346.9963 | 0.10966 | 0 | 0 | 0.21931 | 347.1812 | 0.11006 | 0 | 0 | 0.22012 | 347.4587 | 0.11066 | 0 | 0 | 0.22132 | 347.6437 | 0.11106 | 0 | 0 | 0.22212 | 347.8286 | 0.11146 | 0 | 0 | 0.22292
2017-12-25 12:00 | 309.7495 | 0.92324 |  | 325.257 | 0.062504 | 0 | 0 | 0.12501 | 334.3971 | 0.082329 | 0 | 0 | 0.16466 | 341.8753 | 0.098549 | 0 | 0 | 0.1971 | 342.1523 | 0.09915 | 0 | 0 | 0.1983 | 342.3369 | 0.09955 | 0 | 0 | 0.1991 | 342.6139 | 0.10015 | 0 | 0 | 0.2003 | 342.8909 | 0.10075 | 0 | 0 | 0.2015 | 343.1678 | 0.10135 | 0 | 0 | 0.20271 | 343.5371 | 0.10215 | 0 | 0 | 0.20431 | 343.8141 | 0.10275 | 0 | 0 | 0.20551 | 343.9988 | 0.10315 | 0 | 0 | 0.20631 | 344.2757 | 0.10376 | 0 | 0 | 0.20751 | 344.4604 | 0.10416 | 0 | 0 | 0.20831 | 344.7373 | 0.10476 | 0 | 0 | 0.20951 | 345.0143 | 0.10536 | 0 | 0 | 0.21072 | 345.199 | 0.10576 | 0 | 0 | 0.21152 | 345.4759 | 0.10636 | 0 | 0 | 0.21272 | 345.7529 | 0.10696 | 0 | 0 | 0.21392 | 345.8452 | 0.10716 | 0 | 0 | 0.21432 | 346.1222 | 0.10776 | 0 | 0 | 0.21552 | 346.3992 | 0.10836 | 0 | 0 | 0.21672 | 346.5838 | 0.10876 | 0 | 0 | 0.21752 | 346.8608 | 0.10936 | 0 | 0 | 0.21873 | 347.0454 | 0.10976 | 0 | 0 | 0.21953 | 347.2301 | 0.11016 | 0 | 0 | 0.22033
2017-12-25 13:00 | 309.9972 | 0.92398 |  | 325.5171 | 0.063068 | 0 | 0 | 0.12614 | 334.6644 | 0.082909 | 0 | 0 | 0.16582 | 342.1487 | 0.099142 | 0 | 0 | 0.19828 | 342.4259 | 0.099743 | 0 | 0 | 0.19949 | 342.6107 | 0.10014 | 0 | 0 | 0.20029 | 342.8878 | 0.10075 | 0 | 0 | 0.20149 | 343.165 | 0.10135 | 0 | 0 | 0.20269 | 343.4422 | 0.10195 | 0 | 0 | 0.2039 | 343.8118 | 0.10275 | 0 | 0 | 0.2055 | 344.089 | 0.10335 | 0 | 0 | 0.2067 | 344.2738 | 0.10375 | 0 | 0 | 0.2075 | 344.551 | 0.10435 | 0 | 0 | 0.20871 | 344.7358 | 0.10475 | 0 | 0 | 0.20951 | 345.013 | 0.10535 | 0 | 0 | 0.21071 | 345.2902 | 0.10596 | 0 | 0 | 0.21191 | 345.475 | 0.10636 | 0 | 0 | 0.21271 | 345.7522 | 0.10696 | 0 | 0 | 0.21392 | 346.0294 | 0.10756 | 0 | 0 | 0.21512 | 346.1218 | 0.10776 | 0 | 0 | 0.21552 | 346.399 | 0.10836 | 0 | 0 | 0.21672 | 346.6761 | 0.10896 | 0 | 0 | 0.21792 | 346.8609 | 0.10936 | 0 | 0 | 0.21873 | 347.1381 | 0.10996 | 0 | 0 | 0.21993 | 347.3229 | 0.11037 | 0 | 0 | 0.22073 | 347.5077 | 0.11077 | 0 | 0 | 0.22153
2017-12-25 14:00 | 310.2556 | 0.92475 |  | 325.7885 | 0.063657 | 0 | 0 | 0.12731 | 334.9435 | 0.083514 | 0 | 0 | 0.16703 | 342.4339 | 0.099761 | 0 | 0 | 0.19952 | 342.7114 | 0.10036 | 0 | 0 | 0.20073 | 342.8963 | 0.10076 | 0 | 0 | 0.20153 | 343.1737 | 0.10137 | 0 | 0 | 0.20273 | 343.4512 | 0.10197 | 0 | 0 | 0.20393 | 343.7286 | 0.10257 | 0 | 0 | 0.20514 | 344.0985 | 0.10337 | 0 | 0 | 0.20674 | 344.3759 | 0.10397 | 0 | 0 | 0.20795 | 344.5608 | 0.10437 | 0 | 0 | 0.20875 | 344.8383 | 0.10498 | 0 | 0 | 0.20995 | 345.0232 | 0.10538 | 0 | 0 | 0.21075 | 345.3006 | 0.10598 | 0 | 0 | 0.21196 | 345.5781 | 0.10658 | 0 | 0 | 0.21316 | 345.763 | 0.10698 | 0 | 0 | 0.21396 | 346.0404 | 0.10758 | 0 | 0 | 0.21517 | 346.3179 | 0.10819 | 0 | 0 | 0.21637 | 346.4103 | 0.10839 | 0 | 0 | 0.21677 | 346.6878 | 0.10899 | 0 | 0 | 0.21797 | 346.9652 | 0.10959 | 0 | 0 | 0.21918 | 347.1501 | 0.10999 | 0 | 0 | 0.21998 | 347.4276 | 0.11059 | 0 | 0 | 0.22118 | 347.6125 | 0.11099 | 0 | 0 | 0.22199 | 347.7975 | 0.11139 | 0 | 0 | 0.22279
2017-12-25 15:00 | 304.3221 | 0.90706 |  | 319.558 | 0.050143 | 0 | 0 | 0.10029 | 328.5379 | 0.06962 | 0 | 0 | 0.13924 | 335.8851 | 0.085556 | 0 | 0 | 0.17111 | 336.1572 | 0.086147 | 0 | 0 | 0.17229 | 336.3386 | 0.08654 | 0 | 0 | 0.17308 | 336.6107 | 0.08713 | 0 | 0 | 0.17426 | 336.8828 | 0.087721 | 0 | 0 | 0.17544 | 337.155 | 0.088311 | 0 | 0 | 0.17662 | 337.5178 | 0.089098 | 0 | 0 | 0.1782 | 337.7899 | 0.089688 | 0 | 0 | 0.17938 | 337.9713 | 0.090081 | 0 | 0 | 0.18016 | 338.2434 | 0.090672 | 0 | 0 | 0.18134 | 338.4248 | 0.091065 | 0 | 0 | 0.18213 | 338.697 | 0.091655 | 0 | 0 | 0.18331 | 338.9691 | 0.092246 | 0 | 0 | 0.18449 | 339.1505 | 0.092639 | 0 | 0 | 0.18528 | 339.4226 | 0.093229 | 0 | 0 | 0.18646 | 339.6947 | 0.09382 | 0 | 0 | 0.18764 | 339.7854 | 0.094016 | 0 | 0 | 0.18803 | 340.0576 | 0.094606 | 0 | 0 | 0.18921 | 340.3297 | 0.095197 | 0 | 0 | 0.19039 | 340.5111 | 0.09559 | 0 | 0 | 0.19118 | 340.7832 | 0.09618 | 0 | 0 | 0.19236 | 340.9646 | 0.096574 | 0 | 0 | 0.19315 | 341.146 | 0.096967 | 0 | 0 | 0.19393
2017-12-25 16:00 | 313.4109 | 0.93415 |  | 329.1017 | 0.070843 | 0 | 0 | 0.14169 | 338.3498 | 0.090902 | 0 | 0 | 0.1818 | 345.9165 | 0.10731 | 0 | 0 | 0.21463 | 346.1967 | 0.10792 | 0 | 0 | 0.21584 | 346.3835 | 0.10833 | 0 | 0 | 0.21666 | 346.6638 | 0.10894 | 0 | 0 | 0.21787 | 346.944 | 0.10954 | 0 | 0 | 0.21909 | 347.2243 | 0.11015 | 0 | 0 | 0.2203 | 347.5979 | 0.11096 | 0 | 0 | 0.22192 | 347.8782 | 0.11157 | 0 | 0 | 0.22314 | 348.065 | 0.11197 | 0 | 0 | 0.22395 | 348.3452 | 0.11258 | 0 | 0 | 0.22516 | 348.5321 | 0.11299 | 0 | 0 | 0.22598 | 348.8123 | 0.1136 | 0 | 0 | 0.22719 | 349.0926 | 0.1142 | 0 | 0 | 0.22841 | 349.2794 | 0.11461 | 0 | 0 | 0.22922 | 349.5596 | 0.11522 | 0 | 0 | 0.23043 | 349.8399 | 0.11582 | 0 | 0 | 0.23165 | 349.9333 | 0.11603 | 0 | 0 | 0.23205 | 350.2136 | 0.11663 | 0 | 0 | 0.23327 | 350.4938 | 0.11724 | 0 | 0 | 0.23449 | 350.6806 | 0.11765 | 0 | 0 | 0.2353 | 350.9609 | 0.11826 | 0 | 0 | 0.23651 | 351.1477 | 0.11866 | 0 | 0 | 0.23732 | 351.3345 | 0.11907 | 0 | 0 | 0.23813
2017-12-25 17:00 | 310.1816 | 0.92453 |  | 325.7108 | 0.063488 | 0 | 0 | 0.12698 | 334.8636 | 0.083341 | 0 | 0 | 0.16668 | 342.3523 | 0.099584 | 0 | 0 | 0.19917 | 342.6296 | 0.10019 | 0 | 0 | 0.20037 | 342.8145 | 0.10059 | 0 | 0 | 0.20117 | 343.0919 | 0.10119 | 0 | 0 | 0.20238 | 343.3693 | 0.10179 | 0 | 0 | 0.20358 | 343.6466 | 0.10239 | 0 | 0 | 0.20478 | 344.0164 | 0.10319 | 0 | 0 | 0.20639 | 344.2938 | 0.10379 | 0 | 0 | 0.20759 | 344.4787 | 0.1042 | 0 | 0 | 0.20839 | 344.7561 | 0.1048 | 0 | 0 | 0.2096 | 344.941 | 0.1052 | 0 | 0 | 0.2104 | 345.2183 | 0.1058 | 0 | 0 | 0.2116 | 345.4957 | 0.1064 | 0 | 0 | 0.2128 | 345.6806 | 0.1068 | 0 | 0 | 0.21361 | 345.9579 | 0.1074 | 0 | 0 | 0.21481 | 346.2353 | 0.10801 | 0 | 0 | 0.21601 | 346.3278 | 0.10821 | 0 | 0 | 0.21641 | 346.6051 | 0.10881 | 0 | 0 | 0.21762 | 346.8825 | 0.10941 | 0 | 0 | 0.21882 | 347.0674 | 0.10981 | 0 | 0 | 0.21962 | 347.3447 | 0.11041 | 0 | 0 | 0.22082 | 347.5296 | 0.11081 | 0 | 0 | 0.22163 | 347.7145 | 0.11121 | 0 | 0 | 0.22243
2017-12-25 18:00 | 311.4057 | 0.92818 |  | 326.9961 | 0.066276 | 0 | 0 | 0.13255 | 336.1851 | 0.086207 | 0 | 0 | 0.17241 | 343.7033 | 0.10251 | 0 | 0 | 0.20503 | 343.9817 | 0.10312 | 0 | 0 | 0.20624 | 344.1674 | 0.10352 | 0 | 0 | 0.20704 | 344.4458 | 0.10412 | 0 | 0 | 0.20825 | 344.7243 | 0.10473 | 0 | 0 | 0.20946 | 345.0027 | 0.10533 | 0 | 0 | 0.21067 | 345.374 | 0.10614 | 0 | 0 | 0.21228 | 345.6525 | 0.10674 | 0 | 0 | 0.21348 | 345.8381 | 0.10714 | 0 | 0 | 0.21429 | 346.1165 | 0.10775 | 0 | 0 | 0.2155 | 346.3022 | 0.10815 | 0 | 0 | 0.2163 | 346.5806 | 0.10876 | 0 | 0 | 0.21751 | 346.8591 | 0.10936 | 0 | 0 | 0.21872 | 347.0447 | 0.10976 | 0 | 0 | 0.21952 | 347.3232 | 0.11037 | 0 | 0 | 0.22073 | 347.6016 | 0.11097 | 0 | 0 | 0.22194 | 347.6944 | 0.11117 | 0 | 0 | 0.22234 | 347.9729 | 0.11177 | 0 | 0 | 0.22355 | 348.2513 | 0.11238 | 0 | 0 | 0.22476 | 348.437 | 0.11278 | 0 | 0 | 0.22556 | 348.7154 | 0.11339 | 0 | 0 | 0.22677 | 348.9011 | 0.11379 | 0 | 0 | 0.22758 | 349.0867 | 0.11419 | 0 | 0 | 0.22838
2017-12-25 19:00 | 314.1107 | 0.93624 |  | 329.8365 | 0.072437 | 0 | 0 | 0.14487 | 339.1053 | 0.092541 | 0 | 0 | 0.18508 | 346.6888 | 0.10899 | 0 | 0 | 0.21798 | 346.9697 | 0.1096 | 0 | 0 | 0.2192 | 347.1569 | 0.11 | 0 | 0 | 0.22001 | 347.4378 | 0.11061 | 0 | 0 | 0.22123 | 347.7187 | 0.11122 | 0 | 0 | 0.22245 | 347.9995 | 0.11183 | 0 | 0 | 0.22367 | 348.374 | 0.11264 | 0 | 0 | 0.22529 | 348.6549 | 0.11325 | 0 | 0 | 0.22651 | 348.8421 | 0.11366 | 0 | 0 | 0.22732 | 349.123 | 0.11427 | 0 | 0 | 0.22854 | 349.3103 | 0.11468 | 0 | 0 | 0.22935 | 349.5911 | 0.11528 | 0 | 0 | 0.23057 | 349.872 | 0.11589 | 0 | 0 | 0.23179 | 350.0593 | 0.1163 | 0 | 0 | 0.2326 | 350.3401 | 0.11691 | 0 | 0 | 0.23382 | 350.621 | 0.11752 | 0 | 0 | 0.23504 | 350.7146 | 0.11772 | 0 | 0 | 0.23544 | 350.9955 | 0.11833 | 0 | 0 | 0.23666 | 351.2764 | 0.11894 | 0 | 0 | 0.23788 | 351.4636 | 0.11935 | 0 | 0 | 0.23869 | 351.7445 | 0.11996 | 0 | 0 | 0.23991 | 351.9317 | 0.12036 | 0 | 0 | 0.24072 | 352.119 | 0.12077 | 0 | 0 | 0.24154
2017-12-25 20:00 | 310.0393 | 0.9241 |  | 325.5613 | 0.063164 | 0 | 0 | 0.12633 | 334.7099 | 0.083007 | 0 | 0 | 0.16601 | 342.1952 | 0.099243 | 0 | 0 | 0.19849 | 342.4724 | 0.099844 | 0 | 0 | 0.19969 | 342.6572 | 0.10025 | 0 | 0 | 0.20049 | 342.9345 | 0.10085 | 0 | 0 | 0.20169 | 343.2117 | 0.10145 | 0 | 0 | 0.2029 | 343.4889 | 0.10205 | 0 | 0 | 0.2041 | 343.8586 | 0.10285 | 0 | 0 | 0.2057 | 344.1358 | 0.10345 | 0 | 0 | 0.2069 | 344.3206 | 0.10385 | 0 | 0 | 0.20771 | 344.5978 | 0.10445 | 0 | 0 | 0.20891 | 344.7827 | 0.10486 | 0 | 0 | 0.20971 | 345.0599 | 0.10546 | 0 | 0 | 0.21091 | 345.3371 | 0.10606 | 0 | 0 | 0.21212 | 345.5219 | 0.10646 | 0 | 0 | 0.21292 | 345.7992 | 0.10706 | 0 | 0 | 0.21412 | 346.0764 | 0.10766 | 0 | 0 | 0.21532 | 346.1688 | 0.10786 | 0 | 0 | 0.21572 | 346.446 | 0.10846 | 0 | 0 | 0.21693 | 346.7233 | 0.10906 | 0 | 0 | 0.21813 | 346.9081 | 0.10947 | 0 | 0 | 0.21893 | 347.1853 | 0.11007 | 0 | 0 | 0.22013 | 347.3701 | 0.11047 | 0 | 0 | 0.22093 | 347.555 | 0.11087 | 0 | 0 | 0.22174
2017-12-25 21:00 | 312.691 | 0.93201 |  | 328.3458 | 0.069204 | 0 | 0 | 0.13841 | 337.5726 | 0.089217 | 0 | 0 | 0.17843 | 345.1219 | 0.10559 | 0 | 0 | 0.21118 | 345.4015 | 0.1062 | 0 | 0 | 0.21239 | 345.5879 | 0.1066 | 0 | 0 | 0.2132 | 345.8675 | 0.10721 | 0 | 0 | 0.21442 | 346.1471 | 0.10781 | 0 | 0 | 0.21563 | 346.4267 | 0.10842 | 0 | 0 | 0.21684 | 346.7995 | 0.10923 | 0 | 0 | 0.21846 | 347.0791 | 0.10984 | 0 | 0 | 0.21967 | 347.2655 | 0.11024 | 0 | 0 | 0.22048 | 347.5451 | 0.11085 | 0 | 0 | 0.22169 | 347.7315 | 0.11125 | 0 | 0 | 0.2225 | 348.0111 | 0.11186 | 0 | 0 | 0.22372 | 348.2907 | 0.11246 | 0 | 0 | 0.22493 | 348.4771 | 0.11287 | 0 | 0 | 0.22574 | 348.7567 | 0.11347 | 0 | 0 | 0.22695 | 349.0363 | 0.11408 | 0 | 0 | 0.22816 | 349.1295 | 0.11428 | 0 | 0 | 0.22857 | 349.4091 | 0.11489 | 0 | 0 | 0.22978 | 349.6887 | 0.1155 | 0 | 0 | 0.23099 | 349.8751 | 0.1159 | 0 | 0 | 0.2318 | 350.1547 | 0.11651 | 0 | 0 | 0.23301 | 350.3411 | 0.11691 | 0 | 0 | 0.23382 | 350.5275 | 0.11732 | 0 | 0 | 0.23463
2017-12-25 22:00 | 315.5424 | 0.9405 |  | 331.3399 | 0.075698 | 0 | 0 | 0.1514 | 340.6509 | 0.095893 | 0 | 0 | 0.19179 | 348.269 | 0.11242 | 0 | 0 | 0.22483 | 348.5511 | 0.11303 | 0 | 0 | 0.22606 | 348.7393 | 0.11344 | 0 | 0 | 0.22687 | 349.0214 | 0.11405 | 0 | 0 | 0.2281 | 349.3036 | 0.11466 | 0 | 0 | 0.22932 | 349.5857 | 0.11527 | 0 | 0 | 0.23055 | 349.9619 | 0.11609 | 0 | 0 | 0.23218 | 350.2441 | 0.1167 | 0 | 0 | 0.2334 | 350.4322 | 0.11711 | 0 | 0 | 0.23422 | 350.7143 | 0.11772 | 0 | 0 | 0.23544 | 350.9024 | 0.11813 | 0 | 0 | 0.23626 | 351.1846 | 0.11874 | 0 | 0 | 0.23748 | 351.4667 | 0.11935 | 0 | 0 | 0.23871 | 351.6548 | 0.11976 | 0 | 0 | 0.23952 | 351.937 | 0.12037 | 0 | 0 | 0.24075 | 352.2191 | 0.12098 | 0 | 0 | 0.24197 | 352.3132 | 0.12119 | 0 | 0 | 0.24238 | 352.5953 | 0.1218 | 0 | 0 | 0.2436 | 352.8775 | 0.12241 | 0 | 0 | 0.24483 | 353.0656 | 0.12282 | 0 | 0 | 0.24564 | 353.3477 | 0.12343 | 0 | 0 | 0.24687 | 353.5358 | 0.12384 | 0 | 0 | 0.24768 | 353.7239 | 0.12425 | 0 | 0 | 0.2485
2017-12-25 23:00 | 318.0248 | 0.9479 |  | 333.9467 | 0.081352 | 0 | 0 | 0.1627 | 343.3309 | 0.10171 | 0 | 0 | 0.20341 | 351.0089 | 0.11836 | 0 | 0 | 0.23672 | 351.2933 | 0.11898 | 0 | 0 | 0.23795 | 351.4829 | 0.11939 | 0 | 0 | 0.23878 | 351.7673 | 0.12 | 0 | 0 | 0.24001 | 352.0516 | 0.12062 | 0 | 0 | 0.24124 | 352.336 | 0.12124 | 0 | 0 | 0.24248 | 352.7152 | 0.12206 | 0 | 0 | 0.24412 | 352.9995 | 0.12268 | 0 | 0 | 0.24536 | 353.1891 | 0.12309 | 0 | 0 | 0.24618 | 353.4735 | 0.12371 | 0 | 0 | 0.24741 | 353.6631 | 0.12412 | 0 | 0 | 0.24823 | 353.9474 | 0.12473 | 0 | 0 | 0.24947 | 354.2318 | 0.12535 | 0 | 0 | 0.2507 | 354.4214 | 0.12576 | 0 | 0 | 0.25152 | 354.7058 | 0.12638 | 0 | 0 | 0.25276 | 354.9901 | 0.127 | 0 | 0 | 0.25399 | 355.0849 | 0.1272 | 0 | 0 | 0.2544 | 355.3693 | 0.12782 | 0 | 0 | 0.25564 | 355.6537 | 0.12843 | 0 | 0 | 0.25687 | 355.8433 | 0.12885 | 0 | 0 | 0.25769 | 356.1276 | 0.12946 | 0 | 0 | 0.25892 | 356.3172 | 0.12987 | 0 | 0 | 0.25975 | 356.5068 | 0.13028 | 0 | 0 | 0.26057
2017-12-26 | 309.2074 | 0.92162 |  | 324.6878 | 0.061269 | 0 | 0 | 0.12254 | 333.8118 | 0.081059 | 0 | 0 | 0.16212 | 341.277 | 0.097251 | 0 | 0 | 0.1945 | 341.5535 | 0.097851 | 0 | 0 | 0.1957 | 341.7378 | 0.098251 | 0 | 0 | 0.1965 | 342.0143 | 0.098851 | 0 | 0 | 0.1977 | 342.2908 | 0.09945 | 0 | 0 | 0.1989 | 342.5672 | 0.10005 | 0 | 0 | 0.2001 | 342.9359 | 0.10085 | 0 | 0 | 0.2017 | 343.2124 | 0.10145 | 0 | 0 | 0.2029 | 343.3967 | 0.10185 | 0 | 0 | 0.2037 | 343.6732 | 0.10245 | 0 | 0 | 0.2049 | 343.8575 | 0.10285 | 0 | 0 | 0.2057 | 344.134 | 0.10345 | 0 | 0 | 0.2069 | 344.4105 | 0.10405 | 0 | 0 | 0.2081 | 344.5948 | 0.10445 | 0 | 0 | 0.2089 | 344.8713 | 0.10505 | 0 | 0 | 0.21009 | 345.1478 | 0.10565 | 0 | 0 | 0.21129 | 345.2399 | 0.10585 | 0 | 0 | 0.21169 | 345.5164 | 0.10645 | 0 | 0 | 0.21289 | 345.7929 | 0.10705 | 0 | 0 | 0.21409 | 345.9772 | 0.10745 | 0 | 0 | 0.21489 | 346.2537 | 0.10805 | 0 | 0 | 0.21609 | 346.4381 | 0.10845 | 0 | 0 | 0.21689 | 346.6224 | 0.10885 | 0 | 0 | 0.21769
2017-12-26 01:00 | 314.5789 | 0.93763 |  | 330.3282 | 0.073504 | 0 | 0 | 0.14701 | 339.6108 | 0.093637 | 0 | 0 | 0.18727 | 347.2056 | 0.11011 | 0 | 0 | 0.22022 | 347.4869 | 0.11072 | 0 | 0 | 0.22144 | 347.6745 | 0.11113 | 0 | 0 | 0.22226 | 347.9557 | 0.11174 | 0 | 0 | 0.22348 | 348.237 | 0.11235 | 0 | 0 | 0.2247 | 348.5183 | 0.11296 | 0 | 0 | 0.22592 | 348.8934 | 0.11377 | 0 | 0 | 0.22754 | 349.1747 | 0.11438 | 0 | 0 | 0.22876 | 349.3622 | 0.11479 | 0 | 0 | 0.22958 | 349.6435 | 0.1154 | 0 | 0 | 0.2308 | 349.831 | 0.11581 | 0 | 0 | 0.23161 | 350.1123 | 0.11642 | 0 | 0 | 0.23283 | 350.3936 | 0.11703 | 0 | 0 | 0.23405 | 350.5811 | 0.11743 | 0 | 0 | 0.23486 | 350.8624 | 0.11804 | 0 | 0 | 0.23608 | 351.1437 | 0.11865 | 0 | 0 | 0.2373 | 351.2375 | 0.11886 | 0 | 0 | 0.23771 | 351.5188 | 0.11947 | 0 | 0 | 0.23893 | 351.8 | 0.12008 | 0 | 0 | 0.24015 | 351.9876 | 0.12048 | 0 | 0 | 0.24097 | 352.2689 | 0.12109 | 0 | 0 | 0.24219 | 352.4564 | 0.1215 | 0 | 0 | 0.243 | 352.6439 | 0.12191 | 0 | 0 | 0.24381
2017-12-26 02:00 | 310.7717 | 0.92629 |  | 326.3304 | 0.064832 | 0 | 0 | 0.12966 | 335.5006 | 0.084723 | 0 | 0 | 0.16945 | 343.0035 | 0.101 | 0 | 0 | 0.20199 | 343.2814 | 0.1016 | 0 | 0 | 0.2032 | 343.4667 | 0.102 | 0 | 0 | 0.204 | 343.7446 | 0.1026 | 0 | 0 | 0.20521 | 344.0225 | 0.10321 | 0 | 0 | 0.20641 | 344.3003 | 0.10381 | 0 | 0 | 0.20762 | 344.6709 | 0.10461 | 0 | 0 | 0.20923 | 344.9487 | 0.10522 | 0 | 0 | 0.21043 | 345.134 | 0.10562 | 0 | 0 | 0.21123 | 345.4119 | 0.10622 | 0 | 0 | 0.21244 | 345.5971 | 0.10662 | 0 | 0 | 0.21324 | 345.875 | 0.10722 | 0 | 0 | 0.21445 | 346.1529 | 0.10783 | 0 | 0 | 0.21565 | 346.3382 | 0.10823 | 0 | 0 | 0.21646 | 346.6161 | 0.10883 | 0 | 0 | 0.21766 | 346.8939 | 0.10943 | 0 | 0 | 0.21887 | 346.9866 | 0.10964 | 0 | 0 | 0.21927 | 347.2645 | 0.11024 | 0 | 0 | 0.22048 | 347.5423 | 0.11084 | 0 | 0 | 0.22168 | 347.7276 | 0.11124 | 0 | 0 | 0.22249 | 348.0055 | 0.11185 | 0 | 0 | 0.22369 | 348.1907 | 0.11225 | 0 | 0 | 0.22449 | 348.376 | 0.11265 | 0 | 0 | 0.2253
2017-12-26 03:00 | 312.5317 | 0.93153 |  | 328.1785 | 0.068841 | 0 | 0 | 0.13768 | 337.4007 | 0.088844 | 0 | 0 | 0.17769 | 344.9461 | 0.10521 | 0 | 0 | 0.21042 | 345.2255 | 0.10582 | 0 | 0 | 0.21163 | 345.4118 | 0.10622 | 0 | 0 | 0.21244 | 345.6913 | 0.10683 | 0 | 0 | 0.21365 | 345.9708 | 0.10743 | 0 | 0 | 0.21486 | 346.2502 | 0.10804 | 0 | 0 | 0.21608 | 346.6228 | 0.10885 | 0 | 0 | 0.21769 | 346.9023 | 0.10945 | 0 | 0 | 0.21891 | 347.0886 | 0.10986 | 0 | 0 | 0.21971 | 347.3681 | 0.11046 | 0 | 0 | 0.22093 | 347.5544 | 0.11087 | 0 | 0 | 0.22173 | 347.8338 | 0.11147 | 0 | 0 | 0.22295 | 348.1133 | 0.11208 | 0 | 0 | 0.22416 | 348.2996 | 0.11248 | 0 | 0 | 0.22497 | 348.579 | 0.11309 | 0 | 0 | 0.22618 | 348.8585 | 0.1137 | 0 | 0 | 0.22739 | 348.9517 | 0.1139 | 0 | 0 | 0.2278 | 349.2311 | 0.1145 | 0 | 0 | 0.22901 | 349.5106 | 0.11511 | 0 | 0 | 0.23022 | 349.6969 | 0.11551 | 0 | 0 | 0.23103 | 349.9763 | 0.11612 | 0 | 0 | 0.23224 | 350.1627 | 0.11652 | 0 | 0 | 0.23305 | 350.349 | 0.11693 | 0 | 0 | 0.23386
2017-12-26 04:00 | 308.7733 | 0.92033 |  | 324.2319 | 0.060281 | 0 | 0 | 0.12056 | 333.3432 | 0.080043 | 0 | 0 | 0.16009 | 340.7978 | 0.096212 | 0 | 0 | 0.19242 | 341.0739 | 0.096811 | 0 | 0 | 0.19362 | 341.258 | 0.09721 | 0 | 0 | 0.19442 | 341.5341 | 0.097809 | 0 | 0 | 0.19562 | 341.8102 | 0.098408 | 0 | 0 | 0.19682 | 342.0863 | 0.099007 | 0 | 0 | 0.19801 | 342.4544 | 0.099805 | 0 | 0 | 0.19961 | 342.7305 | 0.1004 | 0 | 0 | 0.20081 | 342.9146 | 0.1008 | 0 | 0 | 0.20161 | 343.1907 | 0.1014 | 0 | 0 | 0.2028 | 343.3747 | 0.1018 | 0 | 0 | 0.2036 | 343.6508 | 0.1024 | 0 | 0 | 0.2048 | 343.9269 | 0.103 | 0 | 0 | 0.206 | 344.111 | 0.1034 | 0 | 0 | 0.2068 | 344.3871 | 0.104 | 0 | 0 | 0.20799 | 344.6632 | 0.1046 | 0 | 0 | 0.20919 | 344.7552 | 0.1048 | 0 | 0 | 0.20959 | 345.0313 | 0.10539 | 0 | 0 | 0.21079 | 345.3074 | 0.10599 | 0 | 0 | 0.21199 | 345.4915 | 0.10639 | 0 | 0 | 0.21279 | 345.7676 | 0.10699 | 0 | 0 | 0.21398 | 345.9517 | 0.10739 | 0 | 0 | 0.21478 | 346.1357 | 0.10779 | 0 | 0 | 0.21558
2017-12-26 05:00 | 307.6125 | 0.91687 |  | 323.013 | 0.057637 | 0 | 0 | 0.11527 | 332.09 | 0.077325 | 0 | 0 | 0.15465 | 339.5166 | 0.093433 | 0 | 0 | 0.18687 | 339.7917 | 0.09403 | 0 | 0 | 0.18806 | 339.9751 | 0.094428 | 0 | 0 | 0.18886 | 340.2501 | 0.095024 | 0 | 0 | 0.19005 | 340.5252 | 0.095621 | 0 | 0 | 0.19124 | 340.8003 | 0.096217 | 0 | 0 | 0.19243 | 341.167 | 0.097013 | 0 | 0 | 0.19403 | 341.4421 | 0.097609 | 0 | 0 | 0.19522 | 341.6254 | 0.098007 | 0 | 0 | 0.19601 | 341.9005 | 0.098604 | 0 | 0 | 0.19721 | 342.0839 | 0.099002 | 0 | 0 | 0.198 | 342.3589 | 0.099598 | 0 | 0 | 0.1992 | 342.634 | 0.10019 | 0 | 0 | 0.20039 | 342.8174 | 0.10059 | 0 | 0 | 0.20119 | 343.0924 | 0.10119 | 0 | 0 | 0.20238 | 343.3675 | 0.10179 | 0 | 0 | 0.20357 | 343.4592 | 0.10198 | 0 | 0 | 0.20397 | 343.7342 | 0.10258 | 0 | 0 | 0.20516 | 344.0093 | 0.10318 | 0 | 0 | 0.20636 | 344.1927 | 0.10358 | 0 | 0 | 0.20715 | 344.4677 | 0.10417 | 0 | 0 | 0.20834 | 344.6511 | 0.10457 | 0 | 0 | 0.20914 | 344.8345 | 0.10497 | 0 | 0 | 0.20994
2017-12-26 06:00 | 298.4613 | 0.88959 |  | 313.4037 | 0.036794 | 0 | 0 | 0.073588 | 322.2106 | 0.055896 | 0 | 0 | 0.11179 | 329.4163 | 0.071526 | 0 | 0 | 0.14305 | 329.6832 | 0.072105 | 0 | 0 | 0.14421 | 329.8611 | 0.07249 | 0 | 0 | 0.14498 | 330.128 | 0.073069 | 0 | 0 | 0.14614 | 330.3949 | 0.073648 | 0 | 0 | 0.1473 | 330.6618 | 0.074227 | 0 | 0 | 0.14845 | 331.0176 | 0.074999 | 0 | 0 | 0.15 | 331.2845 | 0.075578 | 0 | 0 | 0.15116 | 331.4624 | 0.075964 | 0 | 0 | 0.15193 | 331.7293 | 0.076542 | 0 | 0 | 0.15308 | 331.9072 | 0.076928 | 0 | 0 | 0.15386 | 332.1741 | 0.077507 | 0 | 0 | 0.15501 | 332.4409 | 0.078086 | 0 | 0 | 0.15617 | 332.6189 | 0.078472 | 0 | 0 | 0.15694 | 332.8857 | 0.079051 | 0 | 0 | 0.1581 | 333.1526 | 0.07963 | 0 | 0 | 0.15926 | 333.2416 | 0.079823 | 0 | 0 | 0.15965 | 333.5085 | 0.080401 | 0 | 0 | 0.1608 | 333.7753 | 0.08098 | 0 | 0 | 0.16196 | 333.9533 | 0.081366 | 0 | 0 | 0.16273 | 334.2201 | 0.081945 | 0 | 0 | 0.16389 | 334.398 | 0.082331 | 0 | 0 | 0.16466 | 334.576 | 0.082717 | 0 | 0 | 0.16543
2017-12-26 07:00 | 295.687 | 0.88132 |  | 310.4905 | 0.030476 | 0 | 0 | 0.060951 | 319.2156 | 0.0494 | 0 | 0 | 0.098801 | 326.3543 | 0.064884 | 0 | 0 | 0.12977 | 326.6187 | 0.065458 | 0 | 0 | 0.13092 | 326.795 | 0.06584 | 0 | 0 | 0.13168 | 327.0594 | 0.066413 | 0 | 0 | 0.13283 | 327.3238 | 0.066987 | 0 | 0 | 0.13397 | 327.5882 | 0.06756 | 0 | 0 | 0.13512 | 327.9407 | 0.068325 | 0 | 0 | 0.13665 | 328.2051 | 0.068899 | 0 | 0 | 0.1378 | 328.3814 | 0.069281 | 0 | 0 | 0.13856 | 328.6458 | 0.069854 | 0 | 0 | 0.13971 | 328.8221 | 0.070237 | 0 | 0 | 0.14047 | 329.0865 | 0.07081 | 0 | 0 | 0.14162 | 329.3509 | 0.071384 | 0 | 0 | 0.14277 | 329.5271 | 0.071766 | 0 | 0 | 0.14353 | 329.7915 | 0.072339 | 0 | 0 | 0.14468 | 330.0559 | 0.072913 | 0 | 0 | 0.14583 | 330.144 | 0.073104 | 0 | 0 | 0.14621 | 330.4084 | 0.073678 | 0 | 0 | 0.14736 | 330.6728 | 0.074251 | 0 | 0 | 0.1485 | 330.8491 | 0.074633 | 0 | 0 | 0.14927 | 331.1135 | 0.075207 | 0 | 0 | 0.15041 | 331.2898 | 0.075589 | 0 | 0 | 0.15118 | 331.466 | 0.075971 | 0 | 0 | 0.15194
2017-12-26 08:00 | 299.4728 | 0.89261 |  | 314.4658 | 0.039098 | 0 | 0 | 0.078196 | 323.3027 | 0.058265 | 0 | 0 | 0.11653 | 330.5328 | 0.073947 | 0 | 0 | 0.14789 | 330.8006 | 0.074528 | 0 | 0 | 0.14906 | 330.9791 | 0.074915 | 0 | 0 | 0.14983 | 331.2469 | 0.075496 | 0 | 0 | 0.15099 | 331.5147 | 0.076077 | 0 | 0 | 0.15215 | 331.7824 | 0.076658 | 0 | 0 | 0.15332 | 332.1395 | 0.077432 | 0 | 0 | 0.15486 | 332.4073 | 0.078013 | 0 | 0 | 0.15603 | 332.5858 | 0.0784 | 0 | 0 | 0.1568 | 332.8536 | 0.078981 | 0 | 0 | 0.15796 | 333.0321 | 0.079368 | 0 | 0 | 0.15874 | 333.2999 | 0.079949 | 0 | 0 | 0.1599 | 333.5677 | 0.08053 | 0 | 0 | 0.16106 | 333.7462 | 0.080917 | 0 | 0 | 0.16183 | 334.014 | 0.081498 | 0 | 0 | 0.163 | 334.2817 | 0.082079 | 0 | 0 | 0.16416 | 334.371 | 0.082272 | 0 | 0 | 0.16454 | 334.6388 | 0.082853 | 0 | 0 | 0.16571 | 334.9066 | 0.083434 | 0 | 0 | 0.16687 | 335.0851 | 0.083821 | 0 | 0 | 0.16764 | 335.3529 | 0.084402 | 0 | 0 | 0.1688 | 335.5314 | 0.084789 | 0 | 0 | 0.16958 | 335.7099 | 0.085176 | 0 | 0 | 0.17035
2017-12-26 09:00 | 307.3297 | 0.91603 |  | 322.7161 | 0.056993 | 0 | 0 | 0.11399 | 331.7848 | 0.076663 | 0 | 0 | 0.15333 | 339.2046 | 0.092756 | 0 | 0 | 0.18551 | 339.4794 | 0.093352 | 0 | 0 | 0.1867 | 339.6626 | 0.09375 | 0 | 0 | 0.1875 | 339.9374 | 0.094346 | 0 | 0 | 0.18869 | 340.2122 | 0.094942 | 0 | 0 | 0.18988 | 340.487 | 0.095538 | 0 | 0 | 0.19108 | 340.8534 | 0.096333 | 0 | 0 | 0.19267 | 341.1282 | 0.096929 | 0 | 0 | 0.19386 | 341.3114 | 0.097326 | 0 | 0 | 0.19465 | 341.5862 | 0.097922 | 0 | 0 | 0.19584 | 341.7695 | 0.09832 | 0 | 0 | 0.19664 | 342.0443 | 0.098916 | 0 | 0 | 0.19783 | 342.3191 | 0.099512 | 0 | 0 | 0.19902 | 342.5023 | 0.099909 | 0 | 0 | 0.19982 | 342.7771 | 0.10051 | 0 | 0 | 0.20101 | 343.0519 | 0.1011 | 0 | 0 | 0.2022 | 343.1435 | 0.1013 | 0 | 0 | 0.2026 | 343.4183 | 0.1019 | 0 | 0 | 0.20379 | 343.6931 | 0.10249 | 0 | 0 | 0.20498 | 343.8763 | 0.10289 | 0 | 0 | 0.20578 | 344.1511 | 0.10349 | 0 | 0 | 0.20697 | 344.3343 | 0.10388 | 0 | 0 | 0.20777 | 344.5175 | 0.10428 | 0 | 0 | 0.20856
2017-12-26 10:00 | 302.7386 | 0.90234 |  | 317.8951 | 0.046536 | 0 | 0 | 0.093072 | 326.8283 | 0.065912 | 0 | 0 | 0.13182 | 334.1373 | 0.081765 | 0 | 0 | 0.16353 | 334.408 | 0.082353 | 0 | 0 | 0.16471 | 334.5884 | 0.082744 | 0 | 0 | 0.16549 | 334.8591 | 0.083331 | 0 | 0 | 0.16666 | 335.1299 | 0.083918 | 0 | 0 | 0.16784 | 335.4006 | 0.084505 | 0 | 0 | 0.16901 | 335.7615 | 0.085288 | 0 | 0 | 0.17058 | 336.0322 | 0.085875 | 0 | 0 | 0.17175 | 336.2127 | 0.086267 | 0 | 0 | 0.17253 | 336.4834 | 0.086854 | 0 | 0 | 0.17371 | 336.6638 | 0.087245 | 0 | 0 | 0.17449 | 336.9345 | 0.087833 | 0 | 0 | 0.17567 | 337.2052 | 0.08842 | 0 | 0 | 0.17684 | 337.3857 | 0.088811 | 0 | 0 | 0.17762 | 337.6564 | 0.089398 | 0 | 0 | 0.1788 | 337.9271 | 0.089986 | 0 | 0 | 0.17997 | 338.0173 | 0.090181 | 0 | 0 | 0.18036 | 338.288 | 0.090768 | 0 | 0 | 0.18154 | 338.5588 | 0.091356 | 0 | 0 | 0.18271 | 338.7392 | 0.091747 | 0 | 0 | 0.18349 | 339.0099 | 0.092334 | 0 | 0 | 0.18467 | 339.1904 | 0.092726 | 0 | 0 | 0.18545 | 339.3709 | 0.093117 | 0 | 0 | 0.18623
2017-12-26 11:00 | 298.756 | 0.89047 |  | 313.7132 | 0.037466 | 0 | 0 | 0.074931 | 322.5288 | 0.056587 | 0 | 0 | 0.11317 | 329.7417 | 0.072231 | 0 | 0 | 0.14446 | 330.0088 | 0.072811 | 0 | 0 | 0.14562 | 330.1869 | 0.073197 | 0 | 0 | 0.14639 | 330.454 | 0.073776 | 0 | 0 | 0.14755 | 330.7212 | 0.074356 | 0 | 0 | 0.14871 | 330.9883 | 0.074935 | 0 | 0 | 0.14987 | 331.3445 | 0.075708 | 0 | 0 | 0.15142 | 331.6117 | 0.076287 | 0 | 0 | 0.15257 | 331.7898 | 0.076674 | 0 | 0 | 0.15335 | 332.0569 | 0.077253 | 0 | 0 | 0.15451 | 332.235 | 0.077639 | 0 | 0 | 0.15528 | 332.5021 | 0.078219 | 0 | 0 | 0.15644 | 332.7693 | 0.078798 | 0 | 0 | 0.1576 | 332.9474 | 0.079184 | 0 | 0 | 0.15837 | 333.2145 | 0.079764 | 0 | 0 | 0.15953 | 333.4816 | 0.080343 | 0 | 0 | 0.16069 | 333.5707 | 0.080536 | 0 | 0 | 0.16107 | 333.8378 | 0.081116 | 0 | 0 | 0.16223 | 334.105 | 0.081695 | 0 | 0 | 0.16339 | 334.2831 | 0.082082 | 0 | 0 | 0.16416 | 334.5502 | 0.082661 | 0 | 0 | 0.16532 | 334.7283 | 0.083047 | 0 | 0 | 0.16609 | 334.9064 | 0.083434 | 0 | 0 | 0.16687
2017-12-26 12:00 | 301.0257 | 0.89724 |  | 316.0964 | 0.042635 | 0 | 0 | 0.08527 | 324.9791 | 0.061901 | 0 | 0 | 0.1238 | 332.2467 | 0.077665 | 0 | 0 | 0.15533 | 332.5159 | 0.078249 | 0 | 0 | 0.1565 | 332.6953 | 0.078638 | 0 | 0 | 0.15728 | 332.9645 | 0.079222 | 0 | 0 | 0.15844 | 333.2337 | 0.079805 | 0 | 0 | 0.15961 | 333.5028 | 0.080389 | 0 | 0 | 0.16078 | 333.8617 | 0.081168 | 0 | 0 | 0.16234 | 334.1309 | 0.081752 | 0 | 0 | 0.1635 | 334.3103 | 0.082141 | 0 | 0 | 0.16428 | 334.5795 | 0.082725 | 0 | 0 | 0.16545 | 334.759 | 0.083114 | 0 | 0 | 0.16623 | 335.0281 | 0.083698 | 0 | 0 | 0.1674 | 335.2973 | 0.084281 | 0 | 0 | 0.16856 | 335.4768 | 0.084671 | 0 | 0 | 0.16934 | 335.7459 | 0.085255 | 0 | 0 | 0.17051 | 336.0151 | 0.085838 | 0 | 0 | 0.17168 | 336.1048 | 0.086033 | 0 | 0 | 0.17207 | 336.374 | 0.086617 | 0 | 0 | 0.17323 | 336.6432 | 0.087201 | 0 | 0 | 0.1744 | 336.8226 | 0.08759 | 0 | 0 | 0.17518 | 337.0918 | 0.088174 | 0 | 0 | 0.17635 | 337.2712 | 0.088563 | 0 | 0 | 0.17713 | 337.4507 | 0.088952 | 0 | 0 | 0.1779
2017-12-26 13:00 | 294.4676 | 0.87769 |  | 309.2101 | 0.027698 | 0 | 0 | 0.055396 | 317.8992 | 0.046545 | 0 | 0 | 0.09309 | 325.0085 | 0.061965 | 0 | 0 | 0.12393 | 325.2718 | 0.062536 | 0 | 0 | 0.12507 | 325.4473 | 0.062917 | 0 | 0 | 0.12583 | 325.7106 | 0.063488 | 0 | 0 | 0.12698 | 325.9739 | 0.064059 | 0 | 0 | 0.12812 | 326.2372 | 0.06463 | 0 | 0 | 0.12926 | 326.5883 | 0.065392 | 0 | 0 | 0.13078 | 326.8516 | 0.065963 | 0 | 0 | 0.13193 | 327.0272 | 0.066344 | 0 | 0 | 0.13269 | 327.2905 | 0.066915 | 0 | 0 | 0.13383 | 327.466 | 0.067295 | 0 | 0 | 0.13459 | 327.7293 | 0.067867 | 0 | 0 | 0.13573 | 327.9926 | 0.068438 | 0 | 0 | 0.13688 | 328.1681 | 0.068818 | 0 | 0 | 0.13764 | 328.4315 | 0.069389 | 0 | 0 | 0.13878 | 328.6948 | 0.069961 | 0 | 0 | 0.13992 | 328.7825 | 0.070151 | 0 | 0 | 0.1403 | 329.0458 | 0.070722 | 0 | 0 | 0.14144 | 329.3091 | 0.071293 | 0 | 0 | 0.14259 | 329.4847 | 0.071674 | 0 | 0 | 0.14335 | 329.748 | 0.072245 | 0 | 0 | 0.14449 | 329.9235 | 0.072626 | 0 | 0 | 0.14525 | 330.0991 | 0.073007 | 0 | 0 | 0.14601
2017-12-26 14:00 | 298.8277 | 0.89069 |  | 313.7884 | 0.037629 | 0 | 0 | 0.075257 | 322.6062 | 0.056755 | 0 | 0 | 0.11351 | 329.8208 | 0.072403 | 0 | 0 | 0.14481 | 330.088 | 0.072982 | 0 | 0 | 0.14596 | 330.2661 | 0.073369 | 0 | 0 | 0.14674 | 330.5333 | 0.073948 | 0 | 0 | 0.1479 | 330.8005 | 0.074528 | 0 | 0 | 0.14906 | 331.0677 | 0.075108 | 0 | 0 | 0.15022 | 331.424 | 0.07588 | 0 | 0 | 0.15176 | 331.6912 | 0.07646 | 0 | 0 | 0.15292 | 331.8693 | 0.076846 | 0 | 0 | 0.15369 | 332.1365 | 0.077426 | 0 | 0 | 0.15485 | 332.3147 | 0.077812 | 0 | 0 | 0.15562 | 332.5819 | 0.078392 | 0 | 0 | 0.15678 | 332.8491 | 0.078971 | 0 | 0 | 0.15794 | 333.0272 | 0.079358 | 0 | 0 | 0.15872 | 333.2944 | 0.079937 | 0 | 0 | 0.15987 | 333.5616 | 0.080517 | 0 | 0 | 0.16103 | 333.6507 | 0.08071 | 0 | 0 | 0.16142 | 333.9179 | 0.08129 | 0 | 0 | 0.16258 | 334.1851 | 0.081869 | 0 | 0 | 0.16374 | 334.3633 | 0.082256 | 0 | 0 | 0.16451 | 334.6305 | 0.082835 | 0 | 0 | 0.16567 | 334.8086 | 0.083221 | 0 | 0 | 0.16644 | 334.9867 | 0.083608 | 0 | 0 | 0.16722
2017-12-26 15:00 | 302.7426 | 0.90235 |  | 317.8993 | 0.046545 | 0 | 0 | 0.093091 | 326.8326 | 0.065922 | 0 | 0 | 0.13184 | 334.1417 | 0.081775 | 0 | 0 | 0.16355 | 334.4124 | 0.082362 | 0 | 0 | 0.16472 | 334.5929 | 0.082754 | 0 | 0 | 0.16551 | 334.8636 | 0.083341 | 0 | 0 | 0.16668 | 335.1343 | 0.083928 | 0 | 0 | 0.16786 | 335.405 | 0.084515 | 0 | 0 | 0.16903 | 335.7659 | 0.085298 | 0 | 0 | 0.1706 | 336.0366 | 0.085885 | 0 | 0 | 0.17177 | 336.2171 | 0.086277 | 0 | 0 | 0.17255 | 336.4878 | 0.086864 | 0 | 0 | 0.17373 | 336.6683 | 0.087255 | 0 | 0 | 0.17451 | 336.939 | 0.087842 | 0 | 0 | 0.17568 | 337.2097 | 0.088429 | 0 | 0 | 0.17686 | 337.3902 | 0.088821 | 0 | 0 | 0.17764 | 337.6609 | 0.089408 | 0 | 0 | 0.17882 | 337.9316 | 0.089995 | 0 | 0 | 0.17999 | 338.0218 | 0.090191 | 0 | 0 | 0.18038 | 338.2925 | 0.090778 | 0 | 0 | 0.18156 | 338.5632 | 0.091365 | 0 | 0 | 0.18273 | 338.7437 | 0.091757 | 0 | 0 | 0.18351 | 339.0144 | 0.092344 | 0 | 0 | 0.18469 | 339.1949 | 0.092735 | 0 | 0 | 0.18547 | 339.3754 | 0.093127 | 0 | 0 | 0.18625
2017-12-26 16:00 | 302.8579 | 0.9027 |  | 318.0204 | 0.046808 | 0 | 0 | 0.093616 | 326.9571 | 0.066192 | 0 | 0 | 0.13238 | 334.269 | 0.082051 | 0 | 0 | 0.1641 | 334.5398 | 0.082638 | 0 | 0 | 0.16528 | 334.7203 | 0.08303 | 0 | 0 | 0.16606 | 334.9911 | 0.083617 | 0 | 0 | 0.16723 | 335.262 | 0.084205 | 0 | 0 | 0.16841 | 335.5328 | 0.084792 | 0 | 0 | 0.16958 | 335.8938 | 0.085575 | 0 | 0 | 0.17115 | 336.1646 | 0.086163 | 0 | 0 | 0.17233 | 336.3452 | 0.086554 | 0 | 0 | 0.17311 | 336.616 | 0.087142 | 0 | 0 | 0.17428 | 336.7965 | 0.087533 | 0 | 0 | 0.17507 | 337.0673 | 0.088121 | 0 | 0 | 0.17624 | 337.3382 | 0.088708 | 0 | 0 | 0.17742 | 337.5187 | 0.0891 | 0 | 0 | 0.1782 | 337.7895 | 0.089687 | 0 | 0 | 0.17937 | 338.0603 | 0.090274 | 0 | 0 | 0.18055 | 338.1506 | 0.09047 | 0 | 0 | 0.18094 | 338.4214 | 0.091058 | 0 | 0 | 0.18212 | 338.6922 | 0.091645 | 0 | 0 | 0.18329 | 338.8727 | 0.092037 | 0 | 0 | 0.18407 | 339.1436 | 0.092624 | 0 | 0 | 0.18525 | 339.3241 | 0.093016 | 0 | 0 | 0.18603 | 339.5046 | 0.093407 | 0 | 0 | 0.18681
2017-12-26 17:00 | 310.4473 | 0.92532 |  | 325.9898 | 0.064093 | 0 | 0 | 0.12819 | 335.1504 | 0.083963 | 0 | 0 | 0.16793 | 342.6455 | 0.10022 | 0 | 0 | 0.20044 | 342.9231 | 0.10082 | 0 | 0 | 0.20164 | 343.1081 | 0.10122 | 0 | 0 | 0.20245 | 343.3857 | 0.10183 | 0 | 0 | 0.20365 | 343.6633 | 0.10243 | 0 | 0 | 0.20485 | 343.9409 | 0.10303 | 0 | 0 | 0.20606 | 344.3111 | 0.10383 | 0 | 0 | 0.20766 | 344.5887 | 0.10443 | 0 | 0 | 0.20887 | 344.7737 | 0.10484 | 0 | 0 | 0.20967 | 345.0513 | 0.10544 | 0 | 0 | 0.21088 | 345.2364 | 0.10584 | 0 | 0 | 0.21168 | 345.514 | 0.10644 | 0 | 0 | 0.21288 | 345.7916 | 0.10704 | 0 | 0 | 0.21409 | 345.9766 | 0.10744 | 0 | 0 | 0.21489 | 346.2542 | 0.10805 | 0 | 0 | 0.21609 | 346.5318 | 0.10865 | 0 | 0 | 0.2173 | 346.6244 | 0.10885 | 0 | 0 | 0.2177 | 346.902 | 0.10945 | 0 | 0 | 0.2189 | 347.1796 | 0.11005 | 0 | 0 | 0.22011 | 347.3646 | 0.11046 | 0 | 0 | 0.22091 | 347.6422 | 0.11106 | 0 | 0 | 0.22212 | 347.8273 | 0.11146 | 0 | 0 | 0.22292 | 348.0123 | 0.11186 | 0 | 0 | 0.22372
2017-12-26 18:00 | 310.6252 | 0.92585 |  | 326.1766 | 0.064499 | 0 | 0 | 0.129 | 335.3425 | 0.08438 | 0 | 0 | 0.16876 | 342.8419 | 0.10065 | 0 | 0 | 0.20129 | 343.1196 | 0.10125 | 0 | 0 | 0.2025 | 343.3048 | 0.10165 | 0 | 0 | 0.2033 | 343.5826 | 0.10225 | 0 | 0 | 0.2045 | 343.8603 | 0.10285 | 0 | 0 | 0.20571 | 344.1381 | 0.10346 | 0 | 0 | 0.20691 | 344.5084 | 0.10426 | 0 | 0 | 0.20852 | 344.7862 | 0.10486 | 0 | 0 | 0.20973 | 344.9713 | 0.10526 | 0 | 0 | 0.21053 | 345.2491 | 0.10587 | 0 | 0 | 0.21173 | 345.4343 | 0.10627 | 0 | 0 | 0.21254 | 345.712 | 0.10687 | 0 | 0 | 0.21374 | 345.9898 | 0.10747 | 0 | 0 | 0.21495 | 346.1749 | 0.10788 | 0 | 0 | 0.21575 | 346.4527 | 0.10848 | 0 | 0 | 0.21696 | 346.7305 | 0.10908 | 0 | 0 | 0.21816 | 346.823 | 0.10928 | 0 | 0 | 0.21856 | 347.1008 | 0.10988 | 0 | 0 | 0.21977 | 347.3785 | 0.11049 | 0 | 0 | 0.22097 | 347.5637 | 0.11089 | 0 | 0 | 0.22177 | 347.8415 | 0.11149 | 0 | 0 | 0.22298 | 348.0266 | 0.11189 | 0 | 0 | 0.22378 | 348.2118 | 0.11229 | 0 | 0 | 0.22459
2017-12-26 19:00 | 312.8553 | 0.9325 |  | 328.5183 | 0.069578 | 0 | 0 | 0.13916 | 337.75 | 0.089601 | 0 | 0 | 0.1792 | 345.3033 | 0.10598 | 0 | 0 | 0.21197 | 345.583 | 0.10659 | 0 | 0 | 0.21318 | 345.7695 | 0.107 | 0 | 0 | 0.21399 | 346.0492 | 0.1076 | 0 | 0 | 0.2152 | 346.329 | 0.10821 | 0 | 0 | 0.21642 | 346.6087 | 0.10882 | 0 | 0 | 0.21763 | 346.9817 | 0.10963 | 0 | 0 | 0.21925 | 347.2615 | 0.11023 | 0 | 0 | 0.22046 | 347.448 | 0.11064 | 0 | 0 | 0.22127 | 347.7277 | 0.11124 | 0 | 0 | 0.22249 | 347.9142 | 0.11165 | 0 | 0 | 0.2233 | 348.194 | 0.11225 | 0 | 0 | 0.22451 | 348.4737 | 0.11286 | 0 | 0 | 0.22572 | 348.6602 | 0.11327 | 0 | 0 | 0.22653 | 348.94 | 0.11387 | 0 | 0 | 0.22774 | 349.2197 | 0.11448 | 0 | 0 | 0.22896 | 349.313 | 0.11468 | 0 | 0 | 0.22936 | 349.5927 | 0.11529 | 0 | 0 | 0.23058 | 349.8725 | 0.1159 | 0 | 0 | 0.23179 | 350.059 | 0.1163 | 0 | 0 | 0.2326 | 350.3387 | 0.11691 | 0 | 0 | 0.23381 | 350.5252 | 0.11731 | 0 | 0 | 0.23462 | 350.7117 | 0.11772 | 0 | 0 | 0.23543
2017-12-26 20:00 | 303.1019 | 0.90343 |  | 318.2767 | 0.047364 | 0 | 0 | 0.094727 | 327.2206 | 0.066763 | 0 | 0 | 0.13353 | 334.5383 | 0.082635 | 0 | 0 | 0.16527 | 334.8093 | 0.083223 | 0 | 0 | 0.16645 | 334.99 | 0.083615 | 0 | 0 | 0.16723 | 335.2611 | 0.084203 | 0 | 0 | 0.16841 | 335.5321 | 0.084791 | 0 | 0 | 0.16958 | 335.8031 | 0.085379 | 0 | 0 | 0.17076 | 336.1645 | 0.086162 | 0 | 0 | 0.17232 | 336.4355 | 0.08675 | 0 | 0 | 0.1735 | 336.6162 | 0.087142 | 0 | 0 | 0.17428 | 336.8872 | 0.08773 | 0 | 0 | 0.17546 | 337.0679 | 0.088122 | 0 | 0 | 0.17624 | 337.3389 | 0.08871 | 0 | 0 | 0.17742 | 337.61 | 0.089298 | 0 | 0 | 0.1786 | 337.7906 | 0.08969 | 0 | 0 | 0.17938 | 338.0617 | 0.090277 | 0 | 0 | 0.18055 | 338.3327 | 0.090865 | 0 | 0 | 0.18173 | 338.423 | 0.091061 | 0 | 0 | 0.18212 | 338.6941 | 0.091649 | 0 | 0 | 0.1833 | 338.9651 | 0.092237 | 0 | 0 | 0.18447 | 339.1458 | 0.092629 | 0 | 0 | 0.18526 | 339.4168 | 0.093217 | 0 | 0 | 0.18643 | 339.5975 | 0.093609 | 0 | 0 | 0.18722 | 339.7782 | 0.094001 | 0 | 0 | 0.188
2017-12-26 21:00 | 301.9801 | 0.90008 |  | 317.0987 | 0.044809 | 0 | 0 | 0.089617 | 326.0095 | 0.064136 | 0 | 0 | 0.12827 | 333.3001 | 0.07995 | 0 | 0 | 0.1599 | 333.5702 | 0.080535 | 0 | 0 | 0.16107 | 333.7502 | 0.080926 | 0 | 0 | 0.16185 | 334.0202 | 0.081511 | 0 | 0 | 0.16302 | 334.2902 | 0.082097 | 0 | 0 | 0.16419 | 334.5602 | 0.082683 | 0 | 0 | 0.16537 | 334.9203 | 0.083464 | 0 | 0 | 0.16693 | 335.1903 | 0.084049 | 0 | 0 | 0.1681 | 335.3703 | 0.08444 | 0 | 0 | 0.16888 | 335.6403 | 0.085026 | 0 | 0 | 0.17005 | 335.8204 | 0.085416 | 0 | 0 | 0.17083 | 336.0904 | 0.086002 | 0 | 0 | 0.172 | 336.3604 | 0.086587 | 0 | 0 | 0.17317 | 336.5404 | 0.086978 | 0 | 0 | 0.17396 | 336.8104 | 0.087564 | 0 | 0 | 0.17513 | 337.0805 | 0.088149 | 0 | 0 | 0.1763 | 337.1705 | 0.088344 | 0 | 0 | 0.17669 | 337.4405 | 0.08893 | 0 | 0 | 0.17786 | 337.7105 | 0.089516 | 0 | 0 | 0.17903 | 337.8905 | 0.089906 | 0 | 0 | 0.17981 | 338.1606 | 0.090492 | 0 | 0 | 0.18098 | 338.3406 | 0.090882 | 0 | 0 | 0.18176 | 338.5206 | 0.091273 | 0 | 0 | 0.18255
2017-12-26 22:00 | 305.307 | 0.91 |  | 320.5921 | 0.052386 | 0 | 0 | 0.10477 | 329.6011 | 0.071926 | 0 | 0 | 0.14385 | 336.9721 | 0.087914 | 0 | 0 | 0.17583 | 337.2451 | 0.088506 | 0 | 0 | 0.17701 | 337.4271 | 0.088901 | 0 | 0 | 0.1778 | 337.7001 | 0.089493 | 0 | 0 | 0.17899 | 337.9731 | 0.090085 | 0 | 0 | 0.18017 | 338.2461 | 0.090677 | 0 | 0 | 0.18135 | 338.6101 | 0.091467 | 0 | 0 | 0.18293 | 338.8831 | 0.092059 | 0 | 0 | 0.18412 | 339.0651 | 0.092454 | 0 | 0 | 0.18491 | 339.3381 | 0.093046 | 0 | 0 | 0.18609 | 339.5201 | 0.093441 | 0 | 0 | 0.18688 | 339.7931 | 0.094033 | 0 | 0 | 0.18807 | 340.0661 | 0.094625 | 0 | 0 | 0.18925 | 340.2481 | 0.09502 | 0 | 0 | 0.19004 | 340.5211 | 0.095612 | 0 | 0 | 0.19122 | 340.7941 | 0.096204 | 0 | 0 | 0.19241 | 340.8851 | 0.096401 | 0 | 0 | 0.1928 | 341.1581 | 0.096994 | 0 | 0 | 0.19399 | 341.4311 | 0.097586 | 0 | 0 | 0.19517 | 341.6131 | 0.09798 | 0 | 0 | 0.19596 | 341.8861 | 0.098573 | 0 | 0 | 0.19715 | 342.0681 | 0.098967 | 0 | 0 | 0.19793 | 342.2501 | 0.099362 | 0 | 0 | 0.19872
2017-12-26 23:00 | 308.9608 | 0.92089 |  | 324.4289 | 0.060708 | 0 | 0 | 0.12142 | 333.5457 | 0.080482 | 0 | 0 | 0.16096 | 341.0049 | 0.096661 | 0 | 0 | 0.19332 | 341.2811 | 0.09726 | 0 | 0 | 0.19452 | 341.4653 | 0.09766 | 0 | 0 | 0.19532 | 341.7416 | 0.098259 | 0 | 0 | 0.19652 | 342.0178 | 0.098858 | 0 | 0 | 0.19772 | 342.2941 | 0.099458 | 0 | 0 | 0.19892 | 342.6624 | 0.10026 | 0 | 0 | 0.20051 | 342.9387 | 0.10086 | 0 | 0 | 0.20171 | 343.1229 | 0.10126 | 0 | 0 | 0.20251 | 343.3992 | 0.10185 | 0 | 0 | 0.20371 | 343.5833 | 0.10225 | 0 | 0 | 0.20451 | 343.8596 | 0.10285 | 0 | 0 | 0.20571 | 344.1359 | 0.10345 | 0 | 0 | 0.2069 | 344.32 | 0.10385 | 0 | 0 | 0.2077 | 344.5963 | 0.10445 | 0 | 0 | 0.2089 | 344.8726 | 0.10505 | 0 | 0 | 0.2101 | 344.9647 | 0.10525 | 0 | 0 | 0.2105 | 345.2409 | 0.10585 | 0 | 0 | 0.2117 | 345.5172 | 0.10645 | 0 | 0 | 0.2129 | 345.7014 | 0.10685 | 0 | 0 | 0.2137 | 345.9776 | 0.10745 | 0 | 0 | 0.21489 | 346.1618 | 0.10785 | 0 | 0 | 0.21569 | 346.346 | 0.10825 | 0 | 0 | 0.21649
2017-12-27 | 304.1297 | 0.90649 |  | 319.3559 | 0.049705 | 0 | 0 | 0.099409 | 328.3301 | 0.06917 | 0 | 0 | 0.13834 | 335.6727 | 0.085096 | 0 | 0 | 0.17019 | 335.9446 | 0.085686 | 0 | 0 | 0.17137 | 336.1259 | 0.086079 | 0 | 0 | 0.17216 | 336.3979 | 0.086669 | 0 | 0 | 0.17334 | 336.6698 | 0.087258 | 0 | 0 | 0.17452 | 336.9418 | 0.087848 | 0 | 0 | 0.1757 | 337.3044 | 0.088635 | 0 | 0 | 0.17727 | 337.5763 | 0.089225 | 0 | 0 | 0.17845 | 337.7576 | 0.089618 | 0 | 0 | 0.17924 | 338.0296 | 0.090208 | 0 | 0 | 0.18042 | 338.2109 | 0.090601 | 0 | 0 | 0.1812 | 338.4828 | 0.091191 | 0 | 0 | 0.18238 | 338.7548 | 0.091781 | 0 | 0 | 0.18356 | 338.936 | 0.092174 | 0 | 0 | 0.18435 | 339.208 | 0.092764 | 0 | 0 | 0.18553 | 339.4799 | 0.093354 | 0 | 0 | 0.18671 | 339.5706 | 0.09355 | 0 | 0 | 0.1871 | 339.8425 | 0.09414 | 0 | 0 | 0.18828 | 340.1145 | 0.09473 | 0 | 0 | 0.18946 | 340.2958 | 0.095123 | 0 | 0 | 0.19025 | 340.5677 | 0.095713 | 0 | 0 | 0.19143 | 340.749 | 0.096106 | 0 | 0 | 0.19221 | 340.9303 | 0.0965 | 0 | 0 | 0.193
2017-12-27 01:00 | 301.3506 | 0.89821 |  | 316.4377 | 0.043375 | 0 | 0 | 0.08675 | 325.3299 | 0.062662 | 0 | 0 | 0.12532 | 332.6054 | 0.078443 | 0 | 0 | 0.15689 | 332.8748 | 0.079027 | 0 | 0 | 0.15805 | 333.0545 | 0.079417 | 0 | 0 | 0.15883 | 333.3239 | 0.080001 | 0 | 0 | 0.16 | 333.5934 | 0.080586 | 0 | 0 | 0.16117 | 333.8628 | 0.08117 | 0 | 0 | 0.16234 | 334.2221 | 0.081949 | 0 | 0 | 0.1639 | 334.4916 | 0.082534 | 0 | 0 | 0.16507 | 334.6712 | 0.082924 | 0 | 0 | 0.16585 | 334.9407 | 0.083508 | 0 | 0 | 0.16702 | 335.1203 | 0.083898 | 0 | 0 | 0.1678 | 335.3898 | 0.084482 | 0 | 0 | 0.16896 | 335.6593 | 0.085067 | 0 | 0 | 0.17013 | 335.8389 | 0.085456 | 0 | 0 | 0.17091 | 336.1084 | 0.086041 | 0 | 0 | 0.17208 | 336.3778 | 0.086625 | 0 | 0 | 0.17325 | 336.4676 | 0.08682 | 0 | 0 | 0.17364 | 336.7371 | 0.087404 | 0 | 0 | 0.17481 | 337.0066 | 0.087989 | 0 | 0 | 0.17598 | 337.1862 | 0.088379 | 0 | 0 | 0.17676 | 337.4557 | 0.088963 | 0 | 0 | 0.17793 | 337.6353 | 0.089353 | 0 | 0 | 0.17871 | 337.8149 | 0.089742 | 0 | 0 | 0.17948
2017-12-27 02:00 | 302.2002 | 0.90074 |  | 317.3297 | 0.04531 | 0 | 0 | 0.09062 | 326.247 | 0.064651 | 0 | 0 | 0.1293 | 333.543 | 0.080476 | 0 | 0 | 0.16095 | 333.8132 | 0.081063 | 0 | 0 | 0.16213 | 333.9934 | 0.081453 | 0 | 0 | 0.16291 | 334.2636 | 0.082039 | 0 | 0 | 0.16408 | 334.5338 | 0.082626 | 0 | 0 | 0.16525 | 334.804 | 0.083212 | 0 | 0 | 0.16642 | 335.1643 | 0.083993 | 0 | 0 | 0.16799 | 335.4346 | 0.084579 | 0 | 0 | 0.16916 | 335.6147 | 0.08497 | 0 | 0 | 0.16994 | 335.8849 | 0.085556 | 0 | 0 | 0.17111 | 336.0651 | 0.085947 | 0 | 0 | 0.17189 | 336.3353 | 0.086533 | 0 | 0 | 0.17307 | 336.6055 | 0.087119 | 0 | 0 | 0.17424 | 336.7857 | 0.08751 | 0 | 0 | 0.17502 | 337.0559 | 0.088096 | 0 | 0 | 0.17619 | 337.3261 | 0.088682 | 0 | 0 | 0.17736 | 337.4162 | 0.088877 | 0 | 0 | 0.17775 | 337.6864 | 0.089463 | 0 | 0 | 0.17893 | 337.9566 | 0.09005 | 0 | 0 | 0.1801 | 338.1368 | 0.09044 | 0 | 0 | 0.18088 | 338.407 | 0.091026 | 0 | 0 | 0.18205 | 338.5871 | 0.091417 | 0 | 0 | 0.18283 | 338.7673 | 0.091808 | 0 | 0 | 0.18362
2017-12-27 03:00 | 299.1637 | 0.89169 |  | 314.1413 | 0.038394 | 0 | 0 | 0.076788 | 322.969 | 0.057541 | 0 | 0 | 0.11508 | 330.1917 | 0.073207 | 0 | 0 | 0.14641 | 330.4592 | 0.073788 | 0 | 0 | 0.14758 | 330.6375 | 0.074174 | 0 | 0 | 0.14835 | 330.905 | 0.074755 | 0 | 0 | 0.14951 | 331.1725 | 0.075335 | 0 | 0 | 0.15067 | 331.44 | 0.075915 | 0 | 0 | 0.15183 | 331.7967 | 0.076689 | 0 | 0 | 0.15338 | 332.0642 | 0.077269 | 0 | 0 | 0.15454 | 332.2425 | 0.077656 | 0 | 0 | 0.15531 | 332.51 | 0.078236 | 0 | 0 | 0.15647 | 332.6884 | 0.078623 | 0 | 0 | 0.15725 | 332.9559 | 0.079203 | 0 | 0 | 0.15841 | 333.2234 | 0.079783 | 0 | 0 | 0.15957 | 333.4017 | 0.08017 | 0 | 0 | 0.16034 | 333.6692 | 0.08075 | 0 | 0 | 0.1615 | 333.9367 | 0.08133 | 0 | 0 | 0.16266 | 334.0259 | 0.081524 | 0 | 0 | 0.16305 | 334.2934 | 0.082104 | 0 | 0 | 0.16421 | 334.5609 | 0.082684 | 0 | 0 | 0.16537 | 334.7393 | 0.083071 | 0 | 0 | 0.16614 | 335.0068 | 0.083651 | 0 | 0 | 0.1673 | 335.1851 | 0.084038 | 0 | 0 | 0.16808 | 335.3634 | 0.084425 | 0 | 0 | 0.16885
2017-12-27 04:00 | 288.389 | 0.85957 |  | 302.8271 | 0.013854 | 0 | 0 | 0.027707 | 311.3369 | 0.032311 | 0 | 0 | 0.064623 | 318.2994 | 0.047413 | 0 | 0 | 0.094826 | 318.5573 | 0.047972 | 0 | 0 | 0.095945 | 318.7292 | 0.048345 | 0 | 0 | 0.096691 | 318.9871 | 0.048905 | 0 | 0 | 0.097809 | 319.245 | 0.049464 | 0 | 0 | 0.098928 | 319.5028 | 0.050023 | 0 | 0 | 0.10005 | 319.8467 | 0.050769 | 0 | 0 | 0.10154 | 320.1045 | 0.051328 | 0 | 0 | 0.10266 | 320.2764 | 0.051701 | 0 | 0 | 0.1034 | 320.5343 | 0.052261 | 0 | 0 | 0.10452 | 320.7062 | 0.052633 | 0 | 0 | 0.10527 | 320.9641 | 0.053193 | 0 | 0 | 0.10639 | 321.222 | 0.053752 | 0 | 0 | 0.1075 | 321.3939 | 0.054125 | 0 | 0 | 0.10825 | 321.6518 | 0.054684 | 0 | 0 | 0.10937 | 321.9096 | 0.055244 | 0 | 0 | 0.11049 | 321.9956 | 0.05543 | 0 | 0 | 0.11086 | 322.2535 | 0.055989 | 0 | 0 | 0.11198 | 322.5113 | 0.056549 | 0 | 0 | 0.1131 | 322.6832 | 0.056922 | 0 | 0 | 0.11384 | 322.9411 | 0.057481 | 0 | 0 | 0.11496 | 323.113 | 0.057854 | 0 | 0 | 0.11571 | 323.2849 | 0.058227 | 0 | 0 | 0.11645
2017-12-27 05:00 | 292.6703 | 0.87233 |  | 307.3227 | 0.023605 | 0 | 0 | 0.047209 | 315.9588 | 0.042336 | 0 | 0 | 0.084673 | 323.0247 | 0.057662 | 0 | 0 | 0.11532 | 323.2864 | 0.05823 | 0 | 0 | 0.11646 | 323.4609 | 0.058608 | 0 | 0 | 0.11722 | 323.7226 | 0.059176 | 0 | 0 | 0.11835 | 323.9843 | 0.059744 | 0 | 0 | 0.11949 | 324.246 | 0.060311 | 0 | 0 | 0.12062 | 324.5949 | 0.061068 | 0 | 0 | 0.12214 | 324.8566 | 0.061636 | 0 | 0 | 0.12327 | 325.0311 | 0.062014 | 0 | 0 | 0.12403 | 325.2928 | 0.062582 | 0 | 0 | 0.12516 | 325.4673 | 0.06296 | 0 | 0 | 0.12592 | 325.729 | 0.063528 | 0 | 0 | 0.12706 | 325.9907 | 0.064095 | 0 | 0 | 0.12819 | 326.1651 | 0.064474 | 0 | 0 | 0.12895 | 326.4268 | 0.065041 | 0 | 0 | 0.13008 | 326.6885 | 0.065609 | 0 | 0 | 0.13122 | 326.7758 | 0.065798 | 0 | 0 | 0.1316 | 327.0375 | 0.066366 | 0 | 0 | 0.13273 | 327.2992 | 0.066934 | 0 | 0 | 0.13387 | 327.4736 | 0.067312 | 0 | 0 | 0.13462 | 327.7353 | 0.06788 | 0 | 0 | 0.13576 | 327.9098 | 0.068258 | 0 | 0 | 0.13652 | 328.0843 | 0.068636 | 0 | 0 | 0.13727
2017-12-27 06:00 | 294.0653 | 0.87649 |  | 308.7876 | 0.026782 | 0 | 0 | 0.053564 | 317.4648 | 0.045603 | 0 | 0 | 0.091206 | 324.5644 | 0.061002 | 0 | 0 | 0.122 | 324.8274 | 0.061572 | 0 | 0 | 0.12314 | 325.0027 | 0.061952 | 0 | 0 | 0.1239 | 325.2656 | 0.062523 | 0 | 0 | 0.12505 | 325.5286 | 0.063093 | 0 | 0 | 0.12619 | 325.7915 | 0.063663 | 0 | 0 | 0.12733 | 326.1421 | 0.064424 | 0 | 0 | 0.12885 | 326.405 | 0.064994 | 0 | 0 | 0.12999 | 326.5803 | 0.065374 | 0 | 0 | 0.13075 | 326.8433 | 0.065945 | 0 | 0 | 0.13189 | 327.0186 | 0.066325 | 0 | 0 | 0.13265 | 327.2815 | 0.066895 | 0 | 0 | 0.13379 | 327.5445 | 0.067466 | 0 | 0 | 0.13493 | 327.7198 | 0.067846 | 0 | 0 | 0.13569 | 327.9827 | 0.068416 | 0 | 0 | 0.13683 | 328.2457 | 0.068987 | 0 | 0 | 0.13797 | 328.3333 | 0.069177 | 0 | 0 | 0.13835 | 328.5963 | 0.069747 | 0 | 0 | 0.13949 | 328.8592 | 0.070317 | 0 | 0 | 0.14063 | 329.0345 | 0.070698 | 0 | 0 | 0.1414 | 329.2975 | 0.071268 | 0 | 0 | 0.14254 | 329.4728 | 0.071648 | 0 | 0 | 0.1433 | 329.6481 | 0.072028 | 0 | 0 | 0.14406
2017-12-27 07:00 | 302.1603 | 0.90062 |  | 317.2879 | 0.045219 | 0 | 0 | 0.090438 | 326.204 | 0.064558 | 0 | 0 | 0.12912 | 333.499 | 0.080381 | 0 | 0 | 0.16076 | 333.7692 | 0.080967 | 0 | 0 | 0.16193 | 333.9494 | 0.081358 | 0 | 0 | 0.16272 | 334.2195 | 0.081944 | 0 | 0 | 0.16389 | 334.4897 | 0.08253 | 0 | 0 | 0.16506 | 334.7599 | 0.083116 | 0 | 0 | 0.16623 | 335.1202 | 0.083897 | 0 | 0 | 0.16779 | 335.3903 | 0.084483 | 0 | 0 | 0.16897 | 335.5705 | 0.084874 | 0 | 0 | 0.16975 | 335.8407 | 0.08546 | 0 | 0 | 0.17092 | 336.0208 | 0.085851 | 0 | 0 | 0.1717 | 336.291 | 0.086437 | 0 | 0 | 0.17287 | 336.5611 | 0.087023 | 0 | 0 | 0.17405 | 336.7413 | 0.087413 | 0 | 0 | 0.17483 | 337.0115 | 0.087999 | 0 | 0 | 0.176 | 337.2816 | 0.088586 | 0 | 0 | 0.17717 | 337.3717 | 0.088781 | 0 | 0 | 0.17756 | 337.6419 | 0.089367 | 0 | 0 | 0.17873 | 337.9121 | 0.089953 | 0 | 0 | 0.17991 | 338.0922 | 0.090344 | 0 | 0 | 0.18069 | 338.3624 | 0.09093 | 0 | 0 | 0.18186 | 338.5425 | 0.09132 | 0 | 0 | 0.18264 | 338.7226 | 0.091711 | 0 | 0 | 0.18342
2017-12-27 08:00 | 298.032 | 0.88831 |  | 312.9529 | 0.035817 | 0 | 0 | 0.071633 | 321.7472 | 0.054891 | 0 | 0 | 0.10978 | 328.9426 | 0.070498 | 0 | 0 | 0.141 | 329.2091 | 0.071076 | 0 | 0 | 0.14215 | 329.3867 | 0.071461 | 0 | 0 | 0.14292 | 329.6532 | 0.072039 | 0 | 0 | 0.14408 | 329.9197 | 0.072617 | 0 | 0 | 0.14523 | 330.1862 | 0.073196 | 0 | 0 | 0.14639 | 330.5415 | 0.073966 | 0 | 0 | 0.14793 | 330.808 | 0.074544 | 0 | 0 | 0.14909 | 330.9857 | 0.07493 | 0 | 0 | 0.14986 | 331.2522 | 0.075508 | 0 | 0 | 0.15102 | 331.4298 | 0.075893 | 0 | 0 | 0.15179 | 331.6963 | 0.076471 | 0 | 0 | 0.15294 | 331.9628 | 0.077049 | 0 | 0 | 0.1541 | 332.1405 | 0.077434 | 0 | 0 | 0.15487 | 332.407 | 0.078012 | 0 | 0 | 0.15602 | 332.6735 | 0.07859 | 0 | 0 | 0.15718 | 332.7623 | 0.078783 | 0 | 0 | 0.15757 | 333.0288 | 0.079361 | 0 | 0 | 0.15872 | 333.2953 | 0.079939 | 0 | 0 | 0.15988 | 333.473 | 0.080324 | 0 | 0 | 0.16065 | 333.7395 | 0.080903 | 0 | 0 | 0.16181 | 333.9171 | 0.081288 | 0 | 0 | 0.16258 | 334.0948 | 0.081673 | 0 | 0 | 0.16335
2017-12-27 09:00 | 299.2427 | 0.89192 |  | 314.2243 | 0.038574 | 0 | 0 | 0.077148 | 323.0543 | 0.057726 | 0 | 0 | 0.11545 | 330.2789 | 0.073396 | 0 | 0 | 0.14679 | 330.5464 | 0.073977 | 0 | 0 | 0.14795 | 330.7248 | 0.074364 | 0 | 0 | 0.14873 | 330.9924 | 0.074944 | 0 | 0 | 0.14989 | 331.26 | 0.075525 | 0 | 0 | 0.15105 | 331.5275 | 0.076105 | 0 | 0 | 0.15221 | 331.8843 | 0.076879 | 0 | 0 | 0.15376 | 332.1519 | 0.077459 | 0 | 0 | 0.15492 | 332.3303 | 0.077846 | 0 | 0 | 0.15569 | 332.5979 | 0.078426 | 0 | 0 | 0.15685 | 332.7762 | 0.078813 | 0 | 0 | 0.15763 | 333.0438 | 0.079394 | 0 | 0 | 0.15879 | 333.3114 | 0.079974 | 0 | 0 | 0.15995 | 333.4898 | 0.080361 | 0 | 0 | 0.16072 | 333.7574 | 0.080941 | 0 | 0 | 0.16188 | 334.0249 | 0.081522 | 0 | 0 | 0.16304 | 334.1141 | 0.081715 | 0 | 0 | 0.16343 | 334.3817 | 0.082296 | 0 | 0 | 0.16459 | 334.6493 | 0.082876 | 0 | 0 | 0.16575 | 334.8277 | 0.083263 | 0 | 0 | 0.16653 | 335.0952 | 0.083843 | 0 | 0 | 0.16769 | 335.2736 | 0.08423 | 0 | 0 | 0.16846 | 335.452 | 0.084617 | 0 | 0 | 0.16923
2017-12-27 10:00 | 295.7671 | 0.88156 |  | 310.5746 | 0.030658 | 0 | 0 | 0.061316 | 319.3021 | 0.049588 | 0 | 0 | 0.099176 | 326.4427 | 0.065076 | 0 | 0 | 0.13015 | 326.7072 | 0.06565 | 0 | 0 | 0.1313 | 326.8835 | 0.066032 | 0 | 0 | 0.13206 | 327.148 | 0.066606 | 0 | 0 | 0.13321 | 327.4125 | 0.067179 | 0 | 0 | 0.13436 | 327.6769 | 0.067753 | 0 | 0 | 0.13551 | 328.0296 | 0.068518 | 0 | 0 | 0.13704 | 328.294 | 0.069091 | 0 | 0 | 0.13818 | 328.4703 | 0.069474 | 0 | 0 | 0.13895 | 328.7348 | 0.070047 | 0 | 0 | 0.14009 | 328.9111 | 0.07043 | 0 | 0 | 0.14086 | 329.1756 | 0.071004 | 0 | 0 | 0.14201 | 329.4401 | 0.071577 | 0 | 0 | 0.14315 | 329.6164 | 0.07196 | 0 | 0 | 0.14392 | 329.8808 | 0.072533 | 0 | 0 | 0.14507 | 330.1453 | 0.073107 | 0 | 0 | 0.14621 | 330.2335 | 0.073298 | 0 | 0 | 0.1466 | 330.4979 | 0.073872 | 0 | 0 | 0.14774 | 330.7624 | 0.074445 | 0 | 0 | 0.14889 | 330.9387 | 0.074828 | 0 | 0 | 0.14966 | 331.2032 | 0.075401 | 0 | 0 | 0.1508 | 331.3795 | 0.075784 | 0 | 0 | 0.15157 | 331.5558 | 0.076166 | 0 | 0 | 0.15233
2017-12-27 11:00 | 292.7475 | 0.87256 |  | 307.4038 | 0.023781 | 0 | 0 | 0.047561 | 316.0422 | 0.042517 | 0 | 0 | 0.085034 | 323.11 | 0.057847 | 0 | 0 | 0.11569 | 323.3717 | 0.058415 | 0 | 0 | 0.11683 | 323.5462 | 0.058793 | 0 | 0 | 0.11759 | 323.808 | 0.059361 | 0 | 0 | 0.11872 | 324.0698 | 0.059929 | 0 | 0 | 0.11986 | 324.3315 | 0.060497 | 0 | 0 | 0.12099 | 324.6806 | 0.061254 | 0 | 0 | 0.12251 | 324.9423 | 0.061822 | 0 | 0 | 0.12364 | 325.1168 | 0.0622 | 0 | 0 | 0.1244 | 325.3786 | 0.062768 | 0 | 0 | 0.12554 | 325.5531 | 0.063146 | 0 | 0 | 0.12629 | 325.8149 | 0.063714 | 0 | 0 | 0.12743 | 326.0767 | 0.064282 | 0 | 0 | 0.12856 | 326.2512 | 0.06466 | 0 | 0 | 0.12932 | 326.5129 | 0.065228 | 0 | 0 | 0.13046 | 326.7747 | 0.065796 | 0 | 0 | 0.13159 | 326.862 | 0.065985 | 0 | 0 | 0.13197 | 327.1237 | 0.066553 | 0 | 0 | 0.13311 | 327.3855 | 0.067121 | 0 | 0 | 0.13424 | 327.56 | 0.067499 | 0 | 0 | 0.135 | 327.8218 | 0.068067 | 0 | 0 | 0.13613 | 327.9963 | 0.068446 | 0 | 0 | 0.13689 | 328.1708 | 0.068824 | 0 | 0 | 0.13765
2017-12-27 12:00 | 296.0063 | 0.88228 |  | 310.8258 | 0.031203 | 0 | 0 | 0.062406 | 319.5603 | 0.050148 | 0 | 0 | 0.1003 | 326.7068 | 0.065649 | 0 | 0 | 0.1313 | 326.9714 | 0.066223 | 0 | 0 | 0.13245 | 327.1479 | 0.066605 | 0 | 0 | 0.13321 | 327.4126 | 0.06718 | 0 | 0 | 0.13436 | 327.6773 | 0.067754 | 0 | 0 | 0.13551 | 327.9419 | 0.068328 | 0 | 0 | 0.13666 | 328.2949 | 0.069093 | 0 | 0 | 0.13819 | 328.5595 | 0.069667 | 0 | 0 | 0.13933 | 328.736 | 0.07005 | 0 | 0 | 0.1401 | 329.0007 | 0.070624 | 0 | 0 | 0.14125 | 329.1771 | 0.071007 | 0 | 0 | 0.14201 | 329.4418 | 0.071581 | 0 | 0 | 0.14316 | 329.7065 | 0.072155 | 0 | 0 | 0.14431 | 329.8829 | 0.072538 | 0 | 0 | 0.14508 | 330.1476 | 0.073112 | 0 | 0 | 0.14622 | 330.4123 | 0.073686 | 0 | 0 | 0.14737 | 330.5005 | 0.073877 | 0 | 0 | 0.14775 | 330.7652 | 0.074451 | 0 | 0 | 0.1489 | 331.0299 | 0.075026 | 0 | 0 | 0.15005 | 331.2064 | 0.075408 | 0 | 0 | 0.15082 | 331.471 | 0.075982 | 0 | 0 | 0.15196 | 331.6475 | 0.076365 | 0 | 0 | 0.15273 | 331.824 | 0.076748 | 0 | 0 | 0.1535
2017-12-27 13:00 | 285.5155 | 0.85101 |  | 299.8097 | 0.0073089 | 0 | 0 | 0.014618 | 308.2347 | 0.025583 | 0 | 0 | 0.051165 | 315.1278 | 0.040534 | 0 | 0 | 0.081068 | 315.3831 | 0.041088 | 0 | 0 | 0.082175 | 315.5533 | 0.041457 | 0 | 0 | 0.082914 | 315.8086 | 0.042011 | 0 | 0 | 0.084021 | 316.0639 | 0.042564 | 0 | 0 | 0.085129 | 316.3193 | 0.043118 | 0 | 0 | 0.086236 | 316.6597 | 0.043856 | 0 | 0 | 0.087713 | 316.915 | 0.04441 | 0 | 0 | 0.08882 | 317.0852 | 0.044779 | 0 | 0 | 0.089559 | 317.3405 | 0.045333 | 0 | 0 | 0.090666 | 317.5107 | 0.045702 | 0 | 0 | 0.091405 | 317.766 | 0.046256 | 0 | 0 | 0.092512 | 318.0213 | 0.04681 | 0 | 0 | 0.09362 | 318.1915 | 0.047179 | 0 | 0 | 0.094358 | 318.4468 | 0.047733 | 0 | 0 | 0.095465 | 318.7021 | 0.048286 | 0 | 0 | 0.096573 | 318.7872 | 0.048471 | 0 | 0 | 0.096942 | 319.0425 | 0.049025 | 0 | 0 | 0.09805 | 319.2978 | 0.049579 | 0 | 0 | 0.099157 | 319.468 | 0.049948 | 0 | 0 | 0.099895 | 319.7233 | 0.050501 | 0 | 0 | 0.101 | 319.8935 | 0.050871 | 0 | 0 | 0.10174 | 320.0637 | 0.05124 | 0 | 0 | 0.10248
2017-12-27 14:00 | 278.0938 | 0.82889 |  | 292.0165 | 0 | 0 | 0 | 0 | 300.2225 | 0.0082042 | 0 | 0 | 0.016408 | 306.9365 | 0.022767 | 0 | 0 | 0.045534 | 307.1851 | 0.023306 | 0 | 0 | 0.046612 | 307.3509 | 0.023666 | 0 | 0 | 0.047332 | 307.5996 | 0.024205 | 0 | 0 | 0.04841 | 307.8482 | 0.024744 | 0 | 0 | 0.049489 | 308.0969 | 0.025284 | 0 | 0 | 0.050568 | 308.4285 | 0.026003 | 0 | 0 | 0.052006 | 308.6771 | 0.026542 | 0 | 0 | 0.053085 | 308.8429 | 0.026902 | 0 | 0 | 0.053804 | 309.0916 | 0.027441 | 0 | 0 | 0.054883 | 309.2574 | 0.027801 | 0 | 0 | 0.055602 | 309.506 | 0.02834 | 0 | 0 | 0.05668 | 309.7547 | 0.02888 | 0 | 0 | 0.057759 | 309.9205 | 0.029239 | 0 | 0 | 0.058478 | 310.1691 | 0.029778 | 0 | 0 | 0.059557 | 310.4178 | 0.030318 | 0 | 0 | 0.060636 | 310.5007 | 0.030498 | 0 | 0 | 0.060995 | 310.7493 | 0.031037 | 0 | 0 | 0.062074 | 310.998 | 0.031576 | 0 | 0 | 0.063153 | 311.1638 | 0.031936 | 0 | 0 | 0.063872 | 311.4125 | 0.032475 | 0 | 0 | 0.064951 | 311.5782 | 0.032835 | 0 | 0 | 0.06567 | 311.744 | 0.033194 | 0 | 0 | 0.066389
2017-12-27 15:00 | 280.6903 | 0.83662 |  | 294.743 | 0 | 0 | 0 | 0 | 303.0255 | 0.014284 | 0 | 0 | 0.028568 | 309.8022 | 0.028983 | 0 | 0 | 0.057965 | 310.0532 | 0.029527 | 0 | 0 | 0.059054 | 310.2205 | 0.02989 | 0 | 0 | 0.05978 | 310.4715 | 0.030434 | 0 | 0 | 0.060869 | 310.7225 | 0.030979 | 0 | 0 | 0.061957 | 310.9735 | 0.031523 | 0 | 0 | 0.063046 | 311.3081 | 0.032249 | 0 | 0 | 0.064498 | 311.5591 | 0.032793 | 0 | 0 | 0.065587 | 311.7264 | 0.033156 | 0 | 0 | 0.066313 | 311.9774 | 0.033701 | 0 | 0 | 0.067401 | 312.1447 | 0.034064 | 0 | 0 | 0.068127 | 312.3957 | 0.034608 | 0 | 0 | 0.069216 | 312.6467 | 0.035152 | 0 | 0 | 0.070305 | 312.814 | 0.035515 | 0 | 0 | 0.071031 | 313.065 | 0.03606 | 0 | 0 | 0.072119 | 313.316 | 0.036604 | 0 | 0 | 0.073208 | 313.3997 | 0.036786 | 0 | 0 | 0.073571 | 313.6507 | 0.03733 | 0 | 0 | 0.07466 | 313.9017 | 0.037874 | 0 | 0 | 0.075749 | 314.069 | 0.038237 | 0 | 0 | 0.076475 | 314.32 | 0.038782 | 0 | 0 | 0.077563 | 314.4873 | 0.039145 | 0 | 0 | 0.078289 | 314.6546 | 0.039508 | 0 | 0 | 0.079015
2017-12-27 16:00 | 289.8616 | 0.86396 |  | 304.3735 | 0.017208 | 0 | 0 | 0.034415 | 312.9267 | 0.03576 | 0 | 0 | 0.071519 | 319.9248 | 0.050938 | 0 | 0 | 0.10188 | 320.184 | 0.051501 | 0 | 0 | 0.103 | 320.3568 | 0.051875 | 0 | 0 | 0.10375 | 320.6159 | 0.052438 | 0 | 0 | 0.10488 | 320.8751 | 0.053 | 0 | 0 | 0.106 | 321.1343 | 0.053562 | 0 | 0 | 0.10712 | 321.4799 | 0.054312 | 0 | 0 | 0.10862 | 321.7391 | 0.054874 | 0 | 0 | 0.10975 | 321.9119 | 0.055249 | 0 | 0 | 0.1105 | 322.1711 | 0.055811 | 0 | 0 | 0.11162 | 322.3439 | 0.056185 | 0 | 0 | 0.11237 | 322.6031 | 0.056748 | 0 | 0 | 0.1135 | 322.8622 | 0.05731 | 0 | 0 | 0.11462 | 323.035 | 0.057685 | 0 | 0 | 0.11537 | 323.2942 | 0.058247 | 0 | 0 | 0.11649 | 323.5534 | 0.058809 | 0 | 0 | 0.11762 | 323.6398 | 0.058996 | 0 | 0 | 0.11799 | 323.899 | 0.059559 | 0 | 0 | 0.11912 | 324.1582 | 0.060121 | 0 | 0 | 0.12024 | 324.331 | 0.060496 | 0 | 0 | 0.12099 | 324.5902 | 0.061058 | 0 | 0 | 0.12212 | 324.763 | 0.061432 | 0 | 0 | 0.12286 | 324.9357 | 0.061807 | 0 | 0 | 0.12361
2017-12-27 17:00 | 264.3868 | 0.78803 |  | 277.6232 | 0 | 0 | 0 | 0 | 285.4247 | 0 | 0 | 0 | 0 | 291.8078 | 0 | 0 | 0 | 0 | 292.0442 | 0 | 0 | 0 | 0 | 292.2018 | 0 | 0 | 0 | 0 | 292.4382 | 0 | 0 | 0 | 0 | 292.6746 | 0 | 0 | 0 | 0 | 292.911 | 0 | 0 | 0 | 0 | 293.2262 | 0 | 0 | 0 | 0 | 293.4626 | 0 | 0 | 0 | 0 | 293.6202 | 0 | 0 | 0 | 0 | 293.8566 | 0 | 0 | 0 | 0 | 294.0142 | 0 | 0 | 0 | 0 | 294.2507 | 0 | 0 | 0 | 0 | 294.4871 | 0 | 0 | 0 | 0 | 294.6447 | 0 | 0 | 0 | 0 | 294.8811 | 0 | 0 | 0 | 0 | 295.1175 | 0 | 0 | 0 | 0 | 295.1963 | 0 | 0 | 0 | 0 | 295.4327 | 0 | 0 | 0 | 0 | 295.6691 | 0 | 0 | 0 | 0 | 295.8267 | 0 | 0 | 0 | 0 | 296.0631 | 0 | 0 | 0 | 0 | 296.2207 | 0 | 0 | 0 | 0 | 296.3783 | 0 | 0 | 0 | 0
2017-12-27 18:00 | 264.2104 | 0.78751 |  | 277.4381 | 0 | 0 | 0 | 0 | 285.2344 | 0 | 0 | 0 | 0 | 291.6131 | 0 | 0 | 0 | 0 | 291.8494 | 0 | 0 | 0 | 0 | 292.0069 | 0 | 0 | 0 | 0 | 292.2432 | 0 | 0 | 0 | 0 | 292.4794 | 0 | 0 | 0 | 0 | 292.7157 | 0 | 0 | 0 | 0 | 293.0307 | 0 | 0 | 0 | 0 | 293.2669 | 0 | 0 | 0 | 0 | 293.4244 | 0 | 0 | 0 | 0 | 293.6607 | 0 | 0 | 0 | 0 | 293.8182 | 0 | 0 | 0 | 0 | 294.0544 | 0 | 0 | 0 | 0 | 294.2907 | 0 | 0 | 0 | 0 | 294.4482 | 0 | 0 | 0 | 0 | 294.6844 | 0 | 0 | 0 | 0 | 294.9207 | 0 | 0 | 0 | 0 | 294.9994 | 0 | 0 | 0 | 0 | 295.2357 | 0 | 0 | 0 | 0 | 295.4719 | 0 | 0 | 0 | 0 | 295.6294 | 0 | 0 | 0 | 0 | 295.8657 | 0 | 0 | 0 | 0 | 296.0232 | 0 | 0 | 0 | 0 | 296.1807 | 0 | 0 | 0 | 0
2017-12-27 19:00 | 264.1266 | 0.78726 |  | 277.35 | 0 | 0 | 0 | 0 | 285.1438 | 0 | 0 | 0 | 0 | 291.5206 | 0 | 0 | 0 | 0 | 291.7568 | 0 | 0 | 0 | 0 | 291.9142 | 0 | 0 | 0 | 0 | 292.1504 | 0 | 0 | 0 | 0 | 292.3866 | 0 | 0 | 0 | 0 | 292.6227 | 0 | 0 | 0 | 0 | 292.9376 | 0 | 0 | 0 | 0 | 293.1738 | 0 | 0 | 0 | 0 | 293.3313 | 0 | 0 | 0 | 0 | 293.5674 | 0 | 0 | 0 | 0 | 293.7249 | 0 | 0 | 0 | 0 | 293.9611 | 0 | 0 | 0 | 0 | 294.1972 | 0 | 0 | 0 | 0 | 294.3547 | 0 | 0 | 0 | 0 | 294.5909 | 0 | 0 | 0 | 0 | 294.827 | 0 | 0 | 0 | 0 | 294.9058 | 0 | 0 | 0 | 0 | 295.1419 | 0 | 0 | 0 | 0 | 295.3781 | 0 | 0 | 0 | 0 | 295.5356 | 0 | 0 | 0 | 0 | 295.7718 | 0 | 0 | 0 | 0 | 295.9292 | 0 | 0 | 0 | 0 | 296.0867 | 0 | 0 | 0 | 0
2017-12-27 20:00 | 273.521 | 0.81526 |  | 287.2147 | 0 | 0 | 0 | 0 | 295.2858 | 0 | 0 | 0 | 0 | 301.8893 | 0.01182 | 0 | 0 | 0.023639 | 302.1339 | 0.01235 | 0 | 0 | 0.0247 | 302.297 | 0.012704 | 0 | 0 | 0.025407 | 302.5415 | 0.013234 | 0 | 0 | 0.026468 | 302.7861 | 0.013765 | 0 | 0 | 0.027529 | 303.0307 | 0.014295 | 0 | 0 | 0.02859 | 303.3568 | 0.015003 | 0 | 0 | 0.030005 | 303.6014 | 0.015533 | 0 | 0 | 0.031066 | 303.7644 | 0.015887 | 0 | 0 | 0.031773 | 304.009 | 0.016417 | 0 | 0 | 0.032834 | 304.172 | 0.016771 | 0 | 0 | 0.033542 | 304.4166 | 0.017301 | 0 | 0 | 0.034603 | 304.6612 | 0.017832 | 0 | 0 | 0.035664 | 304.8243 | 0.018185 | 0 | 0 | 0.036371 | 305.0688 | 0.018716 | 0 | 0 | 0.037432 | 305.3134 | 0.019246 | 0 | 0 | 0.038493 | 305.3949 | 0.019423 | 0 | 0 | 0.038846 | 305.6395 | 0.019954 | 0 | 0 | 0.039907 | 305.8841 | 0.020484 | 0 | 0 | 0.040968 | 306.0471 | 0.020838 | 0 | 0 | 0.041676 | 306.2917 | 0.021368 | 0 | 0 | 0.042737 | 306.4548 | 0.021722 | 0 | 0 | 0.043444 | 306.6178 | 0.022076 | 0 | 0 | 0.044151
2017-12-27 21:00 | 291.6432 | 0.86927 |  | 306.2443 | 0.021265 | 0 | 0 | 0.042531 | 314.8501 | 0.039931 | 0 | 0 | 0.079863 | 321.8912 | 0.055204 | 0 | 0 | 0.11041 | 322.1519 | 0.055769 | 0 | 0 | 0.11154 | 322.3258 | 0.056146 | 0 | 0 | 0.11229 | 322.5866 | 0.056712 | 0 | 0 | 0.11342 | 322.8474 | 0.057278 | 0 | 0 | 0.11456 | 323.1081 | 0.057843 | 0 | 0 | 0.11569 | 323.4558 | 0.058597 | 0 | 0 | 0.11719 | 323.7166 | 0.059163 | 0 | 0 | 0.11833 | 323.8905 | 0.05954 | 0 | 0 | 0.11908 | 324.1513 | 0.060106 | 0 | 0 | 0.12021 | 324.3251 | 0.060483 | 0 | 0 | 0.12097 | 324.5859 | 0.061048 | 0 | 0 | 0.1221 | 324.8467 | 0.061614 | 0 | 0 | 0.12323 | 325.0205 | 0.061991 | 0 | 0 | 0.12398 | 325.2813 | 0.062557 | 0 | 0 | 0.12511 | 325.5421 | 0.063122 | 0 | 0 | 0.12624 | 325.629 | 0.063311 | 0 | 0 | 0.12662 | 325.8898 | 0.063877 | 0 | 0 | 0.12775 | 326.1506 | 0.064442 | 0 | 0 | 0.12888 | 326.3244 | 0.064819 | 0 | 0 | 0.12964 | 326.5852 | 0.065385 | 0 | 0 | 0.13077 | 326.7591 | 0.065762 | 0 | 0 | 0.13152 | 326.9329 | 0.066139 | 0 | 0 | 0.13228
2017-12-27 22:00 | 297.3637 | 0.88632 |  | 312.2511 | 0.034294 | 0 | 0 | 0.068589 | 321.0257 | 0.053326 | 0 | 0 | 0.10665 | 328.2049 | 0.068898 | 0 | 0 | 0.1378 | 328.4708 | 0.069475 | 0 | 0 | 0.13895 | 328.6481 | 0.069859 | 0 | 0 | 0.13972 | 328.914 | 0.070436 | 0 | 0 | 0.14087 | 329.1799 | 0.071013 | 0 | 0 | 0.14203 | 329.4458 | 0.071589 | 0 | 0 | 0.14318 | 329.8003 | 0.072358 | 0 | 0 | 0.14472 | 330.0662 | 0.072935 | 0 | 0 | 0.14587 | 330.2434 | 0.07332 | 0 | 0 | 0.14664 | 330.5093 | 0.073896 | 0 | 0 | 0.14779 | 330.6866 | 0.074281 | 0 | 0 | 0.14856 | 330.9525 | 0.074858 | 0 | 0 | 0.14972 | 331.2184 | 0.075434 | 0 | 0 | 0.15087 | 331.3957 | 0.075819 | 0 | 0 | 0.15164 | 331.6616 | 0.076396 | 0 | 0 | 0.15279 | 331.9275 | 0.076972 | 0 | 0 | 0.15394 | 332.0161 | 0.077165 | 0 | 0 | 0.15433 | 332.282 | 0.077741 | 0 | 0 | 0.15548 | 332.5479 | 0.078318 | 0 | 0 | 0.15664 | 332.7251 | 0.078702 | 0 | 0 | 0.1574 | 332.991 | 0.079279 | 0 | 0 | 0.15856 | 333.1683 | 0.079664 | 0 | 0 | 0.15933 | 333.3456 | 0.080048 | 0 | 0 | 0.1601
2017-12-27 23:00 | 290.9132 | 0.8671 |  | 305.4777 | 0.019603 | 0 | 0 | 0.039206 | 314.062 | 0.038222 | 0 | 0 | 0.076444 | 321.0855 | 0.053456 | 0 | 0 | 0.10691 | 321.3456 | 0.05402 | 0 | 0 | 0.10804 | 321.519 | 0.054396 | 0 | 0 | 0.10879 | 321.7791 | 0.054961 | 0 | 0 | 0.10992 | 322.0393 | 0.055525 | 0 | 0 | 0.11105 | 322.2994 | 0.056089 | 0 | 0 | 0.11218 | 322.6462 | 0.056841 | 0 | 0 | 0.11368 | 322.9064 | 0.057406 | 0 | 0 | 0.11481 | 323.0798 | 0.057782 | 0 | 0 | 0.11556 | 323.3399 | 0.058346 | 0 | 0 | 0.11669 | 323.5133 | 0.058722 | 0 | 0 | 0.11744 | 323.7735 | 0.059286 | 0 | 0 | 0.11857 | 324.0336 | 0.05985 | 0 | 0 | 0.1197 | 324.207 | 0.060227 | 0 | 0 | 0.12045 | 324.4671 | 0.060791 | 0 | 0 | 0.12158 | 324.7273 | 0.061355 | 0 | 0 | 0.12271 | 324.814 | 0.061543 | 0 | 0 | 0.12309 | 325.0741 | 0.062107 | 0 | 0 | 0.12421 | 325.3342 | 0.062672 | 0 | 0 | 0.12534 | 325.5076 | 0.063048 | 0 | 0 | 0.1261 | 325.7678 | 0.063612 | 0 | 0 | 0.12722 | 325.9412 | 0.063988 | 0 | 0 | 0.12798 | 326.1146 | 0.064364 | 0 | 0 | 0.12873
2017-12-28 | 297.9937 | 0.8882 |  | 312.9127 | 0.035729 | 0 | 0 | 0.071458 | 321.7058 | 0.054802 | 0 | 0 | 0.1096 | 328.9002 | 0.070406 | 0 | 0 | 0.14081 | 329.1667 | 0.070984 | 0 | 0 | 0.14197 | 329.3443 | 0.07137 | 0 | 0 | 0.14274 | 329.6108 | 0.071947 | 0 | 0 | 0.14389 | 329.8773 | 0.072525 | 0 | 0 | 0.14505 | 330.1437 | 0.073103 | 0 | 0 | 0.14621 | 330.499 | 0.073874 | 0 | 0 | 0.14775 | 330.7655 | 0.074452 | 0 | 0 | 0.1489 | 330.9431 | 0.074837 | 0 | 0 | 0.14967 | 331.2096 | 0.075415 | 0 | 0 | 0.15083 | 331.3872 | 0.0758 | 0 | 0 | 0.1516 | 331.6537 | 0.076378 | 0 | 0 | 0.15276 | 331.9201 | 0.076956 | 0 | 0 | 0.15391 | 332.0978 | 0.077342 | 0 | 0 | 0.15468 | 332.3642 | 0.07792 | 0 | 0 | 0.15584 | 332.6307 | 0.078498 | 0 | 0 | 0.157 | 332.7195 | 0.07869 | 0 | 0 | 0.15738 | 332.986 | 0.079268 | 0 | 0 | 0.15854 | 333.2524 | 0.079846 | 0 | 0 | 0.15969 | 333.4301 | 0.080231 | 0 | 0 | 0.16046 | 333.6965 | 0.080809 | 0 | 0 | 0.16162 | 333.8742 | 0.081195 | 0 | 0 | 0.16239 | 334.0518 | 0.08158 | 0 | 0 | 0.16316
2017-12-28 01:00 | 290.3243 | 0.86534 |  | 304.8593 | 0.018261 | 0 | 0 | 0.036523 | 313.4262 | 0.036843 | 0 | 0 | 0.073686 | 320.4354 | 0.052046 | 0 | 0 | 0.10409 | 320.695 | 0.052609 | 0 | 0 | 0.10522 | 320.8681 | 0.052985 | 0 | 0 | 0.10597 | 321.1277 | 0.053548 | 0 | 0 | 0.1071 | 321.3873 | 0.054111 | 0 | 0 | 0.10822 | 321.6469 | 0.054674 | 0 | 0 | 0.10935 | 321.993 | 0.055425 | 0 | 0 | 0.11085 | 322.2526 | 0.055988 | 0 | 0 | 0.11198 | 322.4257 | 0.056363 | 0 | 0 | 0.11273 | 322.6853 | 0.056926 | 0 | 0 | 0.11385 | 322.8584 | 0.057301 | 0 | 0 | 0.1146 | 323.118 | 0.057865 | 0 | 0 | 0.11573 | 323.3776 | 0.058428 | 0 | 0 | 0.11686 | 323.5506 | 0.058803 | 0 | 0 | 0.11761 | 323.8102 | 0.059366 | 0 | 0 | 0.11873 | 324.0698 | 0.059929 | 0 | 0 | 0.11986 | 324.1564 | 0.060117 | 0 | 0 | 0.12023 | 324.416 | 0.06068 | 0 | 0 | 0.12136 | 324.6756 | 0.061243 | 0 | 0 | 0.12249 | 324.8486 | 0.061618 | 0 | 0 | 0.12324 | 325.1082 | 0.062181 | 0 | 0 | 0.12436 | 325.2813 | 0.062557 | 0 | 0 | 0.12511 | 325.4544 | 0.062932 | 0 | 0 | 0.12586
2017-12-28 02:00 | 298.6811 | 0.89025 |  | 313.6344 | 0.037295 | 0 | 0 | 0.07459 | 322.4479 | 0.056411 | 0 | 0 | 0.11282 | 329.6589 | 0.072052 | 0 | 0 | 0.1441 | 329.926 | 0.072631 | 0 | 0 | 0.14526 | 330.104 | 0.073017 | 0 | 0 | 0.14603 | 330.3711 | 0.073597 | 0 | 0 | 0.14719 | 330.6382 | 0.074176 | 0 | 0 | 0.14835 | 330.9053 | 0.074755 | 0 | 0 | 0.14951 | 331.2614 | 0.075528 | 0 | 0 | 0.15106 | 331.5284 | 0.076107 | 0 | 0 | 0.15221 | 331.7065 | 0.076493 | 0 | 0 | 0.15299 | 331.9736 | 0.077072 | 0 | 0 | 0.15414 | 332.1516 | 0.077458 | 0 | 0 | 0.15492 | 332.4187 | 0.078038 | 0 | 0 | 0.15608 | 332.6858 | 0.078617 | 0 | 0 | 0.15723 | 332.8638 | 0.079003 | 0 | 0 | 0.15801 | 333.1309 | 0.079583 | 0 | 0 | 0.15917 | 333.398 | 0.080162 | 0 | 0 | 0.16032 | 333.487 | 0.080355 | 0 | 0 | 0.16071 | 333.7541 | 0.080934 | 0 | 0 | 0.16187 | 334.0211 | 0.081513 | 0 | 0 | 0.16303 | 334.1992 | 0.0819 | 0 | 0 | 0.1638 | 334.4663 | 0.082479 | 0 | 0 | 0.16496 | 334.6443 | 0.082865 | 0 | 0 | 0.16573 | 334.8224 | 0.083251 | 0 | 0 | 0.1665
2017-12-28 03:00 | 298.2375 | 0.88893 |  | 313.1687 | 0.036285 | 0 | 0 | 0.072569 | 321.9691 | 0.055373 | 0 | 0 | 0.11075 | 329.1694 | 0.07099 | 0 | 0 | 0.14198 | 329.4361 | 0.071568 | 0 | 0 | 0.14314 | 329.6139 | 0.071954 | 0 | 0 | 0.14391 | 329.8805 | 0.072533 | 0 | 0 | 0.14507 | 330.1472 | 0.073111 | 0 | 0 | 0.14622 | 330.4139 | 0.073689 | 0 | 0 | 0.14738 | 330.7695 | 0.074461 | 0 | 0 | 0.14892 | 331.0361 | 0.075039 | 0 | 0 | 0.15008 | 331.2139 | 0.075425 | 0 | 0 | 0.15085 | 331.4806 | 0.076003 | 0 | 0 | 0.15201 | 331.6584 | 0.076389 | 0 | 0 | 0.15278 | 331.9251 | 0.076967 | 0 | 0 | 0.15393 | 332.1918 | 0.077546 | 0 | 0 | 0.15509 | 332.3695 | 0.077931 | 0 | 0 | 0.15586 | 332.6362 | 0.07851 | 0 | 0 | 0.15702 | 332.9029 | 0.079088 | 0 | 0 | 0.15818 | 332.9918 | 0.079281 | 0 | 0 | 0.15856 | 333.2585 | 0.079859 | 0 | 0 | 0.15972 | 333.5251 | 0.080438 | 0 | 0 | 0.16088 | 333.7029 | 0.080823 | 0 | 0 | 0.16165 | 333.9696 | 0.081402 | 0 | 0 | 0.1628 | 334.1474 | 0.081787 | 0 | 0 | 0.16357 | 334.3252 | 0.082173 | 0 | 0 | 0.16435
2017-12-28 04:00 | 297.2034 | 0.88584 |  | 312.0828 | 0.033929 | 0 | 0 | 0.067858 | 320.8526 | 0.052951 | 0 | 0 | 0.1059 | 328.028 | 0.068514 | 0 | 0 | 0.13703 | 328.2937 | 0.069091 | 0 | 0 | 0.13818 | 328.4709 | 0.069475 | 0 | 0 | 0.13895 | 328.7366 | 0.070051 | 0 | 0 | 0.1401 | 329.0024 | 0.070628 | 0 | 0 | 0.14126 | 329.2681 | 0.071204 | 0 | 0 | 0.14241 | 329.6225 | 0.071973 | 0 | 0 | 0.14395 | 329.8882 | 0.072549 | 0 | 0 | 0.1451 | 330.0654 | 0.072933 | 0 | 0 | 0.14587 | 330.3311 | 0.07351 | 0 | 0 | 0.14702 | 330.5083 | 0.073894 | 0 | 0 | 0.14779 | 330.7741 | 0.074471 | 0 | 0 | 0.14894 | 331.0398 | 0.075047 | 0 | 0 | 0.15009 | 331.217 | 0.075431 | 0 | 0 | 0.15086 | 331.4827 | 0.076008 | 0 | 0 | 0.15202 | 331.7485 | 0.076584 | 0 | 0 | 0.15317 | 331.8371 | 0.076776 | 0 | 0 | 0.15355 | 332.1028 | 0.077353 | 0 | 0 | 0.15471 | 332.3686 | 0.077929 | 0 | 0 | 0.15586 | 332.5458 | 0.078313 | 0 | 0 | 0.15663 | 332.8115 | 0.07889 | 0 | 0 | 0.15778 | 332.9887 | 0.079274 | 0 | 0 | 0.15855 | 333.1658 | 0.079658 | 0 | 0 | 0.15932
2017-12-28 05:00 | 292.4218 | 0.87159 |  | 307.0618 | 0.023039 | 0 | 0 | 0.046077 | 315.6905 | 0.041754 | 0 | 0 | 0.083509 | 322.7504 | 0.057067 | 0 | 0 | 0.11413 | 323.0119 | 0.057634 | 0 | 0 | 0.11527 | 323.1862 | 0.058013 | 0 | 0 | 0.11603 | 323.4477 | 0.05858 | 0 | 0 | 0.11716 | 323.7092 | 0.059147 | 0 | 0 | 0.11829 | 323.9707 | 0.059714 | 0 | 0 | 0.11943 | 324.3193 | 0.06047 | 0 | 0 | 0.12094 | 324.5808 | 0.061037 | 0 | 0 | 0.12207 | 324.7551 | 0.061415 | 0 | 0 | 0.12283 | 325.0166 | 0.061983 | 0 | 0 | 0.12397 | 325.1909 | 0.062361 | 0 | 0 | 0.12472 | 325.4524 | 0.062928 | 0 | 0 | 0.12586 | 325.7138 | 0.063495 | 0 | 0 | 0.12699 | 325.8882 | 0.063873 | 0 | 0 | 0.12775 | 326.1496 | 0.06444 | 0 | 0 | 0.12888 | 326.4111 | 0.065007 | 0 | 0 | 0.13001 | 326.4983 | 0.065196 | 0 | 0 | 0.13039 | 326.7597 | 0.065764 | 0 | 0 | 0.13153 | 327.0212 | 0.066331 | 0 | 0 | 0.13266 | 327.1955 | 0.066709 | 0 | 0 | 0.13342 | 327.457 | 0.067276 | 0 | 0 | 0.13455 | 327.6313 | 0.067654 | 0 | 0 | 0.13531 | 327.8057 | 0.068032 | 0 | 0 | 0.13606
2017-12-28 06:00 | 291.95 | 0.87019 |  | 306.5664 | 0.021964 | 0 | 0 | 0.043928 | 315.1812 | 0.04065 | 0 | 0 | 0.081299 | 322.2297 | 0.055938 | 0 | 0 | 0.11188 | 322.4908 | 0.056504 | 0 | 0 | 0.11301 | 322.6648 | 0.056882 | 0 | 0 | 0.11376 | 322.9259 | 0.057448 | 0 | 0 | 0.1149 | 323.1869 | 0.058014 | 0 | 0 | 0.11603 | 323.448 | 0.05858 | 0 | 0 | 0.11716 | 323.7961 | 0.059335 | 0 | 0 | 0.11867 | 324.0571 | 0.059902 | 0 | 0 | 0.1198 | 324.2312 | 0.060279 | 0 | 0 | 0.12056 | 324.4922 | 0.060845 | 0 | 0 | 0.12169 | 324.6662 | 0.061223 | 0 | 0 | 0.12245 | 324.9273 | 0.061789 | 0 | 0 | 0.12358 | 325.1884 | 0.062355 | 0 | 0 | 0.12471 | 325.3624 | 0.062733 | 0 | 0 | 0.12547 | 325.6235 | 0.063299 | 0 | 0 | 0.1266 | 325.8845 | 0.063865 | 0 | 0 | 0.12773 | 325.9715 | 0.064054 | 0 | 0 | 0.12811 | 326.2326 | 0.06462 | 0 | 0 | 0.12924 | 326.4936 | 0.065186 | 0 | 0 | 0.13037 | 326.6677 | 0.065564 | 0 | 0 | 0.13113 | 326.9287 | 0.06613 | 0 | 0 | 0.13226 | 327.1028 | 0.066508 | 0 | 0 | 0.13302 | 327.2768 | 0.066885 | 0 | 0 | 0.13377
2017-12-28 07:00 | 294.0935 | 0.87657 |  | 308.8172 | 0.026846 | 0 | 0 | 0.053692 | 317.4953 | 0.045669 | 0 | 0 | 0.091338 | 324.5955 | 0.061069 | 0 | 0 | 0.12214 | 324.8585 | 0.06164 | 0 | 0 | 0.12328 | 325.0338 | 0.06202 | 0 | 0 | 0.12404 | 325.2968 | 0.06259 | 0 | 0 | 0.12518 | 325.5598 | 0.063161 | 0 | 0 | 0.12632 | 325.8227 | 0.063731 | 0 | 0 | 0.12746 | 326.1734 | 0.064492 | 0 | 0 | 0.12898 | 326.4363 | 0.065062 | 0 | 0 | 0.13012 | 326.6116 | 0.065442 | 0 | 0 | 0.13088 | 326.8746 | 0.066013 | 0 | 0 | 0.13203 | 327.0499 | 0.066393 | 0 | 0 | 0.13279 | 327.3129 | 0.066963 | 0 | 0 | 0.13393 | 327.5759 | 0.067534 | 0 | 0 | 0.13507 | 327.7512 | 0.067914 | 0 | 0 | 0.13583 | 328.0142 | 0.068484 | 0 | 0 | 0.13697 | 328.2771 | 0.069055 | 0 | 0 | 0.13811 | 328.3648 | 0.069245 | 0 | 0 | 0.13849 | 328.6278 | 0.069815 | 0 | 0 | 0.13963 | 328.8907 | 0.070386 | 0 | 0 | 0.14077 | 329.0661 | 0.070766 | 0 | 0 | 0.14153 | 329.329 | 0.071336 | 0 | 0 | 0.14267 | 329.5043 | 0.071717 | 0 | 0 | 0.14343 | 329.6797 | 0.072097 | 0 | 0 | 0.14419
2017-12-28 08:00 | 285.7957 | 0.85184 |  | 300.1039 | 0.0079471 | 0 | 0 | 0.015894 | 308.5372 | 0.026239 | 0 | 0 | 0.052478 | 315.4371 | 0.041205 | 0 | 0 | 0.082409 | 315.6926 | 0.041759 | 0 | 0 | 0.083518 | 315.863 | 0.042129 | 0 | 0 | 0.084257 | 316.1186 | 0.042683 | 0 | 0 | 0.085366 | 316.3741 | 0.043237 | 0 | 0 | 0.086474 | 316.6297 | 0.043791 | 0 | 0 | 0.087583 | 316.9704 | 0.04453 | 0 | 0 | 0.089061 | 317.226 | 0.045085 | 0 | 0 | 0.09017 | 317.3963 | 0.045454 | 0 | 0 | 0.090909 | 317.6519 | 0.046009 | 0 | 0 | 0.092017 | 317.8223 | 0.046378 | 0 | 0 | 0.092756 | 318.0778 | 0.046932 | 0 | 0 | 0.093865 | 318.3334 | 0.047487 | 0 | 0 | 0.094973 | 318.5037 | 0.047856 | 0 | 0 | 0.095712 | 318.7593 | 0.048411 | 0 | 0 | 0.096821 | 319.0148 | 0.048965 | 0 | 0 | 0.09793 | 319.1 | 0.04915 | 0 | 0 | 0.098299 | 319.3556 | 0.049704 | 0 | 0 | 0.099408 | 319.6111 | 0.050258 | 0 | 0 | 0.10052 | 319.7815 | 0.050628 | 0 | 0 | 0.10126 | 320.037 | 0.051182 | 0 | 0 | 0.10236 | 320.2074 | 0.051552 | 0 | 0 | 0.1031 | 320.3778 | 0.051921 | 0 | 0 | 0.10384
2017-12-28 09:00 | 289.1147 | 0.86173 |  | 303.5891 | 0.015506 | 0 | 0 | 0.031013 | 312.1203 | 0.034011 | 0 | 0 | 0.068021 | 319.1003 | 0.04915 | 0 | 0 | 0.098301 | 319.3589 | 0.049711 | 0 | 0 | 0.099422 | 319.5312 | 0.050085 | 0 | 0 | 0.10017 | 319.7897 | 0.050646 | 0 | 0 | 0.10129 | 320.0483 | 0.051206 | 0 | 0 | 0.10241 | 320.3068 | 0.051767 | 0 | 0 | 0.10353 | 320.6515 | 0.052515 | 0 | 0 | 0.10503 | 320.91 | 0.053075 | 0 | 0 | 0.10615 | 321.0823 | 0.053449 | 0 | 0 | 0.1069 | 321.3409 | 0.05401 | 0 | 0 | 0.10802 | 321.5132 | 0.054384 | 0 | 0 | 0.10877 | 321.7717 | 0.054945 | 0 | 0 | 0.10989 | 322.0302 | 0.055505 | 0 | 0 | 0.11101 | 322.2026 | 0.055879 | 0 | 0 | 0.11176 | 322.4611 | 0.05644 | 0 | 0 | 0.11288 | 322.7196 | 0.057001 | 0 | 0 | 0.114 | 322.8058 | 0.057187 | 0 | 0 | 0.11437 | 323.0643 | 0.057748 | 0 | 0 | 0.1155 | 323.3228 | 0.058309 | 0 | 0 | 0.11662 | 323.4952 | 0.058683 | 0 | 0 | 0.11737 | 323.7537 | 0.059243 | 0 | 0 | 0.11849 | 323.9261 | 0.059617 | 0 | 0 | 0.11923 | 324.0984 | 0.059991 | 0 | 0 | 0.11998
2017-12-28 10:00 | 276.9373 | 0.82544 |  | 290.802 | 0 | 0 | 0 | 0 | 298.9739 | 0.005496 | 0 | 0 | 0.010992 | 305.6599 | 0.019998 | 0 | 0 | 0.039996 | 305.9076 | 0.020535 | 0 | 0 | 0.04107 | 306.0727 | 0.020893 | 0 | 0 | 0.041786 | 306.3203 | 0.02143 | 0 | 0 | 0.042861 | 306.5679 | 0.021967 | 0 | 0 | 0.043935 | 306.8156 | 0.022505 | 0 | 0 | 0.045009 | 307.1457 | 0.023221 | 0 | 0 | 0.046441 | 307.3934 | 0.023758 | 0 | 0 | 0.047516 | 307.5585 | 0.024116 | 0 | 0 | 0.048232 | 307.8061 | 0.024653 | 0 | 0 | 0.049306 | 307.9712 | 0.025011 | 0 | 0 | 0.050022 | 308.2188 | 0.025548 | 0 | 0 | 0.051096 | 308.4664 | 0.026085 | 0 | 0 | 0.052171 | 308.6315 | 0.026443 | 0 | 0 | 0.052887 | 308.8792 | 0.026981 | 0 | 0 | 0.053961 | 309.1268 | 0.027518 | 0 | 0 | 0.055035 | 309.2093 | 0.027697 | 0 | 0 | 0.055393 | 309.457 | 0.028234 | 0 | 0 | 0.056468 | 309.7046 | 0.028771 | 0 | 0 | 0.057542 | 309.8697 | 0.029129 | 0 | 0 | 0.058258 | 310.1173 | 0.029666 | 0 | 0 | 0.059332 | 310.2824 | 0.030024 | 0 | 0 | 0.060048 | 310.4475 | 0.030382 | 0 | 0 | 0.060764
2017-12-28 11:00 | 278.6011 | 0.8304 |  | 292.5492 | 0 | 0 | 0 | 0 | 300.7701 | 0.009392 | 0 | 0 | 0.018784 | 307.4963 | 0.023981 | 0 | 0 | 0.047962 | 307.7454 | 0.024522 | 0 | 0 | 0.049043 | 307.9115 | 0.024882 | 0 | 0 | 0.049763 | 308.1606 | 0.025422 | 0 | 0 | 0.050844 | 308.4098 | 0.025962 | 0 | 0 | 0.051925 | 308.6589 | 0.026503 | 0 | 0 | 0.053005 | 308.991 | 0.027223 | 0 | 0 | 0.054446 | 309.2402 | 0.027764 | 0 | 0 | 0.055527 | 309.4062 | 0.028124 | 0 | 0 | 0.056248 | 309.6554 | 0.028664 | 0 | 0 | 0.057328 | 309.8214 | 0.029024 | 0 | 0 | 0.058049 | 310.0706 | 0.029565 | 0 | 0 | 0.059129 | 310.3197 | 0.030105 | 0 | 0 | 0.06021 | 310.4858 | 0.030465 | 0 | 0 | 0.06093 | 310.7349 | 0.031006 | 0 | 0 | 0.062011 | 310.984 | 0.031546 | 0 | 0 | 0.063092 | 311.067 | 0.031726 | 0 | 0 | 0.063452 | 311.3162 | 0.032266 | 0 | 0 | 0.064533 | 311.5653 | 0.032807 | 0 | 0 | 0.065613 | 311.7314 | 0.033167 | 0 | 0 | 0.066334 | 311.9805 | 0.033707 | 0 | 0 | 0.067415 | 312.1465 | 0.034068 | 0 | 0 | 0.068135 | 312.3126 | 0.034428 | 0 | 0 | 0.068855
2017-12-28 12:00 | 277.0282 | 0.82571 |  | 290.8976 | 0 | 0 | 0 | 0 | 299.0721 | 0.0057091 | 0 | 0 | 0.011418 | 305.7604 | 0.020216 | 0 | 0 | 0.040432 | 306.0081 | 0.020753 | 0 | 0 | 0.041506 | 306.1732 | 0.021111 | 0 | 0 | 0.042223 | 306.4209 | 0.021649 | 0 | 0 | 0.043297 | 306.6686 | 0.022186 | 0 | 0 | 0.044372 | 306.9164 | 0.022723 | 0 | 0 | 0.045446 | 307.2466 | 0.02344 | 0 | 0 | 0.046879 | 307.4944 | 0.023977 | 0 | 0 | 0.047954 | 307.6595 | 0.024335 | 0 | 0 | 0.04867 | 307.9072 | 0.024872 | 0 | 0 | 0.049745 | 308.0724 | 0.025231 | 0 | 0 | 0.050461 | 308.3201 | 0.025768 | 0 | 0 | 0.051536 | 308.5678 | 0.026305 | 0 | 0 | 0.05261 | 308.7329 | 0.026663 | 0 | 0 | 0.053327 | 308.9806 | 0.027201 | 0 | 0 | 0.054401 | 309.2283 | 0.027738 | 0 | 0 | 0.055476 | 309.3109 | 0.027917 | 0 | 0 | 0.055834 | 309.5586 | 0.028454 | 0 | 0 | 0.056909 | 309.8063 | 0.028992 | 0 | 0 | 0.057983 | 309.9715 | 0.02935 | 0 | 0 | 0.0587 | 310.2192 | 0.029887 | 0 | 0 | 0.059774 | 310.3843 | 0.030245 | 0 | 0 | 0.060491 | 310.5495 | 0.030603 | 0 | 0 | 0.061207
2017-12-28 13:00 | 284.019 | 0.84655 |  | 298.2383 | 0.0039006 | 0 | 0 | 0.0078011 | 306.6191 | 0.022079 | 0 | 0 | 0.044157 | 313.4762 | 0.036951 | 0 | 0 | 0.073903 | 313.7301 | 0.037502 | 0 | 0 | 0.075005 | 313.8994 | 0.03787 | 0 | 0 | 0.075739 | 314.1534 | 0.03842 | 0 | 0 | 0.076841 | 314.4074 | 0.038971 | 0 | 0 | 0.077942 | 314.6613 | 0.039522 | 0 | 0 | 0.079044 | 314.9999 | 0.040257 | 0 | 0 | 0.080513 | 315.2539 | 0.040807 | 0 | 0 | 0.081615 | 315.4232 | 0.041175 | 0 | 0 | 0.082349 | 315.6772 | 0.041725 | 0 | 0 | 0.083451 | 315.8465 | 0.042093 | 0 | 0 | 0.084185 | 316.1005 | 0.042644 | 0 | 0 | 0.085287 | 316.3544 | 0.043194 | 0 | 0 | 0.086389 | 316.5237 | 0.043562 | 0 | 0 | 0.087123 | 316.7777 | 0.044112 | 0 | 0 | 0.088225 | 317.0317 | 0.044663 | 0 | 0 | 0.089327 | 317.1163 | 0.044847 | 0 | 0 | 0.089694 | 317.3703 | 0.045398 | 0 | 0 | 0.090796 | 317.6242 | 0.045949 | 0 | 0 | 0.091897 | 317.7935 | 0.046316 | 0 | 0 | 0.092632 | 318.0475 | 0.046867 | 0 | 0 | 0.093733 | 318.2168 | 0.047234 | 0 | 0 | 0.094468 | 318.3861 | 0.047601 | 0 | 0 | 0.095202
2017-12-28 14:00 | 279.9487 | 0.83441 |  | 293.9642 | 0 | 0 | 0 | 0 | 302.2249 | 0.012548 | 0 | 0 | 0.025095 | 308.9837 | 0.027207 | 0 | 0 | 0.054414 | 309.234 | 0.02775 | 0 | 0 | 0.0555 | 309.4009 | 0.028112 | 0 | 0 | 0.056224 | 309.6512 | 0.028655 | 0 | 0 | 0.05731 | 309.9015 | 0.029198 | 0 | 0 | 0.058396 | 310.1519 | 0.029741 | 0 | 0 | 0.059482 | 310.4856 | 0.030465 | 0 | 0 | 0.06093 | 310.736 | 0.031008 | 0 | 0 | 0.062016 | 310.9028 | 0.03137 | 0 | 0 | 0.06274 | 311.1532 | 0.031913 | 0 | 0 | 0.063826 | 311.32 | 0.032275 | 0 | 0 | 0.06455 | 311.5704 | 0.032818 | 0 | 0 | 0.065636 | 311.8207 | 0.033361 | 0 | 0 | 0.066721 | 311.9876 | 0.033723 | 0 | 0 | 0.067445 | 312.2379 | 0.034266 | 0 | 0 | 0.068531 | 312.4882 | 0.034809 | 0 | 0 | 0.069617 | 312.5717 | 0.03499 | 0 | 0 | 0.069979 | 312.822 | 0.035533 | 0 | 0 | 0.071065 | 313.0723 | 0.036075 | 0 | 0 | 0.072151 | 313.2392 | 0.036437 | 0 | 0 | 0.072875 | 313.4895 | 0.03698 | 0 | 0 | 0.073961 | 313.6564 | 0.037342 | 0 | 0 | 0.074685 | 313.8233 | 0.037704 | 0 | 0 | 0.075409
2017-12-28 15:00 | 278.3304 | 0.82959 |  | 292.2649 | 0 | 0 | 0 | 0 | 300.4778 | 0.0087581 | 0 | 0 | 0.017516 | 307.1975 | 0.023333 | 0 | 0 | 0.046666 | 307.4464 | 0.023873 | 0 | 0 | 0.047746 | 307.6123 | 0.024233 | 0 | 0 | 0.048466 | 307.8612 | 0.024773 | 0 | 0 | 0.049545 | 308.1101 | 0.025312 | 0 | 0 | 0.050625 | 308.3589 | 0.025852 | 0 | 0 | 0.051704 | 308.6908 | 0.026572 | 0 | 0 | 0.053144 | 308.9397 | 0.027112 | 0 | 0 | 0.054224 | 309.1056 | 0.027472 | 0 | 0 | 0.054943 | 309.3545 | 0.028011 | 0 | 0 | 0.056023 | 309.5204 | 0.028371 | 0 | 0 | 0.056743 | 309.7693 | 0.028911 | 0 | 0 | 0.057822 | 310.0181 | 0.029451 | 0 | 0 | 0.058902 | 310.184 | 0.029811 | 0 | 0 | 0.059622 | 310.4329 | 0.030351 | 0 | 0 | 0.060701 | 310.6818 | 0.03089 | 0 | 0 | 0.061781 | 310.7648 | 0.03107 | 0 | 0 | 0.062141 | 311.0136 | 0.03161 | 0 | 0 | 0.06322 | 311.2625 | 0.03215 | 0 | 0 | 0.0643 | 311.4284 | 0.03251 | 0 | 0 | 0.06502 | 311.6773 | 0.03305 | 0 | 0 | 0.066099 | 311.8432 | 0.03341 | 0 | 0 | 0.066819 | 312.0091 | 0.033769 | 0 | 0 | 0.067539
2017-12-28 16:00 | 291.6224 | 0.86921 |  | 306.2224 | 0.021218 | 0 | 0 | 0.042436 | 314.8276 | 0.039883 | 0 | 0 | 0.079765 | 321.8682 | 0.055154 | 0 | 0 | 0.11031 | 322.1289 | 0.055719 | 0 | 0 | 0.11144 | 322.3028 | 0.056096 | 0 | 0 | 0.11219 | 322.5635 | 0.056662 | 0 | 0 | 0.11332 | 322.8243 | 0.057228 | 0 | 0 | 0.11446 | 323.0851 | 0.057793 | 0 | 0 | 0.11559 | 323.4328 | 0.058547 | 0 | 0 | 0.11709 | 323.6935 | 0.059113 | 0 | 0 | 0.11823 | 323.8674 | 0.05949 | 0 | 0 | 0.11898 | 324.1281 | 0.060056 | 0 | 0 | 0.12011 | 324.302 | 0.060433 | 0 | 0 | 0.12087 | 324.5627 | 0.060998 | 0 | 0 | 0.122 | 324.8235 | 0.061564 | 0 | 0 | 0.12313 | 324.9973 | 0.061941 | 0 | 0 | 0.12388 | 325.2581 | 0.062506 | 0 | 0 | 0.12501 | 325.5189 | 0.063072 | 0 | 0 | 0.12614 | 325.6058 | 0.063261 | 0 | 0 | 0.12652 | 325.8665 | 0.063826 | 0 | 0 | 0.12765 | 326.1273 | 0.064392 | 0 | 0 | 0.12878 | 326.3011 | 0.064769 | 0 | 0 | 0.12954 | 326.5619 | 0.065334 | 0 | 0 | 0.13067 | 326.7357 | 0.065711 | 0 | 0 | 0.13142 | 326.9096 | 0.066089 | 0 | 0 | 0.13218
2017-12-28 17:00 | 292.7192 | 0.87248 |  | 307.3741 | 0.023716 | 0 | 0 | 0.047432 | 316.0117 | 0.042451 | 0 | 0 | 0.084902 | 323.0787 | 0.057779 | 0 | 0 | 0.11556 | 323.3405 | 0.058347 | 0 | 0 | 0.11669 | 323.515 | 0.058726 | 0 | 0 | 0.11745 | 323.7767 | 0.059293 | 0 | 0 | 0.11859 | 324.0385 | 0.059861 | 0 | 0 | 0.11972 | 324.3002 | 0.060429 | 0 | 0 | 0.12086 | 324.6492 | 0.061186 | 0 | 0 | 0.12237 | 324.9109 | 0.061753 | 0 | 0 | 0.12351 | 325.0854 | 0.062132 | 0 | 0 | 0.12426 | 325.3472 | 0.0627 | 0 | 0 | 0.1254 | 325.5217 | 0.063078 | 0 | 0 | 0.12616 | 325.7834 | 0.063646 | 0 | 0 | 0.12729 | 326.0452 | 0.064214 | 0 | 0 | 0.12843 | 326.2197 | 0.064592 | 0 | 0 | 0.12918 | 326.4814 | 0.06516 | 0 | 0 | 0.13032 | 326.7431 | 0.065728 | 0 | 0 | 0.13146 | 326.8304 | 0.065917 | 0 | 0 | 0.13183 | 327.0921 | 0.066484 | 0 | 0 | 0.13297 | 327.3539 | 0.067052 | 0 | 0 | 0.1341 | 327.5284 | 0.067431 | 0 | 0 | 0.13486 | 327.7901 | 0.067998 | 0 | 0 | 0.136 | 327.9646 | 0.068377 | 0 | 0 | 0.13675 | 328.1391 | 0.068755 | 0 | 0 | 0.13751
2017-12-28 18:00 | 296.2417 | 0.88298 |  | 311.073 | 0.031739 | 0 | 0 | 0.063478 | 319.8145 | 0.050699 | 0 | 0 | 0.1014 | 326.9666 | 0.066212 | 0 | 0 | 0.13242 | 327.2315 | 0.066787 | 0 | 0 | 0.13357 | 327.4081 | 0.06717 | 0 | 0 | 0.13434 | 327.673 | 0.067744 | 0 | 0 | 0.13549 | 327.9379 | 0.068319 | 0 | 0 | 0.13664 | 328.2027 | 0.068893 | 0 | 0 | 0.13779 | 328.5559 | 0.069659 | 0 | 0 | 0.13932 | 328.8208 | 0.070234 | 0 | 0 | 0.14047 | 328.9974 | 0.070617 | 0 | 0 | 0.14123 | 329.2623 | 0.071192 | 0 | 0 | 0.14238 | 329.4389 | 0.071575 | 0 | 0 | 0.14315 | 329.7038 | 0.072149 | 0 | 0 | 0.1443 | 329.9687 | 0.072724 | 0 | 0 | 0.14545 | 330.1453 | 0.073107 | 0 | 0 | 0.14621 | 330.4102 | 0.073681 | 0 | 0 | 0.14736 | 330.6751 | 0.074256 | 0 | 0 | 0.14851 | 330.7634 | 0.074447 | 0 | 0 | 0.14889 | 331.0283 | 0.075022 | 0 | 0 | 0.15004 | 331.2932 | 0.075597 | 0 | 0 | 0.15119 | 331.4698 | 0.07598 | 0 | 0 | 0.15196 | 331.7347 | 0.076554 | 0 | 0 | 0.15311 | 331.9113 | 0.076937 | 0 | 0 | 0.15387 | 332.0878 | 0.07732 | 0 | 0 | 0.15464
2017-12-28 19:00 | 303.2766 | 0.90395 |  | 318.46 | 0.047761 | 0 | 0 | 0.095523 | 327.4091 | 0.067172 | 0 | 0 | 0.13434 | 334.731 | 0.083053 | 0 | 0 | 0.16611 | 335.0022 | 0.083641 | 0 | 0 | 0.16728 | 335.183 | 0.084034 | 0 | 0 | 0.16807 | 335.4542 | 0.084622 | 0 | 0 | 0.16924 | 335.7254 | 0.08521 | 0 | 0 | 0.17042 | 335.9966 | 0.085798 | 0 | 0 | 0.1716 | 336.3581 | 0.086582 | 0 | 0 | 0.17316 | 336.6293 | 0.087171 | 0 | 0 | 0.17434 | 336.8101 | 0.087563 | 0 | 0 | 0.17513 | 337.0813 | 0.088151 | 0 | 0 | 0.1763 | 337.2621 | 0.088543 | 0 | 0 | 0.17709 | 337.5333 | 0.089131 | 0 | 0 | 0.17826 | 337.8045 | 0.089719 | 0 | 0 | 0.17944 | 337.9852 | 0.090112 | 0 | 0 | 0.18022 | 338.2564 | 0.0907 | 0 | 0 | 0.1814 | 338.5276 | 0.091288 | 0 | 0 | 0.18258 | 338.618 | 0.091484 | 0 | 0 | 0.18297 | 338.8892 | 0.092072 | 0 | 0 | 0.18414 | 339.1604 | 0.09266 | 0 | 0 | 0.18532 | 339.3412 | 0.093053 | 0 | 0 | 0.18611 | 339.6123 | 0.093641 | 0 | 0 | 0.18728 | 339.7931 | 0.094033 | 0 | 0 | 0.18807 | 339.9739 | 0.094425 | 0 | 0 | 0.18885
2017-12-28 20:00 | 303.9418 | 0.90593 |  | 319.1586 | 0.049277 | 0 | 0 | 0.098553 | 328.1272 | 0.06873 | 0 | 0 | 0.13746 | 335.4653 | 0.084646 | 0 | 0 | 0.16929 | 335.737 | 0.085235 | 0 | 0 | 0.17047 | 335.9182 | 0.085628 | 0 | 0 | 0.17126 | 336.19 | 0.086218 | 0 | 0 | 0.17244 | 336.4618 | 0.086807 | 0 | 0 | 0.17361 | 336.7336 | 0.087397 | 0 | 0 | 0.17479 | 337.0959 | 0.088183 | 0 | 0 | 0.17637 | 337.3677 | 0.088772 | 0 | 0 | 0.17754 | 337.5489 | 0.089165 | 0 | 0 | 0.17833 | 337.8207 | 0.089755 | 0 | 0 | 0.17951 | 338.0019 | 0.090148 | 0 | 0 | 0.1803 | 338.2736 | 0.090737 | 0 | 0 | 0.18147 | 338.5454 | 0.091327 | 0 | 0 | 0.18265 | 338.7266 | 0.09172 | 0 | 0 | 0.18344 | 338.9984 | 0.092309 | 0 | 0 | 0.18462 | 339.2702 | 0.092899 | 0 | 0 | 0.1858 | 339.3608 | 0.093095 | 0 | 0 | 0.18619 | 339.6325 | 0.093685 | 0 | 0 | 0.18737 | 339.9043 | 0.094274 | 0 | 0 | 0.18855 | 340.0855 | 0.094667 | 0 | 0 | 0.18933 | 340.3573 | 0.095257 | 0 | 0 | 0.19051 | 340.5385 | 0.09565 | 0 | 0 | 0.1913 | 340.7196 | 0.096043 | 0 | 0 | 0.19209
2017-12-28 21:00 | 310.113 | 0.92432 |  | 325.6387 | 0.063332 | 0 | 0 | 0.12666 | 334.7895 | 0.08318 | 0 | 0 | 0.16636 | 342.2766 | 0.099419 | 0 | 0 | 0.19884 | 342.5538 | 0.10002 | 0 | 0 | 0.20004 | 342.7387 | 0.10042 | 0 | 0 | 0.20084 | 343.016 | 0.10102 | 0 | 0 | 0.20205 | 343.2933 | 0.10162 | 0 | 0 | 0.20325 | 343.5706 | 0.10223 | 0 | 0 | 0.20445 | 343.9403 | 0.10303 | 0 | 0 | 0.20606 | 344.2176 | 0.10363 | 0 | 0 | 0.20726 | 344.4025 | 0.10403 | 0 | 0 | 0.20806 | 344.6798 | 0.10463 | 0 | 0 | 0.20926 | 344.8647 | 0.10503 | 0 | 0 | 0.21007 | 345.1419 | 0.10563 | 0 | 0 | 0.21127 | 345.4192 | 0.10624 | 0 | 0 | 0.21247 | 345.6041 | 0.10664 | 0 | 0 | 0.21327 | 345.8814 | 0.10724 | 0 | 0 | 0.21448 | 346.1587 | 0.10784 | 0 | 0 | 0.21568 | 346.2511 | 0.10804 | 0 | 0 | 0.21608 | 346.5284 | 0.10864 | 0 | 0 | 0.21728 | 346.8057 | 0.10924 | 0 | 0 | 0.21849 | 346.9906 | 0.10964 | 0 | 0 | 0.21929 | 347.2679 | 0.11025 | 0 | 0 | 0.22049 | 347.4528 | 0.11065 | 0 | 0 | 0.22129 | 347.6376 | 0.11105 | 0 | 0 | 0.2221
2017-12-28 22:00 | 311.2828 | 0.92781 |  | 326.867 | 0.065996 | 0 | 0 | 0.13199 | 336.0523 | 0.085919 | 0 | 0 | 0.17184 | 343.5676 | 0.10222 | 0 | 0 | 0.20444 | 343.8459 | 0.10282 | 0 | 0 | 0.20565 | 344.0315 | 0.10323 | 0 | 0 | 0.20645 | 344.3098 | 0.10383 | 0 | 0 | 0.20766 | 344.5882 | 0.10443 | 0 | 0 | 0.20887 | 344.8665 | 0.10504 | 0 | 0 | 0.21007 | 345.2377 | 0.10584 | 0 | 0 | 0.21168 | 345.516 | 0.10645 | 0 | 0 | 0.21289 | 345.7016 | 0.10685 | 0 | 0 | 0.2137 | 345.9799 | 0.10745 | 0 | 0 | 0.2149 | 346.1655 | 0.10785 | 0 | 0 | 0.21571 | 346.4438 | 0.10846 | 0 | 0 | 0.21692 | 346.7222 | 0.10906 | 0 | 0 | 0.21812 | 346.9077 | 0.10946 | 0 | 0 | 0.21893 | 347.1861 | 0.11007 | 0 | 0 | 0.22014 | 347.4644 | 0.11067 | 0 | 0 | 0.22134 | 347.5572 | 0.11087 | 0 | 0 | 0.22175 | 347.8355 | 0.11148 | 0 | 0 | 0.22295 | 348.1139 | 0.11208 | 0 | 0 | 0.22416 | 348.2994 | 0.11248 | 0 | 0 | 0.22497 | 348.5778 | 0.11309 | 0 | 0 | 0.22617 | 348.7633 | 0.11349 | 0 | 0 | 0.22698 | 348.9489 | 0.11389 | 0 | 0 | 0.22778
2017-12-28 23:00 | 308.5664 | 0.91971 |  | 324.0147 | 0.059809 | 0 | 0 | 0.11962 | 333.1198 | 0.079559 | 0 | 0 | 0.15912 | 340.5695 | 0.095717 | 0 | 0 | 0.19143 | 340.8454 | 0.096315 | 0 | 0 | 0.19263 | 341.0293 | 0.096714 | 0 | 0 | 0.19343 | 341.3053 | 0.097313 | 0 | 0 | 0.19463 | 341.5812 | 0.097911 | 0 | 0 | 0.19582 | 341.8571 | 0.09851 | 0 | 0 | 0.19702 | 342.225 | 0.099308 | 0 | 0 | 0.19862 | 342.5009 | 0.099906 | 0 | 0 | 0.19981 | 342.6848 | 0.10031 | 0 | 0 | 0.20061 | 342.9607 | 0.1009 | 0 | 0 | 0.20181 | 343.1447 | 0.1013 | 0 | 0 | 0.2026 | 343.4206 | 0.1019 | 0 | 0 | 0.2038 | 343.6965 | 0.1025 | 0 | 0 | 0.205 | 343.8804 | 0.1029 | 0 | 0 | 0.2058 | 344.1564 | 0.1035 | 0 | 0 | 0.20699 | 344.4323 | 0.1041 | 0 | 0 | 0.20819 | 344.5242 | 0.10429 | 0 | 0 | 0.20859 | 344.8002 | 0.10489 | 0 | 0 | 0.20979 | 345.0761 | 0.10549 | 0 | 0 | 0.21098 | 345.26 | 0.10589 | 0 | 0 | 0.21178 | 345.5359 | 0.10649 | 0 | 0 | 0.21298 | 345.7199 | 0.10689 | 0 | 0 | 0.21378 | 345.9038 | 0.10729 | 0 | 0 | 0.21457
2017-12-29 | 304.348 | 0.90714 |  | 319.5851 | 0.050202 | 0 | 0 | 0.1004 | 328.5657 | 0.069681 | 0 | 0 | 0.13936 | 335.9136 | 0.085618 | 0 | 0 | 0.17124 | 336.1857 | 0.086208 | 0 | 0 | 0.17242 | 336.3671 | 0.086602 | 0 | 0 | 0.1732 | 336.6393 | 0.087192 | 0 | 0 | 0.17438 | 336.9114 | 0.087782 | 0 | 0 | 0.17556 | 337.1836 | 0.088373 | 0 | 0 | 0.17675 | 337.5464 | 0.08916 | 0 | 0 | 0.17832 | 337.8186 | 0.08975 | 0 | 0 | 0.1795 | 338 | 0.090144 | 0 | 0 | 0.18029 | 338.2721 | 0.090734 | 0 | 0 | 0.18147 | 338.4535 | 0.091127 | 0 | 0 | 0.18225 | 338.7257 | 0.091718 | 0 | 0 | 0.18344 | 338.9978 | 0.092308 | 0 | 0 | 0.18462 | 339.1793 | 0.092701 | 0 | 0 | 0.1854 | 339.4514 | 0.093292 | 0 | 0 | 0.18658 | 339.7235 | 0.093882 | 0 | 0 | 0.18776 | 339.8143 | 0.094079 | 0 | 0 | 0.18816 | 340.0864 | 0.094669 | 0 | 0 | 0.18934 | 340.3585 | 0.095259 | 0 | 0 | 0.19052 | 340.54 | 0.095653 | 0 | 0 | 0.19131 | 340.8121 | 0.096243 | 0 | 0 | 0.19249 | 340.9935 | 0.096637 | 0 | 0 | 0.19327 | 341.175 | 0.09703 | 0 | 0 | 0.19406
2017-12-29 01:00 | 302.1993 | 0.90073 |  | 317.3288 | 0.045308 | 0 | 0 | 0.090616 | 326.2461 | 0.064649 | 0 | 0 | 0.1293 | 333.542 | 0.080474 | 0 | 0 | 0.16095 | 333.8123 | 0.08106 | 0 | 0 | 0.16212 | 333.9924 | 0.081451 | 0 | 0 | 0.1629 | 334.2626 | 0.082037 | 0 | 0 | 0.16407 | 334.5328 | 0.082623 | 0 | 0 | 0.16525 | 334.8031 | 0.083209 | 0 | 0 | 0.16642 | 335.1634 | 0.083991 | 0 | 0 | 0.16798 | 335.4336 | 0.084577 | 0 | 0 | 0.16915 | 335.6137 | 0.084968 | 0 | 0 | 0.16994 | 335.8839 | 0.085554 | 0 | 0 | 0.17111 | 336.0641 | 0.085945 | 0 | 0 | 0.17189 | 336.3343 | 0.086531 | 0 | 0 | 0.17306 | 336.6045 | 0.087117 | 0 | 0 | 0.17423 | 336.7847 | 0.087508 | 0 | 0 | 0.17502 | 337.0549 | 0.088094 | 0 | 0 | 0.17619 | 337.3251 | 0.08868 | 0 | 0 | 0.17736 | 337.4152 | 0.088875 | 0 | 0 | 0.17775 | 337.6854 | 0.089461 | 0 | 0 | 0.17892 | 337.9556 | 0.090047 | 0 | 0 | 0.18009 | 338.1358 | 0.090438 | 0 | 0 | 0.18088 | 338.406 | 0.091024 | 0 | 0 | 0.18205 | 338.5862 | 0.091415 | 0 | 0 | 0.18283 | 338.7663 | 0.091806 | 0 | 0 | 0.18361
2017-12-29 02:00 | 300.7193 | 0.89632 |  | 315.7747 | 0.041937 | 0 | 0 | 0.083874 | 324.6483 | 0.061184 | 0 | 0 | 0.12237 | 331.9085 | 0.076931 | 0 | 0 | 0.15386 | 332.1774 | 0.077515 | 0 | 0 | 0.15503 | 332.3567 | 0.077903 | 0 | 0 | 0.15581 | 332.6256 | 0.078487 | 0 | 0 | 0.15697 | 332.8945 | 0.07907 | 0 | 0 | 0.15814 | 333.1634 | 0.079653 | 0 | 0 | 0.15931 | 333.5219 | 0.080431 | 0 | 0 | 0.16086 | 333.7908 | 0.081014 | 0 | 0 | 0.16203 | 333.9701 | 0.081403 | 0 | 0 | 0.16281 | 334.239 | 0.081986 | 0 | 0 | 0.16397 | 334.4183 | 0.082375 | 0 | 0 | 0.16475 | 334.6872 | 0.082958 | 0 | 0 | 0.16592 | 334.956 | 0.083541 | 0 | 0 | 0.16708 | 335.1353 | 0.08393 | 0 | 0 | 0.16786 | 335.4042 | 0.084513 | 0 | 0 | 0.16903 | 335.6731 | 0.085097 | 0 | 0 | 0.17019 | 335.7627 | 0.085291 | 0 | 0 | 0.17058 | 336.0316 | 0.085874 | 0 | 0 | 0.17175 | 336.3005 | 0.086457 | 0 | 0 | 0.17291 | 336.4798 | 0.086846 | 0 | 0 | 0.17369 | 336.7487 | 0.08743 | 0 | 0 | 0.17486 | 336.928 | 0.087818 | 0 | 0 | 0.17564 | 337.1072 | 0.088207 | 0 | 0 | 0.17641
2017-12-29 03:00 | 295.7865 | 0.88162 |  | 310.595 | 0.030702 | 0 | 0 | 0.061404 | 319.3231 | 0.049633 | 0 | 0 | 0.099267 | 326.4642 | 0.065122 | 0 | 0 | 0.13024 | 326.7287 | 0.065696 | 0 | 0 | 0.13139 | 326.905 | 0.066079 | 0 | 0 | 0.13216 | 327.1695 | 0.066652 | 0 | 0 | 0.1333 | 327.434 | 0.067226 | 0 | 0 | 0.13445 | 327.6985 | 0.0678 | 0 | 0 | 0.1356 | 328.0511 | 0.068564 | 0 | 0 | 0.13713 | 328.3156 | 0.069138 | 0 | 0 | 0.13828 | 328.4919 | 0.069521 | 0 | 0 | 0.13904 | 328.7564 | 0.070094 | 0 | 0 | 0.14019 | 328.9327 | 0.070477 | 0 | 0 | 0.14095 | 329.1972 | 0.07105 | 0 | 0 | 0.1421 | 329.4617 | 0.071624 | 0 | 0 | 0.14325 | 329.638 | 0.072007 | 0 | 0 | 0.14401 | 329.9025 | 0.07258 | 0 | 0 | 0.14516 | 330.167 | 0.073154 | 0 | 0 | 0.14631 | 330.2552 | 0.073345 | 0 | 0 | 0.14669 | 330.5196 | 0.073919 | 0 | 0 | 0.14784 | 330.7841 | 0.074492 | 0 | 0 | 0.14898 | 330.9604 | 0.074875 | 0 | 0 | 0.14975 | 331.2249 | 0.075449 | 0 | 0 | 0.1509 | 331.4013 | 0.075831 | 0 | 0 | 0.15166 | 331.5776 | 0.076213 | 0 | 0 | 0.15243
2017-12-29 04:00 | 304.7159 | 0.90824 |  | 319.9714 | 0.05104 | 0 | 0 | 0.10208 | 328.9629 | 0.070542 | 0 | 0 | 0.14108 | 336.3196 | 0.086499 | 0 | 0 | 0.173 | 336.5921 | 0.08709 | 0 | 0 | 0.17418 | 336.7737 | 0.087484 | 0 | 0 | 0.17497 | 337.0462 | 0.088075 | 0 | 0 | 0.17615 | 337.3187 | 0.088666 | 0 | 0 | 0.17733 | 337.5911 | 0.089257 | 0 | 0 | 0.17851 | 337.9544 | 0.090045 | 0 | 0 | 0.18009 | 338.2269 | 0.090636 | 0 | 0 | 0.18127 | 338.4086 | 0.09103 | 0 | 0 | 0.18206 | 338.681 | 0.091621 | 0 | 0 | 0.18324 | 338.8627 | 0.092015 | 0 | 0 | 0.18403 | 339.1351 | 0.092606 | 0 | 0 | 0.18521 | 339.4076 | 0.093197 | 0 | 0 | 0.18639 | 339.5893 | 0.093591 | 0 | 0 | 0.18718 | 339.8617 | 0.094182 | 0 | 0 | 0.18836 | 340.1342 | 0.094773 | 0 | 0 | 0.18955 | 340.225 | 0.09497 | 0 | 0 | 0.18994 | 340.4975 | 0.095561 | 0 | 0 | 0.19112 | 340.77 | 0.096152 | 0 | 0 | 0.1923 | 340.9516 | 0.096546 | 0 | 0 | 0.19309 | 341.2241 | 0.097137 | 0 | 0 | 0.19427 | 341.4057 | 0.097531 | 0 | 0 | 0.19506 | 341.5874 | 0.097925 | 0 | 0 | 0.19585
2017-12-29 05:00 | 305.3031 | 0.90999 |  | 320.588 | 0.052377 | 0 | 0 | 0.10475 | 329.5968 | 0.071917 | 0 | 0 | 0.14383 | 336.9677 | 0.087905 | 0 | 0 | 0.17581 | 337.2407 | 0.088497 | 0 | 0 | 0.17699 | 337.4227 | 0.088892 | 0 | 0 | 0.17778 | 337.6957 | 0.089484 | 0 | 0 | 0.17897 | 337.9687 | 0.090076 | 0 | 0 | 0.18015 | 338.2417 | 0.090668 | 0 | 0 | 0.18134 | 338.6057 | 0.091457 | 0 | 0 | 0.18291 | 338.8787 | 0.09205 | 0 | 0 | 0.1841 | 339.0607 | 0.092444 | 0 | 0 | 0.18489 | 339.3337 | 0.093036 | 0 | 0 | 0.18607 | 339.5157 | 0.093431 | 0 | 0 | 0.18686 | 339.7887 | 0.094023 | 0 | 0 | 0.18805 | 340.0617 | 0.094615 | 0 | 0 | 0.18923 | 340.2437 | 0.09501 | 0 | 0 | 0.19002 | 340.5167 | 0.095602 | 0 | 0 | 0.1912 | 340.7897 | 0.096194 | 0 | 0 | 0.19239 | 340.8807 | 0.096392 | 0 | 0 | 0.19278 | 341.1537 | 0.096984 | 0 | 0 | 0.19397 | 341.4267 | 0.097576 | 0 | 0 | 0.19515 | 341.6087 | 0.097971 | 0 | 0 | 0.19594 | 341.8817 | 0.098563 | 0 | 0 | 0.19713 | 342.0637 | 0.098958 | 0 | 0 | 0.19792 | 342.2456 | 0.099352 | 0 | 0 | 0.1987
2017-12-29 06:00 | 306.3593 | 0.91313 |  | 321.6971 | 0.054783 | 0 | 0 | 0.10957 | 330.7371 | 0.07439 | 0 | 0 | 0.14878 | 338.1335 | 0.090433 | 0 | 0 | 0.18087 | 338.4074 | 0.091027 | 0 | 0 | 0.18205 | 338.5901 | 0.091423 | 0 | 0 | 0.18285 | 338.864 | 0.092018 | 0 | 0 | 0.18404 | 339.1379 | 0.092612 | 0 | 0 | 0.18522 | 339.4119 | 0.093206 | 0 | 0 | 0.18641 | 339.7771 | 0.093998 | 0 | 0 | 0.188 | 340.0511 | 0.094592 | 0 | 0 | 0.18918 | 340.2337 | 0.094989 | 0 | 0 | 0.18998 | 340.5076 | 0.095583 | 0 | 0 | 0.19117 | 340.6903 | 0.095979 | 0 | 0 | 0.19196 | 340.9642 | 0.096573 | 0 | 0 | 0.19315 | 341.2382 | 0.097167 | 0 | 0 | 0.19433 | 341.4208 | 0.097563 | 0 | 0 | 0.19513 | 341.6947 | 0.098157 | 0 | 0 | 0.19631 | 341.9687 | 0.098752 | 0 | 0 | 0.1975 | 342.06 | 0.09895 | 0 | 0 | 0.1979 | 342.3339 | 0.099544 | 0 | 0 | 0.19909 | 342.6079 | 0.10014 | 0 | 0 | 0.20028 | 342.7905 | 0.10053 | 0 | 0 | 0.20107 | 343.0644 | 0.10113 | 0 | 0 | 0.20226 | 343.247 | 0.10152 | 0 | 0 | 0.20305 | 343.4297 | 0.10192 | 0 | 0 | 0.20384
2017-12-29 07:00 | 303.0166 | 0.90317 |  | 318.1871 | 0.047169 | 0 | 0 | 0.094339 | 327.1284 | 0.066563 | 0 | 0 | 0.13313 | 334.4441 | 0.082431 | 0 | 0 | 0.16486 | 334.7151 | 0.083019 | 0 | 0 | 0.16604 | 334.8957 | 0.08341 | 0 | 0 | 0.16682 | 335.1667 | 0.083998 | 0 | 0 | 0.168 | 335.4376 | 0.084586 | 0 | 0 | 0.16917 | 335.7086 | 0.085174 | 0 | 0 | 0.17035 | 336.0698 | 0.085957 | 0 | 0 | 0.17191 | 336.3408 | 0.086545 | 0 | 0 | 0.17309 | 336.5214 | 0.086937 | 0 | 0 | 0.17387 | 336.7924 | 0.087524 | 0 | 0 | 0.17505 | 336.973 | 0.087916 | 0 | 0 | 0.17583 | 337.244 | 0.088504 | 0 | 0 | 0.17701 | 337.5149 | 0.089091 | 0 | 0 | 0.17818 | 337.6955 | 0.089483 | 0 | 0 | 0.17897 | 337.9665 | 0.090071 | 0 | 0 | 0.18014 | 338.2374 | 0.090659 | 0 | 0 | 0.18132 | 338.3278 | 0.090855 | 0 | 0 | 0.18171 | 338.5987 | 0.091442 | 0 | 0 | 0.18288 | 338.8697 | 0.09203 | 0 | 0 | 0.18406 | 339.0503 | 0.092422 | 0 | 0 | 0.18484 | 339.3213 | 0.093009 | 0 | 0 | 0.18602 | 339.5019 | 0.093401 | 0 | 0 | 0.1868 | 339.6825 | 0.093793 | 0 | 0 | 0.18759
2017-12-29 08:00 | 303.6782 | 0.90514 |  | 318.8818 | 0.048676 | 0 | 0 | 0.097352 | 327.8427 | 0.068112 | 0 | 0 | 0.13622 | 335.1744 | 0.084015 | 0 | 0 | 0.16803 | 335.4459 | 0.084604 | 0 | 0 | 0.16921 | 335.6269 | 0.084996 | 0 | 0 | 0.16999 | 335.8985 | 0.085585 | 0 | 0 | 0.17117 | 336.17 | 0.086174 | 0 | 0 | 0.17235 | 336.4416 | 0.086763 | 0 | 0 | 0.17353 | 336.8036 | 0.087549 | 0 | 0 | 0.1751 | 337.0752 | 0.088138 | 0 | 0 | 0.17628 | 337.2562 | 0.08853 | 0 | 0 | 0.17706 | 337.5277 | 0.089119 | 0 | 0 | 0.17824 | 337.7088 | 0.089512 | 0 | 0 | 0.17902 | 337.9803 | 0.090101 | 0 | 0 | 0.1802 | 338.2518 | 0.09069 | 0 | 0 | 0.18138 | 338.4329 | 0.091083 | 0 | 0 | 0.18217 | 338.7044 | 0.091672 | 0 | 0 | 0.18334 | 338.976 | 0.09226 | 0 | 0 | 0.18452 | 339.0665 | 0.092457 | 0 | 0 | 0.18491 | 339.338 | 0.093046 | 0 | 0 | 0.18609 | 339.6096 | 0.093635 | 0 | 0 | 0.18727 | 339.7906 | 0.094027 | 0 | 0 | 0.18805 | 340.0621 | 0.094616 | 0 | 0 | 0.18923 | 340.2432 | 0.095009 | 0 | 0 | 0.19002 | 340.4242 | 0.095402 | 0 | 0 | 0.1908
2017-12-29 09:00 | 308.2324 | 0.91872 |  | 323.664 | 0.059049 | 0 | 0 | 0.1181 | 332.7593 | 0.078777 | 0 | 0 | 0.15755 | 340.2009 | 0.094917 | 0 | 0 | 0.18983 | 340.4765 | 0.095515 | 0 | 0 | 0.19103 | 340.6602 | 0.095914 | 0 | 0 | 0.19183 | 340.9359 | 0.096512 | 0 | 0 | 0.19302 | 341.2115 | 0.097109 | 0 | 0 | 0.19422 | 341.4871 | 0.097707 | 0 | 0 | 0.19541 | 341.8546 | 0.098504 | 0 | 0 | 0.19701 | 342.1302 | 0.099102 | 0 | 0 | 0.1982 | 342.3139 | 0.099501 | 0 | 0 | 0.199 | 342.5896 | 0.1001 | 0 | 0 | 0.2002 | 342.7733 | 0.1005 | 0 | 0 | 0.20099 | 343.0489 | 0.10109 | 0 | 0 | 0.20219 | 343.3245 | 0.10169 | 0 | 0 | 0.20339 | 343.5083 | 0.10209 | 0 | 0 | 0.20418 | 343.7839 | 0.10269 | 0 | 0 | 0.20538 | 344.0595 | 0.10329 | 0 | 0 | 0.20657 | 344.1514 | 0.10349 | 0 | 0 | 0.20697 | 344.427 | 0.10408 | 0 | 0 | 0.20817 | 344.7026 | 0.10468 | 0 | 0 | 0.20936 | 344.8863 | 0.10508 | 0 | 0 | 0.21016 | 345.162 | 0.10568 | 0 | 0 | 0.21136 | 345.3457 | 0.10608 | 0 | 0 | 0.21215 | 345.5294 | 0.10648 | 0 | 0 | 0.21295
2017-12-29 10:00 | 301.2157 | 0.8978 |  | 316.2959 | 0.043068 | 0 | 0 | 0.086135 | 325.1842 | 0.062346 | 0 | 0 | 0.12469 | 332.4564 | 0.07812 | 0 | 0 | 0.15624 | 332.7257 | 0.078704 | 0 | 0 | 0.15741 | 332.9053 | 0.079093 | 0 | 0 | 0.15819 | 333.1746 | 0.079677 | 0 | 0 | 0.15935 | 333.444 | 0.080262 | 0 | 0 | 0.16052 | 333.7133 | 0.080846 | 0 | 0 | 0.16169 | 334.0724 | 0.081625 | 0 | 0 | 0.16325 | 334.3418 | 0.082209 | 0 | 0 | 0.16442 | 334.5213 | 0.082598 | 0 | 0 | 0.1652 | 334.7907 | 0.083183 | 0 | 0 | 0.16637 | 334.9702 | 0.083572 | 0 | 0 | 0.16714 | 335.2396 | 0.084156 | 0 | 0 | 0.16831 | 335.5089 | 0.08474 | 0 | 0 | 0.16948 | 335.6885 | 0.08513 | 0 | 0 | 0.17026 | 335.9578 | 0.085714 | 0 | 0 | 0.17143 | 336.2272 | 0.086298 | 0 | 0 | 0.1726 | 336.3169 | 0.086493 | 0 | 0 | 0.17299 | 336.5863 | 0.087077 | 0 | 0 | 0.17415 | 336.8556 | 0.087661 | 0 | 0 | 0.17532 | 337.0352 | 0.088051 | 0 | 0 | 0.1761 | 337.3045 | 0.088635 | 0 | 0 | 0.17727 | 337.4841 | 0.089025 | 0 | 0 | 0.17805 | 337.6636 | 0.089414 | 0 | 0 | 0.17883
2017-12-29 11:00 | 291.7685 | 0.86964 |  | 306.3758 | 0.021551 | 0 | 0 | 0.043101 | 314.9853 | 0.040225 | 0 | 0 | 0.080449 | 322.0294 | 0.055503 | 0 | 0 | 0.11101 | 322.2903 | 0.056069 | 0 | 0 | 0.11214 | 322.4642 | 0.056447 | 0 | 0 | 0.11289 | 322.7251 | 0.057012 | 0 | 0 | 0.11402 | 322.986 | 0.057578 | 0 | 0 | 0.11516 | 323.2469 | 0.058144 | 0 | 0 | 0.11629 | 323.5948 | 0.058899 | 0 | 0 | 0.1178 | 323.8557 | 0.059465 | 0 | 0 | 0.11893 | 324.0296 | 0.059842 | 0 | 0 | 0.11968 | 324.2905 | 0.060408 | 0 | 0 | 0.12082 | 324.4644 | 0.060785 | 0 | 0 | 0.12157 | 324.7253 | 0.061351 | 0 | 0 | 0.1227 | 324.9862 | 0.061917 | 0 | 0 | 0.12383 | 325.1601 | 0.062294 | 0 | 0 | 0.12459 | 325.421 | 0.06286 | 0 | 0 | 0.12572 | 325.6819 | 0.063426 | 0 | 0 | 0.12685 | 325.7689 | 0.063614 | 0 | 0 | 0.12723 | 326.0298 | 0.06418 | 0 | 0 | 0.12836 | 326.2907 | 0.064746 | 0 | 0 | 0.12949 | 326.4646 | 0.065123 | 0 | 0 | 0.13025 | 326.7255 | 0.065689 | 0 | 0 | 0.13138 | 326.8994 | 0.066066 | 0 | 0 | 0.13213 | 327.0733 | 0.066444 | 0 | 0 | 0.13289
2017-12-29 12:00 | 231.3975 | 0.6897 |  | 242.9824 | 0 | 0 | 0 | 0 | 249.8104 | 0 | 0 | 0 | 0 | 255.397 | 0 | 0 | 0 | 0 | 255.6039 | 0 | 0 | 0 | 0 | 255.7419 | 0 | 0 | 0 | 0 | 255.9488 | 0 | 0 | 0 | 0 | 256.1557 | 0 | 0 | 0 | 0 | 256.3626 | 0 | 0 | 0 | 0 | 256.6385 | 0 | 0 | 0 | 0 | 256.8454 | 0 | 0 | 0 | 0 | 256.9833 | 0 | 0 | 0 | 0 | 257.1902 | 0 | 0 | 0 | 0 | 257.3282 | 0 | 0 | 0 | 0 | 257.5351 | 0 | 0 | 0 | 0 | 257.742 | 0 | 0 | 0 | 0 | 257.88 | 0 | 0 | 0 | 0 | 258.0869 | 0 | 0 | 0 | 0 | 258.2938 | 0 | 0 | 0 | 0 | 258.3627 | 0 | 0 | 0 | 0 | 258.5697 | 0 | 0 | 0 | 0 | 258.7766 | 0 | 0 | 0 | 0 | 258.9145 | 0 | 0 | 0 | 0 | 259.1214 | 0 | 0 | 0 | 0 | 259.2594 | 0 | 0 | 0 | 0 | 259.3973 | 0 | 0 | 0 | 0
2017-12-29 13:00 | 308.95 | 0.92086 |  | 324.4174 | 0.060683 | 0 | 0 | 0.12137 | 333.5339 | 0.080457 | 0 | 0 | 0.16091 | 340.9928 | 0.096635 | 0 | 0 | 0.19327 | 341.2691 | 0.097234 | 0 | 0 | 0.19447 | 341.4533 | 0.097634 | 0 | 0 | 0.19527 | 341.7295 | 0.098233 | 0 | 0 | 0.19647 | 342.0058 | 0.098832 | 0 | 0 | 0.19766 | 342.282 | 0.099431 | 0 | 0 | 0.19886 | 342.6504 | 0.10023 | 0 | 0 | 0.20046 | 342.9266 | 0.10083 | 0 | 0 | 0.20166 | 343.1108 | 0.10123 | 0 | 0 | 0.20246 | 343.3871 | 0.10183 | 0 | 0 | 0.20366 | 343.5712 | 0.10223 | 0 | 0 | 0.20446 | 343.8475 | 0.10283 | 0 | 0 | 0.20565 | 344.1238 | 0.10343 | 0 | 0 | 0.20685 | 344.3079 | 0.10383 | 0 | 0 | 0.20765 | 344.5842 | 0.10442 | 0 | 0 | 0.20885 | 344.8604 | 0.10502 | 0 | 0 | 0.21005 | 344.9525 | 0.10522 | 0 | 0 | 0.21045 | 345.2288 | 0.10582 | 0 | 0 | 0.21165 | 345.505 | 0.10642 | 0 | 0 | 0.21284 | 345.6892 | 0.10682 | 0 | 0 | 0.21364 | 345.9655 | 0.10742 | 0 | 0 | 0.21484 | 346.1496 | 0.10782 | 0 | 0 | 0.21564 | 346.3338 | 0.10822 | 0 | 0 | 0.21644
2017-12-29 14:00 | 303.593 | 0.90489 |  | 318.7923 | 0.048482 | 0 | 0 | 0.096964 | 327.7507 | 0.067913 | 0 | 0 | 0.13583 | 335.0802 | 0.083811 | 0 | 0 | 0.16762 | 335.3517 | 0.0844 | 0 | 0 | 0.1688 | 335.5327 | 0.084792 | 0 | 0 | 0.16958 | 335.8042 | 0.085381 | 0 | 0 | 0.17076 | 336.0756 | 0.08597 | 0 | 0 | 0.17194 | 336.3471 | 0.086558 | 0 | 0 | 0.17312 | 336.709 | 0.087344 | 0 | 0 | 0.17469 | 336.9805 | 0.087932 | 0 | 0 | 0.17586 | 337.1615 | 0.088325 | 0 | 0 | 0.17665 | 337.433 | 0.088914 | 0 | 0 | 0.17783 | 337.6139 | 0.089306 | 0 | 0 | 0.17861 | 337.8854 | 0.089895 | 0 | 0 | 0.17979 | 338.1569 | 0.090484 | 0 | 0 | 0.18097 | 338.3378 | 0.090876 | 0 | 0 | 0.18175 | 338.6093 | 0.091465 | 0 | 0 | 0.18293 | 338.8808 | 0.092054 | 0 | 0 | 0.18411 | 338.9713 | 0.09225 | 0 | 0 | 0.1845 | 339.2427 | 0.092839 | 0 | 0 | 0.18568 | 339.5142 | 0.093428 | 0 | 0 | 0.18686 | 339.6952 | 0.09382 | 0 | 0 | 0.18764 | 339.9666 | 0.094409 | 0 | 0 | 0.18882 | 340.1476 | 0.094802 | 0 | 0 | 0.1896 | 340.3286 | 0.095194 | 0 | 0 | 0.19039
2017-12-29 15:00 | 301.4324 | 0.89845 |  | 316.5235 | 0.043561 | 0 | 0 | 0.087122 | 325.4181 | 0.062854 | 0 | 0 | 0.12571 | 332.6956 | 0.078638 | 0 | 0 | 0.15728 | 332.9651 | 0.079223 | 0 | 0 | 0.15845 | 333.1448 | 0.079613 | 0 | 0 | 0.15923 | 333.4143 | 0.080197 | 0 | 0 | 0.16039 | 333.6839 | 0.080782 | 0 | 0 | 0.16156 | 333.9534 | 0.081367 | 0 | 0 | 0.16273 | 334.3128 | 0.082146 | 0 | 0 | 0.16429 | 334.5823 | 0.082731 | 0 | 0 | 0.16546 | 334.762 | 0.08312 | 0 | 0 | 0.16624 | 335.0315 | 0.083705 | 0 | 0 | 0.16741 | 335.2112 | 0.084095 | 0 | 0 | 0.16819 | 335.4808 | 0.084679 | 0 | 0 | 0.16936 | 335.7503 | 0.085264 | 0 | 0 | 0.17053 | 335.93 | 0.085654 | 0 | 0 | 0.17131 | 336.1995 | 0.086238 | 0 | 0 | 0.17248 | 336.469 | 0.086823 | 0 | 0 | 0.17365 | 336.5589 | 0.087018 | 0 | 0 | 0.17404 | 336.8284 | 0.087602 | 0 | 0 | 0.1752 | 337.098 | 0.088187 | 0 | 0 | 0.17637 | 337.2777 | 0.088577 | 0 | 0 | 0.17715 | 337.5472 | 0.089161 | 0 | 0 | 0.17832 | 337.7269 | 0.089551 | 0 | 0 | 0.1791 | 337.9066 | 0.089941 | 0 | 0 | 0.17988
2017-12-29 16:00 | 310.0309 | 0.92408 |  | 325.5525 | 0.063145 | 0 | 0 | 0.12629 | 334.7009 | 0.082988 | 0 | 0 | 0.16598 | 342.1859 | 0.099223 | 0 | 0 | 0.19845 | 342.4631 | 0.099824 | 0 | 0 | 0.19965 | 342.6479 | 0.10022 | 0 | 0 | 0.20045 | 342.9251 | 0.10083 | 0 | 0 | 0.20165 | 343.2024 | 0.10143 | 0 | 0 | 0.20286 | 343.4796 | 0.10203 | 0 | 0 | 0.20406 | 343.8492 | 0.10283 | 0 | 0 | 0.20566 | 344.1264 | 0.10343 | 0 | 0 | 0.20686 | 344.3113 | 0.10383 | 0 | 0 | 0.20767 | 344.5885 | 0.10443 | 0 | 0 | 0.20887 | 344.7733 | 0.10483 | 0 | 0 | 0.20967 | 345.0505 | 0.10544 | 0 | 0 | 0.21087 | 345.3277 | 0.10604 | 0 | 0 | 0.21208 | 345.5126 | 0.10644 | 0 | 0 | 0.21288 | 345.7898 | 0.10704 | 0 | 0 | 0.21408 | 346.067 | 0.10764 | 0 | 0 | 0.21528 | 346.1594 | 0.10784 | 0 | 0 | 0.21568 | 346.4366 | 0.10844 | 0 | 0 | 0.21689 | 346.7139 | 0.10904 | 0 | 0 | 0.21809 | 346.8987 | 0.10944 | 0 | 0 | 0.21889 | 347.1759 | 0.11005 | 0 | 0 | 0.22009 | 347.3607 | 0.11045 | 0 | 0 | 0.22089 | 347.5455 | 0.11085 | 0 | 0 | 0.2217
2017-12-29 17:00 | 316.6482 | 0.9438 |  | 332.5011 | 0.078217 | 0 | 0 | 0.15643 | 341.8447 | 0.098483 | 0 | 0 | 0.19697 | 349.4895 | 0.11506 | 0 | 0 | 0.23013 | 349.7727 | 0.11568 | 0 | 0 | 0.23136 | 349.9614 | 0.11609 | 0 | 0 | 0.23218 | 350.2446 | 0.1167 | 0 | 0 | 0.2334 | 350.5277 | 0.11732 | 0 | 0 | 0.23463 | 350.8109 | 0.11793 | 0 | 0 | 0.23586 | 351.1884 | 0.11875 | 0 | 0 | 0.2375 | 351.4715 | 0.11936 | 0 | 0 | 0.23873 | 351.6603 | 0.11977 | 0 | 0 | 0.23955 | 351.9434 | 0.12039 | 0 | 0 | 0.24077 | 352.1322 | 0.1208 | 0 | 0 | 0.24159 | 352.4153 | 0.12141 | 0 | 0 | 0.24282 | 352.6985 | 0.12202 | 0 | 0 | 0.24405 | 352.8872 | 0.12243 | 0 | 0 | 0.24487 | 353.1704 | 0.12305 | 0 | 0 | 0.2461 | 353.4535 | 0.12366 | 0 | 0 | 0.24732 | 353.5479 | 0.12387 | 0 | 0 | 0.24773 | 353.831 | 0.12448 | 0 | 0 | 0.24896 | 354.1142 | 0.1251 | 0 | 0 | 0.25019 | 354.3029 | 0.1255 | 0 | 0 | 0.25101 | 354.5861 | 0.12612 | 0 | 0 | 0.25224 | 354.7748 | 0.12653 | 0 | 0 | 0.25306 | 354.9636 | 0.12694 | 0 | 0 | 0.25388
2017-12-29 18:00 | 328.5417 | 0.97925 |  | 344.99 | 0.1053 | 0 | 0 | 0.21061 | 354.6846 | 0.12633 | 0 | 0 | 0.25267 | 362.6165 | 0.14354 | 0 | 0 | 0.28707 | 362.9103 | 0.14417 | 0 | 0 | 0.28835 | 363.1061 | 0.1446 | 0 | 0 | 0.2892 | 363.3999 | 0.14524 | 0 | 0 | 0.29047 | 363.6937 | 0.14587 | 0 | 0 | 0.29175 | 363.9875 | 0.14651 | 0 | 0 | 0.29302 | 364.3792 | 0.14736 | 0 | 0 | 0.29472 | 364.673 | 0.148 | 0.017783 | 0 | 0.31378 | 364.8688 | 0.14842 | 0.030542 | 0 | 0.32739 | 365.1626 | 0.14906 | 0.049682 | 0 | 0.3478 | 365.3584 | 0.14948 | 0.062441 | 0 | 0.36141 | 365.6522 | 0.15012 | 0.081581 | 0 | 0.38182 | 365.946 | 0.15076 | 0.10072 | 0 | 0.40224 | 366.1418 | 0.15118 | 0.11348 | 0 | 0.41585 | 366.4356 | 0.15182 | 0.13262 | 0 | 0.43626 | 366.7294 | 0.15246 | 0.15176 | 0 | 0.45667 | 366.8273 | 0.15267 | 0.15814 | 0 | 0.46348 | 367.1211 | 0.15331 | 0.17728 | 0 | 0.48389 | 367.4149 | 0.15394 | 0.19642 | 0.012043 | 0.52839 | 367.6107 | 0.15437 | 0.20918 | 0.024803 | 0.56752 | 367.9045 | 0.15501 | 0.22832 | 0.043942 | 0.62621 | 368.1003 | 0.15543 | 0.24108 | 0.056702 | 0.66534 | 368.2962 | 0.15586 | 0.25384 | 0.069462 | 0.70447
2017-12-29 19:00 | 326.1112 | 0.97201 |  | 342.4378 | 0.099769 | 0 | 0 | 0.19954 | 352.0607 | 0.12064 | 0 | 0 | 0.24128 | 359.934 | 0.13772 | 0 | 0 | 0.27544 | 360.2256 | 0.13835 | 0 | 0 | 0.2767 | 360.42 | 0.13877 | 0 | 0 | 0.27755 | 360.7116 | 0.13941 | 0 | 0 | 0.27881 | 361.0032 | 0.14004 | 0 | 0 | 0.28008 | 361.2948 | 0.14067 | 0 | 0 | 0.28134 | 361.6836 | 0.14151 | 0 | 0 | 0.28303 | 361.9752 | 0.14215 | 0 | 0 | 0.28429 | 362.1696 | 0.14257 | 0 | 0 | 0.28513 | 362.4612 | 0.1432 | 0 | 0 | 0.2864 | 362.6556 | 0.14362 | 0 | 0 | 0.28724 | 362.9472 | 0.14425 | 0 | 0 | 0.28851 | 363.2388 | 0.14489 | 0 | 0 | 0.28977 | 363.4332 | 0.14531 | 0 | 0 | 0.29062 | 363.7248 | 0.14594 | 0 | 0 | 0.29188 | 364.0164 | 0.14657 | 0 | 0 | 0.29315 | 364.1136 | 0.14678 | 0 | 0 | 0.29357 | 364.4052 | 0.14742 | 0.00033785 | 0 | 0.29517 | 364.6968 | 0.14805 | 0.019336 | 0 | 0.31543 | 364.8912 | 0.14847 | 0.032001 | 0 | 0.32894 | 365.1828 | 0.1491 | 0.050999 | 0 | 0.34921 | 365.3772 | 0.14952 | 0.063664 | 0 | 0.36271 | 365.5716 | 0.14995 | 0.076329 | 0 | 0.37622
2017-12-29 20:00 | 325.061 | 0.96888 |  | 341.3351 | 0.097378 | 0 | 0 | 0.19476 | 350.927 | 0.11818 | 0 | 0 | 0.23636 | 358.7749 | 0.1352 | 0 | 0 | 0.27041 | 359.0656 | 0.13583 | 0 | 0 | 0.27167 | 359.2593 | 0.13626 | 0 | 0 | 0.27251 | 359.55 | 0.13689 | 0 | 0 | 0.27377 | 359.8407 | 0.13752 | 0 | 0 | 0.27503 | 360.1313 | 0.13815 | 0 | 0 | 0.27629 | 360.5189 | 0.13899 | 0 | 0 | 0.27797 | 360.8095 | 0.13962 | 0 | 0 | 0.27924 | 361.0033 | 0.14004 | 0 | 0 | 0.28008 | 361.294 | 0.14067 | 0 | 0 | 0.28134 | 361.4877 | 0.14109 | 0 | 0 | 0.28218 | 361.7784 | 0.14172 | 0 | 0 | 0.28344 | 362.0691 | 0.14235 | 0 | 0 | 0.2847 | 362.2628 | 0.14277 | 0 | 0 | 0.28554 | 362.5535 | 0.1434 | 0 | 0 | 0.2868 | 362.8442 | 0.14403 | 0 | 0 | 0.28806 | 362.9411 | 0.14424 | 0 | 0 | 0.28848 | 363.2317 | 0.14487 | 0 | 0 | 0.28974 | 363.5224 | 0.1455 | 0 | 0 | 0.291 | 363.7162 | 0.14592 | 0 | 0 | 0.29184 | 364.0068 | 0.14655 | 0 | 0 | 0.2931 | 364.2006 | 0.14697 | 0 | 0 | 0.29395 | 364.3944 | 0.14739 | 0 | 0 | 0.29479
2017-12-29 21:00 | 325.3662 | 0.96979 |  | 341.6556 | 0.098073 | 0 | 0 | 0.19615 | 351.2565 | 0.1189 | 0 | 0 | 0.23779 | 359.1117 | 0.13593 | 0 | 0 | 0.27187 | 359.4027 | 0.13657 | 0 | 0 | 0.27313 | 359.5966 | 0.13699 | 0 | 0 | 0.27397 | 359.8876 | 0.13762 | 0 | 0 | 0.27524 | 360.1785 | 0.13825 | 0 | 0 | 0.2765 | 360.4694 | 0.13888 | 0 | 0 | 0.27776 | 360.8573 | 0.13972 | 0 | 0 | 0.27944 | 361.1483 | 0.14035 | 0 | 0 | 0.2807 | 361.3422 | 0.14077 | 0 | 0 | 0.28155 | 361.6332 | 0.1414 | 0 | 0 | 0.28281 | 361.8271 | 0.14182 | 0 | 0 | 0.28365 | 362.1181 | 0.14246 | 0 | 0 | 0.28491 | 362.409 | 0.14309 | 0 | 0 | 0.28617 | 362.603 | 0.14351 | 0 | 0 | 0.28701 | 362.8939 | 0.14414 | 0 | 0 | 0.28828 | 363.1848 | 0.14477 | 0 | 0 | 0.28954 | 363.2818 | 0.14498 | 0 | 0 | 0.28996 | 363.5727 | 0.14561 | 0 | 0 | 0.29122 | 363.8637 | 0.14624 | 0 | 0 | 0.29248 | 364.0576 | 0.14666 | 0 | 0 | 0.29333 | 364.3486 | 0.14729 | 0 | 0 | 0.29459 | 364.5425 | 0.14771 | 0.0092857 | 0 | 0.30471 | 364.7365 | 0.14814 | 0.021922 | 0 | 0.31819
2017-12-29 22:00 | 330.2323 | 0.98429 |  | 346.7653 | 0.10916 | 0 | 0 | 0.21831 | 356.5098 | 0.13029 | 0 | 0 | 0.26058 | 364.4825 | 0.14758 | 0.005378 | 0 | 0.30055 | 364.7778 | 0.14822 | 0.024616 | 0 | 0.32107 | 364.9747 | 0.14865 | 0.037441 | 0 | 0.33474 | 365.27 | 0.14929 | 0.056679 | 0 | 0.35526 | 365.5653 | 0.14993 | 0.075917 | 0 | 0.37578 | 365.8606 | 0.15057 | 0.095155 | 0 | 0.3963 | 366.2543 | 0.15143 | 0.12081 | 0 | 0.42366 | 366.5496 | 0.15207 | 0.14004 | 0 | 0.44418 | 366.7464 | 0.15249 | 0.15287 | 0 | 0.45786 | 367.0417 | 0.15314 | 0.17211 | 0 | 0.47838 | 367.2386 | 0.15356 | 0.18493 | 0.00055762 | 0.49317 | 367.5338 | 0.1542 | 0.20417 | 0.019796 | 0.55217 | 367.8291 | 0.15484 | 0.22341 | 0.039034 | 0.61116 | 368.026 | 0.15527 | 0.23623 | 0.051859 | 0.65049 | 368.3213 | 0.15591 | 0.25547 | 0.071097 | 0.70949 | 368.6166 | 0.15655 | 0.27471 | 0.090335 | 0.76848 | 368.715 | 0.15676 | 0.28112 | 0.096747 | 0.78815 | 369.0103 | 0.1574 | 0.30036 | 0.11599 | 0.84714 | 369.3056 | 0.15805 | 0.3196 | 0.13522 | 0.90614 | 369.5024 | 0.15847 | 0.33242 | 0.14805 | 0.94546 | 369.7977 | 0.15911 | 0.35166 | 0.16729 | 1.0045 | 369.9946 | 0.15954 | 0.36449 | 0.18011 | 1.0438 | 370.1914 | 0.15997 | 0.37731 | 0.19294 | 1.0831
2017-12-29 23:00 | 331.3082 | 0.9875 |  | 347.895 | 0.11161 | 0 | 0 | 0.22321 | 357.6713 | 0.13281 | 0 | 0 | 0.26562 | 365.67 | 0.15016 | 0.082739 | 0 | 0.38306 | 365.9662 | 0.1508 | 0.10204 | 0 | 0.40364 | 366.1637 | 0.15123 | 0.11491 | 0 | 0.41737 | 366.46 | 0.15187 | 0.13421 | 0 | 0.43795 | 366.7562 | 0.15252 | 0.15351 | 0 | 0.45854 | 367.0525 | 0.15316 | 0.17281 | 0 | 0.47913 | 367.4475 | 0.15402 | 0.19854 | 0.014168 | 0.53491 | 367.7437 | 0.15466 | 0.21784 | 0.033469 | 0.5941 | 367.9412 | 0.15509 | 0.23071 | 0.046336 | 0.63356 | 368.2375 | 0.15573 | 0.25001 | 0.065637 | 0.69274 | 368.435 | 0.15616 | 0.26288 | 0.078504 | 0.7322 | 368.7312 | 0.1568 | 0.28218 | 0.097805 | 0.79139 | 369.0275 | 0.15744 | 0.30148 | 0.11711 | 0.85057 | 369.225 | 0.15787 | 0.31435 | 0.12997 | 0.89003 | 369.5212 | 0.15851 | 0.33365 | 0.14927 | 0.94922 | 369.8175 | 0.15916 | 0.35295 | 0.16857 | 1.0084 | 369.9162 | 0.15937 | 0.35938 | 0.17501 | 1.0281 | 370.2125 | 0.16001 | 0.37868 | 0.19431 | 1.0873 | 370.5087 | 0.16066 | 0.39798 | 0.21361 | 1.1465 | 370.7062 | 0.16108 | 0.41085 | 0.22648 | 1.186 | 371.0025 | 0.16173 | 0.43015 | 0.24578 | 1.2452 | 371.2 | 0.16215 | 0.44302 | 0.25864 | 1.2846 | 371.3975 | 0.16258 | 0.45588 | 0.27151 | 1.3241
2017-12-30 | 330.9675 | 0.98648 |  | 347.5373 | 0.11083 | 0 | 0 | 0.22166 | 357.3034 | 0.13201 | 0 | 0 | 0.26403 | 365.2939 | 0.14934 | 0.058239 | 0 | 0.35693 | 365.5899 | 0.14999 | 0.07752 | 0 | 0.37749 | 365.7872 | 0.15041 | 0.090374 | 0 | 0.3912 | 366.0831 | 0.15106 | 0.10965 | 0 | 0.41177 | 366.3791 | 0.1517 | 0.12894 | 0 | 0.43233 | 366.675 | 0.15234 | 0.14822 | 0 | 0.4529 | 367.0696 | 0.1532 | 0.17392 | 0 | 0.48031 | 367.3655 | 0.15384 | 0.1932 | 0.0088299 | 0.51854 | 367.5628 | 0.15427 | 0.20606 | 0.021684 | 0.55796 | 367.8588 | 0.15491 | 0.22534 | 0.040965 | 0.61708 | 368.0561 | 0.15534 | 0.23819 | 0.053818 | 0.6565 | 368.352 | 0.15598 | 0.25747 | 0.073099 | 0.71563 | 368.648 | 0.15662 | 0.27675 | 0.09238 | 0.77475 | 368.8453 | 0.15705 | 0.28961 | 0.10523 | 0.81417 | 369.1412 | 0.15769 | 0.30889 | 0.12451 | 0.8733 | 369.4371 | 0.15833 | 0.32817 | 0.1438 | 0.93242 | 369.5358 | 0.15854 | 0.3346 | 0.15022 | 0.95213 | 369.8317 | 0.15919 | 0.35388 | 0.1695 | 1.0113 | 370.1277 | 0.15983 | 0.37316 | 0.18878 | 1.0704 | 370.325 | 0.16026 | 0.38601 | 0.20164 | 1.1098 | 370.6209 | 0.1609 | 0.40529 | 0.22092 | 1.1689 | 370.8182 | 0.16133 | 0.41815 | 0.23377 | 1.2083 | 371.0155 | 0.16175 | 0.431 | 0.24663 | 1.2478
2017-12-30 01:00 | 331.192 | 0.98715 |  | 347.773 | 0.11134 | 0 | 0 | 0.22268 | 357.5458 | 0.13254 | 0 | 0 | 0.26508 | 365.5418 | 0.14988 | 0.074385 | 0 | 0.37415 | 365.8379 | 0.15052 | 0.093679 | 0 | 0.39473 | 366.0353 | 0.15095 | 0.10654 | 0 | 0.40845 | 366.3315 | 0.15159 | 0.12584 | 0 | 0.42902 | 366.6276 | 0.15224 | 0.14513 | 0 | 0.4496 | 366.9238 | 0.15288 | 0.16442 | 0 | 0.47018 | 367.3186 | 0.15374 | 0.19015 | 0.0057737 | 0.50917 | 367.6148 | 0.15438 | 0.20944 | 0.025068 | 0.56833 | 367.8122 | 0.15481 | 0.2223 | 0.03793 | 0.60778 | 368.1083 | 0.15545 | 0.2416 | 0.057224 | 0.66694 | 368.3058 | 0.15588 | 0.25446 | 0.070087 | 0.70639 | 368.6019 | 0.15652 | 0.27375 | 0.08938 | 0.76555 | 368.8981 | 0.15716 | 0.29305 | 0.10867 | 0.82472 | 369.0955 | 0.15759 | 0.30591 | 0.12154 | 0.86416 | 369.3916 | 0.15823 | 0.32521 | 0.14083 | 0.92333 | 369.6878 | 0.15887 | 0.3445 | 0.16012 | 0.9825 | 369.7865 | 0.15909 | 0.35093 | 0.16656 | 1.0022 | 370.0826 | 0.15973 | 0.37022 | 0.18585 | 1.0614 | 370.3788 | 0.16037 | 0.38952 | 0.20514 | 1.1206 | 370.5762 | 0.1608 | 0.40238 | 0.21801 | 1.16 | 370.8724 | 0.16144 | 0.42167 | 0.2373 | 1.2192 | 371.0698 | 0.16187 | 0.43454 | 0.25016 | 1.2586 | 371.2672 | 0.1623 | 0.4474 | 0.26303 | 1.2981
2017-12-30 02:00 | 330.2315 | 0.98429 |  | 346.7644 | 0.10915 | 0 | 0 | 0.21831 | 356.5088 | 0.13029 | 0 | 0 | 0.26058 | 364.4816 | 0.14758 | 0.0053143 | 0 | 0.30048 | 364.7769 | 0.14822 | 0.024552 | 0 | 0.321 | 364.9737 | 0.14865 | 0.037377 | 0 | 0.33468 | 365.269 | 0.14929 | 0.056615 | 0 | 0.3552 | 365.5643 | 0.14993 | 0.075853 | 0 | 0.37571 | 365.8596 | 0.15057 | 0.095091 | 0 | 0.39623 | 366.2533 | 0.15143 | 0.12074 | 0 | 0.42359 | 366.5486 | 0.15207 | 0.13998 | 0 | 0.44411 | 366.7454 | 0.15249 | 0.1528 | 0 | 0.45779 | 367.0407 | 0.15313 | 0.17204 | 0 | 0.47831 | 367.2376 | 0.15356 | 0.18487 | 0.0004935 | 0.49297 | 367.5329 | 0.1542 | 0.20411 | 0.019731 | 0.55197 | 367.8281 | 0.15484 | 0.22334 | 0.038969 | 0.61096 | 368.025 | 0.15527 | 0.23617 | 0.051795 | 0.65029 | 368.3203 | 0.15591 | 0.25541 | 0.071032 | 0.70929 | 368.6156 | 0.15655 | 0.27464 | 0.09027 | 0.76828 | 368.714 | 0.15676 | 0.28106 | 0.096683 | 0.78795 | 369.0093 | 0.1574 | 0.3003 | 0.11592 | 0.84694 | 369.3046 | 0.15804 | 0.31953 | 0.13516 | 0.90594 | 369.5014 | 0.15847 | 0.33236 | 0.14798 | 0.94527 | 369.7967 | 0.15911 | 0.3516 | 0.16722 | 1.0043 | 369.9936 | 0.15954 | 0.36442 | 0.18005 | 1.0436 | 370.1904 | 0.15996 | 0.37725 | 0.19287 | 1.0829
2017-12-30 03:00 | 326.8276 | 0.97414 |  | 343.1902 | 0.1014 | 0 | 0 | 0.2028 | 352.8342 | 0.12232 | 0 | 0 | 0.24464 | 360.7247 | 0.13943 | 0 | 0 | 0.27887 | 361.017 | 0.14007 | 0 | 0 | 0.28013 | 361.2118 | 0.14049 | 0 | 0 | 0.28098 | 361.504 | 0.14112 | 0 | 0 | 0.28225 | 361.7963 | 0.14176 | 0 | 0 | 0.28352 | 362.0885 | 0.14239 | 0 | 0 | 0.28478 | 362.4782 | 0.14324 | 0 | 0 | 0.28647 | 362.7704 | 0.14387 | 0 | 0 | 0.28774 | 362.9652 | 0.14429 | 0 | 0 | 0.28859 | 363.2575 | 0.14493 | 0 | 0 | 0.28985 | 363.4523 | 0.14535 | 0 | 0 | 0.2907 | 363.7445 | 0.14598 | 0 | 0 | 0.29197 | 364.0368 | 0.14662 | 0 | 0 | 0.29323 | 364.2316 | 0.14704 | 0 | 0 | 0.29408 | 364.5239 | 0.14767 | 0.0080696 | 0 | 0.30342 | 364.8161 | 0.14831 | 0.027109 | 0 | 0.32372 | 364.9135 | 0.14852 | 0.033456 | 0 | 0.33049 | 365.2058 | 0.14915 | 0.052495 | 0 | 0.3508 | 365.498 | 0.14979 | 0.071535 | 0 | 0.37111 | 365.6928 | 0.15021 | 0.084228 | 0 | 0.38465 | 365.9851 | 0.15084 | 0.10327 | 0 | 0.40495 | 366.1799 | 0.15127 | 0.11596 | 0 | 0.41849 | 366.3747 | 0.15169 | 0.12865 | 0 | 0.43203
2017-12-30 04:00 | 325.0675 | 0.9689 |  | 341.3419 | 0.097392 | 0 | 0 | 0.19478 | 350.934 | 0.1182 | 0 | 0 | 0.23639 | 358.782 | 0.13522 | 0 | 0 | 0.27044 | 359.0727 | 0.13585 | 0 | 0 | 0.2717 | 359.2665 | 0.13627 | 0 | 0 | 0.27254 | 359.5572 | 0.1369 | 0 | 0 | 0.2738 | 359.8478 | 0.13753 | 0 | 0 | 0.27506 | 360.1385 | 0.13816 | 0 | 0 | 0.27632 | 360.5261 | 0.139 | 0 | 0 | 0.27801 | 360.8167 | 0.13963 | 0 | 0 | 0.27927 | 361.0105 | 0.14005 | 0 | 0 | 0.28011 | 361.3012 | 0.14068 | 0 | 0 | 0.28137 | 361.4949 | 0.1411 | 0 | 0 | 0.28221 | 361.7856 | 0.14173 | 0 | 0 | 0.28347 | 362.0763 | 0.14237 | 0 | 0 | 0.28473 | 362.2701 | 0.14279 | 0 | 0 | 0.28557 | 362.5607 | 0.14342 | 0 | 0 | 0.28683 | 362.8514 | 0.14405 | 0 | 0 | 0.28809 | 362.9483 | 0.14426 | 0 | 0 | 0.28851 | 363.239 | 0.14489 | 0 | 0 | 0.28977 | 363.5296 | 0.14552 | 0 | 0 | 0.29103 | 363.7234 | 0.14594 | 0 | 0 | 0.29188 | 364.0141 | 0.14657 | 0 | 0 | 0.29314 | 364.2079 | 0.14699 | 0 | 0 | 0.29398 | 364.4016 | 0.14741 | 0.00010655 | 0 | 0.29492
2017-12-30 05:00 | 330.9976 | 0.98657 |  | 347.5689 | 0.1109 | 0 | 0 | 0.2218 | 357.336 | 0.13208 | 0 | 0 | 0.26417 | 365.3272 | 0.14942 | 0.060405 | 0 | 0.35924 | 365.6231 | 0.15006 | 0.079688 | 0 | 0.3798 | 365.8205 | 0.15049 | 0.092543 | 0 | 0.39352 | 366.1164 | 0.15113 | 0.11183 | 0 | 0.41408 | 366.4124 | 0.15177 | 0.13111 | 0 | 0.43465 | 366.7084 | 0.15241 | 0.15039 | 0 | 0.45521 | 367.103 | 0.15327 | 0.1761 | 0 | 0.48264 | 367.399 | 0.15391 | 0.19538 | 0.011009 | 0.52522 | 367.5963 | 0.15434 | 0.20824 | 0.023864 | 0.56464 | 367.8923 | 0.15498 | 0.22752 | 0.043146 | 0.62377 | 368.0896 | 0.15541 | 0.24038 | 0.056001 | 0.66319 | 368.3855 | 0.15605 | 0.25966 | 0.075284 | 0.72233 | 368.6815 | 0.15669 | 0.27894 | 0.094566 | 0.78146 | 368.8788 | 0.15712 | 0.2918 | 0.10742 | 0.82088 | 369.1748 | 0.15776 | 0.31108 | 0.1267 | 0.88001 | 369.4708 | 0.1584 | 0.33036 | 0.14599 | 0.93914 | 369.5694 | 0.15862 | 0.33679 | 0.15241 | 0.95885 | 369.8654 | 0.15926 | 0.35607 | 0.1717 | 1.018 | 370.1614 | 0.1599 | 0.37535 | 0.19098 | 1.0771 | 370.3587 | 0.16033 | 0.38821 | 0.20383 | 1.1165 | 370.6547 | 0.16097 | 0.40749 | 0.22312 | 1.1757 | 370.852 | 0.1614 | 0.42035 | 0.23597 | 1.2151 | 371.0493 | 0.16183 | 0.4332 | 0.24883 | 1.2545
2017-12-30 06:00 | 327.333 | 0.97565 |  | 343.7208 | 0.10255 | 0 | 0 | 0.2051 | 353.3797 | 0.1235 | 0 | 0 | 0.247 | 361.2825 | 0.14064 | 0 | 0 | 0.28129 | 361.5752 | 0.14128 | 0 | 0 | 0.28256 | 361.7703 | 0.1417 | 0 | 0 | 0.2834 | 362.063 | 0.14234 | 0 | 0 | 0.28467 | 362.3557 | 0.14297 | 0 | 0 | 0.28594 | 362.6484 | 0.14361 | 0 | 0 | 0.28721 | 363.0386 | 0.14445 | 0 | 0 | 0.2889 | 363.3313 | 0.14509 | 0 | 0 | 0.29017 | 363.5265 | 0.14551 | 0 | 0 | 0.29102 | 363.8192 | 0.14615 | 0 | 0 | 0.29229 | 364.0143 | 0.14657 | 0 | 0 | 0.29314 | 364.307 | 0.1472 | 0 | 0 | 0.29441 | 364.5997 | 0.14784 | 0.013009 | 0 | 0.30869 | 364.7948 | 0.14826 | 0.025721 | 0 | 0.32224 | 365.0875 | 0.1489 | 0.04479 | 0 | 0.34258 | 365.3802 | 0.14953 | 0.063859 | 0 | 0.36292 | 365.4778 | 0.14974 | 0.070216 | 0 | 0.3697 | 365.7705 | 0.15038 | 0.089285 | 0 | 0.39004 | 366.0631 | 0.15101 | 0.10835 | 0 | 0.41038 | 366.2583 | 0.15144 | 0.12107 | 0 | 0.42394 | 366.551 | 0.15207 | 0.14014 | 0 | 0.44428 | 366.7461 | 0.15249 | 0.15285 | 0 | 0.45784 | 366.9412 | 0.15292 | 0.16556 | 0 | 0.4714
2017-12-30 07:00 | 324.7313 | 0.96789 |  | 340.9888 | 0.096626 | 0 | 0 | 0.19325 | 350.571 | 0.11741 | 0 | 0 | 0.23482 | 358.4109 | 0.13441 | 0 | 0 | 0.26883 | 358.7013 | 0.13504 | 0 | 0 | 0.27009 | 358.8949 | 0.13546 | 0 | 0 | 0.27093 | 359.1852 | 0.13609 | 0 | 0 | 0.27219 | 359.4756 | 0.13672 | 0 | 0 | 0.27345 | 359.766 | 0.13735 | 0 | 0 | 0.27471 | 360.1531 | 0.13819 | 0 | 0 | 0.27639 | 360.4435 | 0.13882 | 0 | 0 | 0.27765 | 360.6371 | 0.13924 | 0 | 0 | 0.27849 | 360.9274 | 0.13987 | 0 | 0 | 0.27975 | 361.121 | 0.14029 | 0 | 0 | 0.28059 | 361.4114 | 0.14092 | 0 | 0 | 0.28185 | 361.7018 | 0.14155 | 0 | 0 | 0.28311 | 361.8953 | 0.14197 | 0 | 0 | 0.28395 | 362.1857 | 0.1426 | 0 | 0 | 0.2852 | 362.4761 | 0.14323 | 0 | 0 | 0.28646 | 362.5729 | 0.14344 | 0 | 0 | 0.28688 | 362.8632 | 0.14407 | 0 | 0 | 0.28814 | 363.1536 | 0.1447 | 0 | 0 | 0.2894 | 363.3472 | 0.14512 | 0 | 0 | 0.29024 | 363.6375 | 0.14575 | 0 | 0 | 0.2915 | 363.8311 | 0.14617 | 0 | 0 | 0.29234 | 364.0247 | 0.14659 | 0 | 0 | 0.29318
2017-12-30 08:00 | 315.5349 | 0.94048 |  | 331.332 | 0.075681 | 0 | 0 | 0.15136 | 340.6428 | 0.095876 | 0 | 0 | 0.19175 | 348.2607 | 0.1124 | 0 | 0 | 0.2248 | 348.5429 | 0.11301 | 0 | 0 | 0.22602 | 348.731 | 0.11342 | 0 | 0 | 0.22684 | 349.0131 | 0.11403 | 0 | 0 | 0.22806 | 349.2952 | 0.11464 | 0 | 0 | 0.22929 | 349.5774 | 0.11525 | 0 | 0 | 0.23051 | 349.9536 | 0.11607 | 0 | 0 | 0.23214 | 350.2357 | 0.11668 | 0 | 0 | 0.23337 | 350.4238 | 0.11709 | 0 | 0 | 0.23418 | 350.706 | 0.1177 | 0 | 0 | 0.23541 | 350.8941 | 0.11811 | 0 | 0 | 0.23622 | 351.1762 | 0.11872 | 0 | 0 | 0.23745 | 351.4584 | 0.11933 | 0 | 0 | 0.23867 | 351.6464 | 0.11974 | 0 | 0 | 0.23949 | 351.9286 | 0.12035 | 0 | 0 | 0.24071 | 352.2107 | 0.12097 | 0 | 0 | 0.24193 | 352.3048 | 0.12117 | 0 | 0 | 0.24234 | 352.5869 | 0.12178 | 0 | 0 | 0.24357 | 352.8691 | 0.12239 | 0 | 0 | 0.24479 | 353.0572 | 0.1228 | 0 | 0 | 0.24561 | 353.3393 | 0.12341 | 0 | 0 | 0.24683 | 353.5274 | 0.12382 | 0 | 0 | 0.24765 | 353.7155 | 0.12423 | 0 | 0 | 0.24846
2017-12-30 09:00 | 319.4187 | 0.95206 |  | 335.4103 | 0.084527 | 0 | 0 | 0.16905 | 344.8357 | 0.10497 | 0 | 0 | 0.20994 | 352.5474 | 0.1217 | 0 | 0 | 0.24339 | 352.833 | 0.12232 | 0 | 0 | 0.24463 | 353.0234 | 0.12273 | 0 | 0 | 0.24546 | 353.309 | 0.12335 | 0 | 0 | 0.2467 | 353.5947 | 0.12397 | 0 | 0 | 0.24794 | 353.8803 | 0.12459 | 0 | 0 | 0.24918 | 354.2611 | 0.12541 | 0 | 0 | 0.25083 | 354.5467 | 0.12603 | 0 | 0 | 0.25207 | 354.7371 | 0.12645 | 0 | 0 | 0.25289 | 355.0228 | 0.12707 | 0 | 0 | 0.25413 | 355.2132 | 0.12748 | 0 | 0 | 0.25496 | 355.4988 | 0.1281 | 0 | 0 | 0.2562 | 355.7844 | 0.12872 | 0 | 0 | 0.25744 | 355.9748 | 0.12913 | 0 | 0 | 0.25826 | 356.2604 | 0.12975 | 0 | 0 | 0.2595 | 356.546 | 0.13037 | 0 | 0 | 0.26074 | 356.6413 | 0.13058 | 0 | 0 | 0.26115 | 356.9269 | 0.1312 | 0 | 0 | 0.26239 | 357.2125 | 0.13182 | 0 | 0 | 0.26363 | 357.4029 | 0.13223 | 0 | 0 | 0.26446 | 357.6885 | 0.13285 | 0 | 0 | 0.2657 | 357.8789 | 0.13326 | 0 | 0 | 0.26652 | 358.0693 | 0.13367 | 0 | 0 | 0.26735
2017-12-30 10:00 | 314.5071 | 0.93742 |  | 330.2528 | 0.07334 | 0 | 0 | 0.14668 | 339.5332 | 0.093469 | 0 | 0 | 0.18694 | 347.1263 | 0.10994 | 0 | 0 | 0.21988 | 347.4075 | 0.11055 | 0 | 0 | 0.2211 | 347.595 | 0.11096 | 0 | 0 | 0.22191 | 347.8763 | 0.11157 | 0 | 0 | 0.22313 | 348.1575 | 0.11218 | 0 | 0 | 0.22435 | 348.4387 | 0.11279 | 0 | 0 | 0.22557 | 348.8137 | 0.1136 | 0 | 0 | 0.2272 | 349.0949 | 0.11421 | 0 | 0 | 0.22842 | 349.2824 | 0.11462 | 0 | 0 | 0.22923 | 349.5636 | 0.11523 | 0 | 0 | 0.23045 | 349.7511 | 0.11563 | 0 | 0 | 0.23126 | 350.0323 | 0.11624 | 0 | 0 | 0.23248 | 350.3135 | 0.11685 | 0 | 0 | 0.2337 | 350.501 | 0.11726 | 0 | 0 | 0.23452 | 350.7823 | 0.11787 | 0 | 0 | 0.23574 | 351.0635 | 0.11848 | 0 | 0 | 0.23696 | 351.1572 | 0.11868 | 0 | 0 | 0.23736 | 351.4384 | 0.11929 | 0 | 0 | 0.23858 | 351.7197 | 0.1199 | 0 | 0 | 0.2398 | 351.9072 | 0.12031 | 0 | 0 | 0.24062 | 352.1884 | 0.12092 | 0 | 0 | 0.24184 | 352.3759 | 0.12132 | 0 | 0 | 0.24265 | 352.5634 | 0.12173 | 0 | 0 | 0.24346
2017-12-30 11:00 | 306.6342 | 0.91395 |  | 321.9858 | 0.055409 | 0 | 0 | 0.11082 | 331.0339 | 0.075034 | 0 | 0 | 0.15007 | 338.437 | 0.091091 | 0 | 0 | 0.18218 | 338.7111 | 0.091686 | 0 | 0 | 0.18337 | 338.8939 | 0.092083 | 0 | 0 | 0.18417 | 339.1681 | 0.092677 | 0 | 0 | 0.18535 | 339.4423 | 0.093272 | 0 | 0 | 0.18654 | 339.7165 | 0.093867 | 0 | 0 | 0.18773 | 340.0821 | 0.09466 | 0 | 0 | 0.18932 | 340.3563 | 0.095254 | 0 | 0 | 0.19051 | 340.5391 | 0.095651 | 0 | 0 | 0.1913 | 340.8132 | 0.096246 | 0 | 0 | 0.19249 | 340.996 | 0.096642 | 0 | 0 | 0.19328 | 341.2702 | 0.097237 | 0 | 0 | 0.19447 | 341.5444 | 0.097831 | 0 | 0 | 0.19566 | 341.7272 | 0.098228 | 0 | 0 | 0.19646 | 342.0014 | 0.098823 | 0 | 0 | 0.19765 | 342.2756 | 0.099417 | 0 | 0 | 0.19883 | 342.367 | 0.099616 | 0 | 0 | 0.19923 | 342.6411 | 0.10021 | 0 | 0 | 0.20042 | 342.9153 | 0.1008 | 0 | 0 | 0.20161 | 343.0981 | 0.1012 | 0 | 0 | 0.2024 | 343.3723 | 0.1018 | 0 | 0 | 0.20359 | 343.5551 | 0.10219 | 0 | 0 | 0.20439 | 343.7379 | 0.10259 | 0 | 0 | 0.20518
2017-12-30 12:00 | 295.8245 | 0.88173 |  | 310.6349 | 0.030789 | 0 | 0 | 0.061578 | 319.3641 | 0.049722 | 0 | 0 | 0.099445 | 326.5061 | 0.065213 | 0 | 0 | 0.13043 | 326.7707 | 0.065787 | 0 | 0 | 0.13157 | 326.947 | 0.06617 | 0 | 0 | 0.13234 | 327.2115 | 0.066743 | 0 | 0 | 0.13349 | 327.476 | 0.067317 | 0 | 0 | 0.13463 | 327.7406 | 0.067891 | 0 | 0 | 0.13578 | 328.0933 | 0.068656 | 0 | 0 | 0.13731 | 328.3578 | 0.06923 | 0 | 0 | 0.13846 | 328.5341 | 0.069612 | 0 | 0 | 0.13922 | 328.7986 | 0.070186 | 0 | 0 | 0.14037 | 328.975 | 0.070568 | 0 | 0 | 0.14114 | 329.2395 | 0.071142 | 0 | 0 | 0.14228 | 329.504 | 0.071716 | 0 | 0 | 0.14343 | 329.6804 | 0.072098 | 0 | 0 | 0.1442 | 329.9449 | 0.072672 | 0 | 0 | 0.14534 | 330.2094 | 0.073246 | 0 | 0 | 0.14649 | 330.2976 | 0.073437 | 0 | 0 | 0.14687 | 330.5621 | 0.074011 | 0 | 0 | 0.14802 | 330.8266 | 0.074585 | 0 | 0 | 0.14917 | 331.003 | 0.074967 | 0 | 0 | 0.14993 | 331.2675 | 0.075541 | 0 | 0 | 0.15108 | 331.4438 | 0.075923 | 0 | 0 | 0.15185 | 331.6202 | 0.076306 | 0 | 0 | 0.15261
2017-12-30 13:00 | 305.247 | 0.90982 |  | 320.5291 | 0.052249 | 0 | 0 | 0.1045 | 329.5363 | 0.071786 | 0 | 0 | 0.14357 | 336.9059 | 0.08777 | 0 | 0 | 0.17554 | 337.1788 | 0.088362 | 0 | 0 | 0.17672 | 337.3608 | 0.088757 | 0 | 0 | 0.17751 | 337.6337 | 0.089349 | 0 | 0 | 0.1787 | 337.9067 | 0.089941 | 0 | 0 | 0.17988 | 338.1796 | 0.090533 | 0 | 0 | 0.18107 | 338.5435 | 0.091323 | 0 | 0 | 0.18265 | 338.8165 | 0.091915 | 0 | 0 | 0.18383 | 338.9985 | 0.092309 | 0 | 0 | 0.18462 | 339.2714 | 0.092901 | 0 | 0 | 0.1858 | 339.4534 | 0.093296 | 0 | 0 | 0.18659 | 339.7263 | 0.093888 | 0 | 0 | 0.18778 | 339.9993 | 0.09448 | 0 | 0 | 0.18896 | 340.1812 | 0.094875 | 0 | 0 | 0.18975 | 340.4542 | 0.095467 | 0 | 0 | 0.19093 | 340.7271 | 0.096059 | 0 | 0 | 0.19212 | 340.8181 | 0.096256 | 0 | 0 | 0.19251 | 341.091 | 0.096848 | 0 | 0 | 0.1937 | 341.364 | 0.09744 | 0 | 0 | 0.19488 | 341.5459 | 0.097835 | 0 | 0 | 0.19567 | 341.8189 | 0.098427 | 0 | 0 | 0.19685 | 342.0009 | 0.098821 | 0 | 0 | 0.19764 | 342.1828 | 0.099216 | 0 | 0 | 0.19843
2017-12-30 14:00 | 289.3617 | 0.86247 |  | 303.8485 | 0.016069 | 0 | 0 | 0.032138 | 312.387 | 0.034589 | 0 | 0 | 0.069178 | 319.373 | 0.049742 | 0 | 0 | 0.099483 | 319.6317 | 0.050303 | 0 | 0 | 0.10061 | 319.8042 | 0.050677 | 0 | 0 | 0.10135 | 320.063 | 0.051238 | 0 | 0 | 0.10248 | 320.3217 | 0.051799 | 0 | 0 | 0.1036 | 320.5804 | 0.052361 | 0 | 0 | 0.10472 | 320.9254 | 0.053109 | 0 | 0 | 0.10622 | 321.1842 | 0.05367 | 0 | 0 | 0.10734 | 321.3567 | 0.054044 | 0 | 0 | 0.10809 | 321.6154 | 0.054605 | 0 | 0 | 0.10921 | 321.7879 | 0.05498 | 0 | 0 | 0.10996 | 322.0466 | 0.055541 | 0 | 0 | 0.11108 | 322.3054 | 0.056102 | 0 | 0 | 0.1122 | 322.4779 | 0.056476 | 0 | 0 | 0.11295 | 322.7366 | 0.057037 | 0 | 0 | 0.11407 | 322.9954 | 0.057599 | 0 | 0 | 0.1152 | 323.0816 | 0.057786 | 0 | 0 | 0.11557 | 323.3403 | 0.058347 | 0 | 0 | 0.11669 | 323.5991 | 0.058908 | 0 | 0 | 0.11782 | 323.7716 | 0.059282 | 0 | 0 | 0.11856 | 324.0303 | 0.059843 | 0 | 0 | 0.11969 | 324.2028 | 0.060218 | 0 | 0 | 0.12044 | 324.3753 | 0.060592 | 0 | 0 | 0.12118
2017-12-30 15:00 | 293.167 | 0.87381 |  | 307.8444 | 0.024736 | 0 | 0 | 0.049472 | 316.4951 | 0.0435 | 0 | 0 | 0.086999 | 323.573 | 0.058851 | 0 | 0 | 0.1177 | 323.8351 | 0.05942 | 0 | 0 | 0.11884 | 324.0099 | 0.059799 | 0 | 0 | 0.1196 | 324.272 | 0.060368 | 0 | 0 | 0.12074 | 324.5342 | 0.060936 | 0 | 0 | 0.12187 | 324.7963 | 0.061505 | 0 | 0 | 0.12301 | 325.1459 | 0.062263 | 0 | 0 | 0.12453 | 325.408 | 0.062832 | 0 | 0 | 0.12566 | 325.5828 | 0.063211 | 0 | 0 | 0.12642 | 325.8449 | 0.063779 | 0 | 0 | 0.12756 | 326.0197 | 0.064158 | 0 | 0 | 0.12832 | 326.2818 | 0.064727 | 0 | 0 | 0.12945 | 326.544 | 0.065295 | 0 | 0 | 0.13059 | 326.7187 | 0.065675 | 0 | 0 | 0.13135 | 326.9809 | 0.066243 | 0 | 0 | 0.13249 | 327.243 | 0.066812 | 0 | 0 | 0.13362 | 327.3304 | 0.067001 | 0 | 0 | 0.134 | 327.5925 | 0.06757 | 0 | 0 | 0.13514 | 327.8547 | 0.068138 | 0 | 0 | 0.13628 | 328.0294 | 0.068517 | 0 | 0 | 0.13703 | 328.2916 | 0.069086 | 0 | 0 | 0.13817 | 328.4663 | 0.069465 | 0 | 0 | 0.13893 | 328.6411 | 0.069844 | 0 | 0 | 0.13969
2017-12-30 16:00 | 291.9206 | 0.8701 |  | 306.5355 | 0.021897 | 0 | 0 | 0.043794 | 315.1495 | 0.040581 | 0 | 0 | 0.081162 | 322.1973 | 0.055868 | 0 | 0 | 0.11174 | 322.4583 | 0.056434 | 0 | 0 | 0.11287 | 322.6323 | 0.056811 | 0 | 0 | 0.11362 | 322.8933 | 0.057377 | 0 | 0 | 0.11475 | 323.1544 | 0.057943 | 0 | 0 | 0.11589 | 323.4154 | 0.05851 | 0 | 0 | 0.11702 | 323.7634 | 0.059265 | 0 | 0 | 0.11853 | 324.0245 | 0.059831 | 0 | 0 | 0.11966 | 324.1985 | 0.060208 | 0 | 0 | 0.12042 | 324.4595 | 0.060774 | 0 | 0 | 0.12155 | 324.6335 | 0.061152 | 0 | 0 | 0.1223 | 324.8946 | 0.061718 | 0 | 0 | 0.12344 | 325.1556 | 0.062284 | 0 | 0 | 0.12457 | 325.3296 | 0.062662 | 0 | 0 | 0.12532 | 325.5907 | 0.063228 | 0 | 0 | 0.12646 | 325.8517 | 0.063794 | 0 | 0 | 0.12759 | 325.9387 | 0.063983 | 0 | 0 | 0.12797 | 326.1997 | 0.064549 | 0 | 0 | 0.1291 | 326.4607 | 0.065115 | 0 | 0 | 0.13023 | 326.6348 | 0.065492 | 0 | 0 | 0.13098 | 326.8958 | 0.066059 | 0 | 0 | 0.13212 | 327.0698 | 0.066436 | 0 | 0 | 0.13287 | 327.2438 | 0.066814 | 0 | 0 | 0.13363
2017-12-30 17:00 | 285.0883 | 0.84973 |  | 299.3611 | 0.0063359 | 0 | 0 | 0.012672 | 307.7735 | 0.024582 | 0 | 0 | 0.049165 | 314.6563 | 0.039511 | 0 | 0 | 0.079022 | 314.9112 | 0.040064 | 0 | 0 | 0.080128 | 315.0812 | 0.040433 | 0 | 0 | 0.080866 | 315.3361 | 0.040986 | 0 | 0 | 0.081971 | 315.591 | 0.041539 | 0 | 0 | 0.083077 | 315.846 | 0.042092 | 0 | 0 | 0.084183 | 316.1859 | 0.042829 | 0 | 0 | 0.085657 | 316.4408 | 0.043382 | 0 | 0 | 0.086763 | 316.6107 | 0.04375 | 0 | 0 | 0.087501 | 316.8656 | 0.044303 | 0 | 0 | 0.088606 | 317.0356 | 0.044672 | 0 | 0 | 0.089344 | 317.2905 | 0.045225 | 0 | 0 | 0.090449 | 317.5454 | 0.045778 | 0 | 0 | 0.091555 | 317.7154 | 0.046146 | 0 | 0 | 0.092293 | 317.9703 | 0.046699 | 0 | 0 | 0.093398 | 318.2252 | 0.047252 | 0 | 0 | 0.094504 | 318.3102 | 0.047436 | 0 | 0 | 0.094873 | 318.5651 | 0.047989 | 0 | 0 | 0.095979 | 318.82 | 0.048542 | 0 | 0 | 0.097085 | 318.99 | 0.048911 | 0 | 0 | 0.097822 | 319.2449 | 0.049464 | 0 | 0 | 0.098928 | 319.4148 | 0.049832 | 0 | 0 | 0.099665 | 319.5848 | 0.050201 | 0 | 0 | 0.1004
2017-12-30 18:00 | 284.4775 | 0.84791 |  | 298.7198 | 0.0049448 | 0 | 0 | 0.0098896 | 307.1141 | 0.023152 | 0 | 0 | 0.046304 | 313.9822 | 0.038049 | 0 | 0 | 0.076098 | 314.2366 | 0.038601 | 0 | 0 | 0.077202 | 314.4062 | 0.038969 | 0 | 0 | 0.077937 | 314.6605 | 0.03952 | 0 | 0 | 0.079041 | 314.9149 | 0.040072 | 0 | 0 | 0.080144 | 315.1693 | 0.040624 | 0 | 0 | 0.081248 | 315.5084 | 0.041359 | 0 | 0 | 0.082719 | 315.7628 | 0.041911 | 0 | 0 | 0.083822 | 315.9324 | 0.042279 | 0 | 0 | 0.084558 | 316.1868 | 0.042831 | 0 | 0 | 0.085662 | 316.3564 | 0.043199 | 0 | 0 | 0.086397 | 316.6107 | 0.04375 | 0 | 0 | 0.087501 | 316.8651 | 0.044302 | 0 | 0 | 0.088604 | 317.0347 | 0.04467 | 0 | 0 | 0.08934 | 317.2891 | 0.045222 | 0 | 0 | 0.090443 | 317.5434 | 0.045773 | 0 | 0 | 0.091547 | 317.6282 | 0.045957 | 0 | 0 | 0.091915 | 317.8826 | 0.046509 | 0 | 0 | 0.093018 | 318.137 | 0.047061 | 0 | 0 | 0.094121 | 318.3066 | 0.047429 | 0 | 0 | 0.094857 | 318.5609 | 0.04798 | 0 | 0 | 0.095961 | 318.7305 | 0.048348 | 0 | 0 | 0.096696 | 318.9001 | 0.048716 | 0 | 0 | 0.097432
2017-12-30 19:00 | 281.8375 | 0.84004 |  | 295.9476 | 0 | 0 | 0 | 0 | 304.264 | 0.01697 | 0 | 0 | 0.033941 | 311.0684 | 0.031729 | 0 | 0 | 0.063458 | 311.3204 | 0.032276 | 0 | 0 | 0.064551 | 311.4884 | 0.03264 | 0 | 0 | 0.06528 | 311.7404 | 0.033187 | 0 | 0 | 0.066373 | 311.9924 | 0.033733 | 0 | 0 | 0.067466 | 312.2445 | 0.03428 | 0 | 0 | 0.06856 | 312.5805 | 0.035009 | 0 | 0 | 0.070017 | 312.8325 | 0.035555 | 0 | 0 | 0.071111 | 313.0005 | 0.03592 | 0 | 0 | 0.071839 | 313.2525 | 0.036466 | 0 | 0 | 0.072933 | 313.4205 | 0.036831 | 0 | 0 | 0.073661 | 313.6725 | 0.037377 | 0 | 0 | 0.074755 | 313.9245 | 0.037924 | 0 | 0 | 0.075848 | 314.0926 | 0.038288 | 0 | 0 | 0.076577 | 314.3446 | 0.038835 | 0 | 0 | 0.07767 | 314.5966 | 0.039382 | 0 | 0 | 0.078763 | 314.6806 | 0.039564 | 0 | 0 | 0.079128 | 314.9326 | 0.04011 | 0 | 0 | 0.080221 | 315.1846 | 0.040657 | 0 | 0 | 0.081314 | 315.3526 | 0.041021 | 0 | 0 | 0.082043 | 315.6046 | 0.041568 | 0 | 0 | 0.083136 | 315.7726 | 0.041932 | 0 | 0 | 0.083865 | 315.9406 | 0.042297 | 0 | 0 | 0.084594
2017-12-30 20:00 | 288.6936 | 0.86048 |  | 303.147 | 0.014547 | 0 | 0 | 0.029095 | 311.6657 | 0.033025 | 0 | 0 | 0.066049 | 318.6356 | 0.048142 | 0 | 0 | 0.096285 | 318.8937 | 0.048702 | 0 | 0 | 0.097404 | 319.0658 | 0.049075 | 0 | 0 | 0.098151 | 319.324 | 0.049635 | 0 | 0 | 0.099271 | 319.5821 | 0.050195 | 0 | 0 | 0.10039 | 319.8403 | 0.050755 | 0 | 0 | 0.10151 | 320.1845 | 0.051502 | 0 | 0 | 0.103 | 320.4426 | 0.052062 | 0 | 0 | 0.10412 | 320.6147 | 0.052435 | 0 | 0 | 0.10487 | 320.8728 | 0.052995 | 0 | 0 | 0.10599 | 321.0449 | 0.053368 | 0 | 0 | 0.10674 | 321.3031 | 0.053928 | 0 | 0 | 0.10786 | 321.5612 | 0.054488 | 0 | 0 | 0.10898 | 321.7333 | 0.054861 | 0 | 0 | 0.10972 | 321.9915 | 0.055421 | 0 | 0 | 0.11084 | 322.2496 | 0.055981 | 0 | 0 | 0.11196 | 322.3357 | 0.056168 | 0 | 0 | 0.11234 | 322.5938 | 0.056728 | 0 | 0 | 0.11346 | 322.852 | 0.057288 | 0 | 0 | 0.11458 | 323.024 | 0.057661 | 0 | 0 | 0.11532 | 323.2822 | 0.058221 | 0 | 0 | 0.11644 | 323.4543 | 0.058594 | 0 | 0 | 0.11719 | 323.6264 | 0.058967 | 0 | 0 | 0.11793
2017-12-30 21:00 | 293.6264 | 0.87518 |  | 308.3268 | 0.025782 | 0 | 0 | 0.051565 | 316.9911 | 0.044575 | 0 | 0 | 0.08915 | 324.08 | 0.059951 | 0 | 0 | 0.1199 | 324.3426 | 0.060521 | 0 | 0 | 0.12104 | 324.5176 | 0.0609 | 0 | 0 | 0.1218 | 324.7802 | 0.06147 | 0 | 0 | 0.12294 | 325.0427 | 0.062039 | 0 | 0 | 0.12408 | 325.3053 | 0.062609 | 0 | 0 | 0.12522 | 325.6554 | 0.063368 | 0 | 0 | 0.12674 | 325.9179 | 0.063938 | 0 | 0 | 0.12788 | 326.093 | 0.064317 | 0 | 0 | 0.12863 | 326.3555 | 0.064887 | 0 | 0 | 0.12977 | 326.5305 | 0.065266 | 0 | 0 | 0.13053 | 326.7931 | 0.065836 | 0 | 0 | 0.13167 | 327.0557 | 0.066405 | 0 | 0 | 0.13281 | 327.2307 | 0.066785 | 0 | 0 | 0.13357 | 327.4932 | 0.067354 | 0 | 0 | 0.13471 | 327.7558 | 0.067924 | 0 | 0 | 0.13585 | 327.8433 | 0.068114 | 0 | 0 | 0.13623 | 328.1059 | 0.068683 | 0 | 0 | 0.13737 | 328.3684 | 0.069253 | 0 | 0 | 0.13851 | 328.5435 | 0.069632 | 0 | 0 | 0.13926 | 328.806 | 0.070202 | 0 | 0 | 0.1404 | 328.9811 | 0.070582 | 0 | 0 | 0.14116 | 329.1561 | 0.070961 | 0 | 0 | 0.14192
2017-12-30 22:00 | 307.4391 | 0.91635 |  | 322.8309 | 0.057242 | 0 | 0 | 0.11448 | 331.9028 | 0.076919 | 0 | 0 | 0.15384 | 339.3253 | 0.093018 | 0 | 0 | 0.18604 | 339.6002 | 0.093614 | 0 | 0 | 0.18723 | 339.7835 | 0.094012 | 0 | 0 | 0.18802 | 340.0584 | 0.094608 | 0 | 0 | 0.18922 | 340.3333 | 0.095205 | 0 | 0 | 0.19041 | 340.6082 | 0.095801 | 0 | 0 | 0.1916 | 340.9747 | 0.096596 | 0 | 0 | 0.19319 | 341.2496 | 0.097192 | 0 | 0 | 0.19438 | 341.4329 | 0.09759 | 0 | 0 | 0.19518 | 341.7078 | 0.098186 | 0 | 0 | 0.19637 | 341.8911 | 0.098583 | 0 | 0 | 0.19717 | 342.166 | 0.09918 | 0 | 0 | 0.19836 | 342.4409 | 0.099776 | 0 | 0 | 0.19955 | 342.6242 | 0.10017 | 0 | 0 | 0.20035 | 342.8991 | 0.10077 | 0 | 0 | 0.20154 | 343.174 | 0.10137 | 0 | 0 | 0.20273 | 343.2656 | 0.10156 | 0 | 0 | 0.20313 | 343.5405 | 0.10216 | 0 | 0 | 0.20432 | 343.8154 | 0.10276 | 0 | 0 | 0.20551 | 343.9987 | 0.10315 | 0 | 0 | 0.20631 | 344.2736 | 0.10375 | 0 | 0 | 0.2075 | 344.4569 | 0.10415 | 0 | 0 | 0.2083 | 344.6401 | 0.10455 | 0 | 0 | 0.20909
2017-12-30 23:00 | 302.4896 | 0.9016 |  | 317.6337 | 0.045969 | 0 | 0 | 0.091938 | 326.5595 | 0.065329 | 0 | 0 | 0.13066 | 333.8625 | 0.081169 | 0 | 0 | 0.16234 | 334.133 | 0.081756 | 0 | 0 | 0.16351 | 334.3133 | 0.082147 | 0 | 0 | 0.16429 | 334.5838 | 0.082734 | 0 | 0 | 0.16547 | 334.8542 | 0.08332 | 0 | 0 | 0.16664 | 335.1247 | 0.083907 | 0 | 0 | 0.16781 | 335.4854 | 0.084689 | 0 | 0 | 0.16938 | 335.7558 | 0.085276 | 0 | 0 | 0.17055 | 335.9362 | 0.085667 | 0 | 0 | 0.17133 | 336.2066 | 0.086254 | 0 | 0 | 0.17251 | 336.387 | 0.086645 | 0 | 0 | 0.17329 | 336.6574 | 0.087232 | 0 | 0 | 0.17446 | 336.9279 | 0.087818 | 0 | 0 | 0.17564 | 337.1082 | 0.088209 | 0 | 0 | 0.17642 | 337.3787 | 0.088796 | 0 | 0 | 0.17759 | 337.6492 | 0.089383 | 0 | 0 | 0.17877 | 337.7394 | 0.089578 | 0 | 0 | 0.17916 | 338.0098 | 0.090165 | 0 | 0 | 0.18033 | 338.2803 | 0.090752 | 0 | 0 | 0.1815 | 338.4606 | 0.091143 | 0 | 0 | 0.18229 | 338.7311 | 0.091729 | 0 | 0 | 0.18346 | 338.9114 | 0.092121 | 0 | 0 | 0.18424 | 339.0918 | 0.092512 | 0 | 0 | 0.18502
2017-12-31 | 302.2167 | 0.90079 |  | 317.3471 | 0.045348 | 0 | 0 | 0.090695 | 326.2649 | 0.06469 | 0 | 0 | 0.12938 | 333.5613 | 0.080516 | 0 | 0 | 0.16103 | 333.8315 | 0.081102 | 0 | 0 | 0.1622 | 334.0117 | 0.081493 | 0 | 0 | 0.16299 | 334.2819 | 0.082079 | 0 | 0 | 0.16416 | 334.5522 | 0.082665 | 0 | 0 | 0.16533 | 334.8224 | 0.083251 | 0 | 0 | 0.1665 | 335.1827 | 0.084033 | 0 | 0 | 0.16807 | 335.4529 | 0.084619 | 0 | 0 | 0.16924 | 335.6331 | 0.08501 | 0 | 0 | 0.17002 | 335.9033 | 0.085596 | 0 | 0 | 0.17119 | 336.0835 | 0.085987 | 0 | 0 | 0.17197 | 336.3537 | 0.086573 | 0 | 0 | 0.17315 | 336.624 | 0.087159 | 0 | 0 | 0.17432 | 336.8041 | 0.08755 | 0 | 0 | 0.1751 | 337.0744 | 0.088136 | 0 | 0 | 0.17627 | 337.3446 | 0.088722 | 0 | 0 | 0.17744 | 337.4347 | 0.088917 | 0 | 0 | 0.17783 | 337.7049 | 0.089504 | 0 | 0 | 0.17901 | 337.9751 | 0.09009 | 0 | 0 | 0.18018 | 338.1553 | 0.09048 | 0 | 0 | 0.18096 | 338.4255 | 0.091067 | 0 | 0 | 0.18213 | 338.6057 | 0.091457 | 0 | 0 | 0.18291 | 338.7858 | 0.091848 | 0 | 0 | 0.1837
2017-12-31 01:00 | 301.6323 | 0.89904 |  | 316.7334 | 0.044016 | 0 | 0 | 0.088033 | 325.634 | 0.063322 | 0 | 0 | 0.12664 | 332.9162 | 0.079117 | 0 | 0 | 0.15823 | 333.1859 | 0.079702 | 0 | 0 | 0.1594 | 333.3657 | 0.080092 | 0 | 0 | 0.16018 | 333.6355 | 0.080677 | 0 | 0 | 0.16135 | 333.9052 | 0.081262 | 0 | 0 | 0.16252 | 334.1749 | 0.081847 | 0 | 0 | 0.16369 | 334.5345 | 0.082627 | 0 | 0 | 0.16525 | 334.8042 | 0.083212 | 0 | 0 | 0.16642 | 334.984 | 0.083602 | 0 | 0 | 0.1672 | 335.2537 | 0.084187 | 0 | 0 | 0.16837 | 335.4335 | 0.084577 | 0 | 0 | 0.16915 | 335.7033 | 0.085162 | 0 | 0 | 0.17032 | 335.973 | 0.085747 | 0 | 0 | 0.17149 | 336.1528 | 0.086137 | 0 | 0 | 0.17227 | 336.4225 | 0.086722 | 0 | 0 | 0.17344 | 336.6922 | 0.087307 | 0 | 0 | 0.17461 | 336.7821 | 0.087502 | 0 | 0 | 0.175 | 337.0518 | 0.088087 | 0 | 0 | 0.17617 | 337.3215 | 0.088672 | 0 | 0 | 0.17734 | 337.5013 | 0.089062 | 0 | 0 | 0.17812 | 337.7711 | 0.089647 | 0 | 0 | 0.17929 | 337.9509 | 0.090037 | 0 | 0 | 0.18007 | 338.1307 | 0.090427 | 0 | 0 | 0.18085
2017-12-31 02:00 | 294.9799 | 0.87922 |  | 309.748 | 0.028865 | 0 | 0 | 0.05773 | 318.4523 | 0.047745 | 0 | 0 | 0.095489 | 325.5739 | 0.063192 | 0 | 0 | 0.12638 | 325.8377 | 0.063764 | 0 | 0 | 0.12753 | 326.0135 | 0.064145 | 0 | 0 | 0.12829 | 326.2773 | 0.064717 | 0 | 0 | 0.12943 | 326.5411 | 0.065289 | 0 | 0 | 0.13058 | 326.8048 | 0.065861 | 0 | 0 | 0.13172 | 327.1565 | 0.066624 | 0 | 0 | 0.13325 | 327.4203 | 0.067196 | 0 | 0 | 0.13439 | 327.5961 | 0.067578 | 0 | 0 | 0.13516 | 327.8599 | 0.06815 | 0 | 0 | 0.1363 | 328.0357 | 0.068531 | 0 | 0 | 0.13706 | 328.2995 | 0.069103 | 0 | 0 | 0.13821 | 328.5633 | 0.069675 | 0 | 0 | 0.13935 | 328.7391 | 0.070057 | 0 | 0 | 0.14011 | 329.0029 | 0.070629 | 0 | 0 | 0.14126 | 329.2666 | 0.071201 | 0 | 0 | 0.1424 | 329.3546 | 0.071392 | 0 | 0 | 0.14278 | 329.6183 | 0.071964 | 0 | 0 | 0.14393 | 329.8821 | 0.072536 | 0 | 0 | 0.14507 | 330.0579 | 0.072917 | 0 | 0 | 0.14583 | 330.3217 | 0.073489 | 0 | 0 | 0.14698 | 330.4975 | 0.073871 | 0 | 0 | 0.14774 | 330.6734 | 0.074252 | 0 | 0 | 0.1485
2017-12-31 03:00 | 293.5723 | 0.87502 |  | 308.2699 | 0.025659 | 0 | 0 | 0.051318 | 316.9326 | 0.044448 | 0 | 0 | 0.088897 | 324.0203 | 0.059822 | 0 | 0 | 0.11964 | 324.2828 | 0.060391 | 0 | 0 | 0.12078 | 324.4578 | 0.060771 | 0 | 0 | 0.12154 | 324.7203 | 0.06134 | 0 | 0 | 0.12268 | 324.9828 | 0.061909 | 0 | 0 | 0.12382 | 325.2453 | 0.062479 | 0 | 0 | 0.12496 | 325.5953 | 0.063238 | 0 | 0 | 0.12648 | 325.8578 | 0.063807 | 0 | 0 | 0.12761 | 326.0328 | 0.064187 | 0 | 0 | 0.12837 | 326.2953 | 0.064756 | 0 | 0 | 0.12951 | 326.4703 | 0.065136 | 0 | 0 | 0.13027 | 326.7328 | 0.065705 | 0 | 0 | 0.13141 | 326.9953 | 0.066275 | 0 | 0 | 0.13255 | 327.1703 | 0.066654 | 0 | 0 | 0.13331 | 327.4328 | 0.067223 | 0 | 0 | 0.13445 | 327.6953 | 0.067793 | 0 | 0 | 0.13559 | 327.7829 | 0.067983 | 0 | 0 | 0.13597 | 328.0454 | 0.068552 | 0 | 0 | 0.1371 | 328.3079 | 0.069121 | 0 | 0 | 0.13824 | 328.4829 | 0.069501 | 0 | 0 | 0.139 | 328.7454 | 0.07007 | 0 | 0 | 0.14014 | 328.9204 | 0.07045 | 0 | 0 | 0.1409 | 329.0954 | 0.07083 | 0 | 0 | 0.14166
2017-12-31 04:00 | 304.47 | 0.9075 |  | 319.7132 | 0.05048 | 0 | 0 | 0.10096 | 328.6975 | 0.069966 | 0 | 0 | 0.13993 | 336.0482 | 0.08591 | 0 | 0 | 0.17182 | 336.3205 | 0.086501 | 0 | 0 | 0.173 | 336.502 | 0.086894 | 0 | 0 | 0.17379 | 336.7742 | 0.087485 | 0 | 0 | 0.17497 | 337.0465 | 0.088075 | 0 | 0 | 0.17615 | 337.3187 | 0.088666 | 0 | 0 | 0.17733 | 337.6817 | 0.089453 | 0 | 0 | 0.17891 | 337.954 | 0.090044 | 0 | 0 | 0.18009 | 338.1355 | 0.090437 | 0 | 0 | 0.18087 | 338.4077 | 0.091028 | 0 | 0 | 0.18206 | 338.5892 | 0.091422 | 0 | 0 | 0.18284 | 338.8615 | 0.092012 | 0 | 0 | 0.18402 | 339.1337 | 0.092603 | 0 | 0 | 0.18521 | 339.3152 | 0.092996 | 0 | 0 | 0.18599 | 339.5875 | 0.093587 | 0 | 0 | 0.18717 | 339.8597 | 0.094177 | 0 | 0 | 0.18835 | 339.9505 | 0.094374 | 0 | 0 | 0.18875 | 340.2227 | 0.094965 | 0 | 0 | 0.18993 | 340.495 | 0.095555 | 0 | 0 | 0.19111 | 340.6765 | 0.095949 | 0 | 0 | 0.1919 | 340.9487 | 0.096539 | 0 | 0 | 0.19308 | 341.1302 | 0.096933 | 0 | 0 | 0.19387 | 341.3117 | 0.097327 | 0 | 0 | 0.19465
2017-12-31 05:00 | 305.6667 | 0.91107 |  | 320.9698 | 0.053205 | 0 | 0 | 0.10641 | 329.9894 | 0.072769 | 0 | 0 | 0.14554 | 337.3691 | 0.088775 | 0 | 0 | 0.17755 | 337.6424 | 0.089368 | 0 | 0 | 0.17874 | 337.8246 | 0.089763 | 0 | 0 | 0.17953 | 338.0979 | 0.090356 | 0 | 0 | 0.18071 | 338.3712 | 0.090949 | 0 | 0 | 0.1819 | 338.6446 | 0.091542 | 0 | 0 | 0.18308 | 339.009 | 0.092332 | 0 | 0 | 0.18466 | 339.2823 | 0.092925 | 0 | 0 | 0.18585 | 339.4645 | 0.09332 | 0 | 0 | 0.18664 | 339.7378 | 0.093913 | 0 | 0 | 0.18783 | 339.9201 | 0.094308 | 0 | 0 | 0.18862 | 340.1934 | 0.094901 | 0 | 0 | 0.1898 | 340.4667 | 0.095494 | 0 | 0 | 0.19099 | 340.6489 | 0.095889 | 0 | 0 | 0.19178 | 340.9222 | 0.096482 | 0 | 0 | 0.19296 | 341.1956 | 0.097075 | 0 | 0 | 0.19415 | 341.2867 | 0.097272 | 0 | 0 | 0.19454 | 341.56 | 0.097865 | 0 | 0 | 0.19573 | 341.8333 | 0.098458 | 0 | 0 | 0.19692 | 342.0155 | 0.098853 | 0 | 0 | 0.19771 | 342.2888 | 0.099446 | 0 | 0 | 0.19889 | 342.4711 | 0.099841 | 0 | 0 | 0.19968 | 342.6533 | 0.10024 | 0 | 0 | 0.20047
2017-12-31 06:00 | 299.5974 | 0.89298 |  | 314.5966 | 0.039382 | 0 | 0 | 0.078763 | 323.4371 | 0.058557 | 0 | 0 | 0.11711 | 330.6703 | 0.074245 | 0 | 0 | 0.14849 | 330.9382 | 0.074827 | 0 | 0 | 0.14965 | 331.1168 | 0.075214 | 0 | 0 | 0.15043 | 331.3847 | 0.075795 | 0 | 0 | 0.15159 | 331.6525 | 0.076376 | 0 | 0 | 0.15275 | 331.9204 | 0.076957 | 0 | 0 | 0.15391 | 332.2776 | 0.077732 | 0 | 0 | 0.15546 | 332.5455 | 0.078313 | 0 | 0 | 0.15663 | 332.7241 | 0.0787 | 0 | 0 | 0.1574 | 332.992 | 0.079281 | 0 | 0 | 0.15856 | 333.1706 | 0.079669 | 0 | 0 | 0.15934 | 333.4385 | 0.08025 | 0 | 0 | 0.1605 | 333.7064 | 0.080831 | 0 | 0 | 0.16166 | 333.885 | 0.081218 | 0 | 0 | 0.16244 | 334.1529 | 0.081799 | 0 | 0 | 0.1636 | 334.4208 | 0.08238 | 0 | 0 | 0.16476 | 334.5101 | 0.082574 | 0 | 0 | 0.16515 | 334.778 | 0.083155 | 0 | 0 | 0.16631 | 335.0459 | 0.083736 | 0 | 0 | 0.16747 | 335.2245 | 0.084123 | 0 | 0 | 0.16825 | 335.4924 | 0.084705 | 0 | 0 | 0.16941 | 335.671 | 0.085092 | 0 | 0 | 0.17018 | 335.8495 | 0.085479 | 0 | 0 | 0.17096
2017-12-31 07:00 | 298.5973 | 0.89 |  | 313.5465 | 0.037104 | 0 | 0 | 0.074208 | 322.3575 | 0.056215 | 0 | 0 | 0.11243 | 329.5665 | 0.071851 | 0 | 0 | 0.1437 | 329.8335 | 0.07243 | 0 | 0 | 0.14486 | 330.0115 | 0.072817 | 0 | 0 | 0.14563 | 330.2785 | 0.073396 | 0 | 0 | 0.14679 | 330.5455 | 0.073975 | 0 | 0 | 0.14795 | 330.8125 | 0.074554 | 0 | 0 | 0.14911 | 331.1685 | 0.075326 | 0 | 0 | 0.15065 | 331.4355 | 0.075905 | 0 | 0 | 0.15181 | 331.6135 | 0.076291 | 0 | 0 | 0.15258 | 331.8805 | 0.07687 | 0 | 0 | 0.15374 | 332.0585 | 0.077257 | 0 | 0 | 0.15451 | 332.3255 | 0.077836 | 0 | 0 | 0.15567 | 332.5925 | 0.078415 | 0 | 0 | 0.15683 | 332.7705 | 0.078801 | 0 | 0 | 0.1576 | 333.0375 | 0.07938 | 0 | 0 | 0.15876 | 333.3045 | 0.079959 | 0 | 0 | 0.15992 | 333.3935 | 0.080152 | 0 | 0 | 0.1603 | 333.6605 | 0.080731 | 0 | 0 | 0.16146 | 333.9275 | 0.08131 | 0 | 0 | 0.16262 | 334.1055 | 0.081696 | 0 | 0 | 0.16339 | 334.3725 | 0.082276 | 0 | 0 | 0.16455 | 334.5505 | 0.082662 | 0 | 0 | 0.16532 | 334.7285 | 0.083048 | 0 | 0 | 0.1661
2017-12-31 08:00 | 289.199 | 0.86199 |  | 303.6776 | 0.015698 | 0 | 0 | 0.031397 | 312.2113 | 0.034208 | 0 | 0 | 0.068416 | 319.1934 | 0.049352 | 0 | 0 | 0.098704 | 319.452 | 0.049913 | 0 | 0 | 0.099826 | 319.6244 | 0.050287 | 0 | 0 | 0.10057 | 319.883 | 0.050848 | 0 | 0 | 0.1017 | 320.1416 | 0.051409 | 0 | 0 | 0.10282 | 320.4002 | 0.05197 | 0 | 0 | 0.10394 | 320.745 | 0.052717 | 0 | 0 | 0.10543 | 321.0036 | 0.053278 | 0 | 0 | 0.10656 | 321.1759 | 0.053652 | 0 | 0 | 0.1073 | 321.4345 | 0.054213 | 0 | 0 | 0.10843 | 321.6069 | 0.054587 | 0 | 0 | 0.10917 | 321.8655 | 0.055148 | 0 | 0 | 0.1103 | 322.1241 | 0.055709 | 0 | 0 | 0.11142 | 322.2965 | 0.056083 | 0 | 0 | 0.11217 | 322.5551 | 0.056644 | 0 | 0 | 0.11329 | 322.8137 | 0.057205 | 0 | 0 | 0.11441 | 322.8999 | 0.057392 | 0 | 0 | 0.11478 | 323.1585 | 0.057952 | 0 | 0 | 0.1159 | 323.4171 | 0.058513 | 0 | 0 | 0.11703 | 323.5895 | 0.058887 | 0 | 0 | 0.11777 | 323.8481 | 0.059448 | 0 | 0 | 0.1189 | 324.0205 | 0.059822 | 0 | 0 | 0.11964 | 324.1929 | 0.060196 | 0 | 0 | 0.12039
2017-12-31 09:00 | 293.697 | 0.87539 |  | 308.4009 | 0.025943 | 0 | 0 | 0.051886 | 317.0673 | 0.044741 | 0 | 0 | 0.089481 | 324.158 | 0.06012 | 0 | 0 | 0.12024 | 324.4206 | 0.06069 | 0 | 0 | 0.12138 | 324.5957 | 0.06107 | 0 | 0 | 0.12214 | 324.8583 | 0.061639 | 0 | 0 | 0.12328 | 325.1209 | 0.062209 | 0 | 0 | 0.12442 | 325.3835 | 0.062778 | 0 | 0 | 0.12556 | 325.7337 | 0.063538 | 0 | 0 | 0.12708 | 325.9963 | 0.064108 | 0 | 0 | 0.12822 | 326.1714 | 0.064487 | 0 | 0 | 0.12897 | 326.434 | 0.065057 | 0 | 0 | 0.13011 | 326.6091 | 0.065437 | 0 | 0 | 0.13087 | 326.8717 | 0.066006 | 0 | 0 | 0.13201 | 327.1343 | 0.066576 | 0 | 0 | 0.13315 | 327.3094 | 0.066956 | 0 | 0 | 0.13391 | 327.572 | 0.067525 | 0 | 0 | 0.13505 | 327.8346 | 0.068095 | 0 | 0 | 0.13619 | 327.9222 | 0.068285 | 0 | 0 | 0.13657 | 328.1848 | 0.068854 | 0 | 0 | 0.13771 | 328.4474 | 0.069424 | 0 | 0 | 0.13885 | 328.6225 | 0.069804 | 0 | 0 | 0.13961 | 328.8851 | 0.070373 | 0 | 0 | 0.14075 | 329.0602 | 0.070753 | 0 | 0 | 0.14151 | 329.2352 | 0.071133 | 0 | 0 | 0.14227
2017-12-31 10:00 | 294.5778 | 0.87802 |  | 309.3257 | 0.027949 | 0 | 0 | 0.055898 | 318.0181 | 0.046803 | 0 | 0 | 0.093606 | 325.13 | 0.062229 | 0 | 0 | 0.12446 | 325.3934 | 0.0628 | 0 | 0 | 0.1256 | 325.5691 | 0.063181 | 0 | 0 | 0.12636 | 325.8325 | 0.063752 | 0 | 0 | 0.1275 | 326.0959 | 0.064324 | 0 | 0 | 0.12865 | 326.3593 | 0.064895 | 0 | 0 | 0.12979 | 326.7105 | 0.065657 | 0 | 0 | 0.13131 | 326.9739 | 0.066228 | 0 | 0 | 0.13246 | 327.1495 | 0.066609 | 0 | 0 | 0.13322 | 327.4129 | 0.06718 | 0 | 0 | 0.13436 | 327.5885 | 0.067561 | 0 | 0 | 0.13512 | 327.8519 | 0.068132 | 0 | 0 | 0.13626 | 328.1153 | 0.068704 | 0 | 0 | 0.13741 | 328.2909 | 0.069085 | 0 | 0 | 0.13817 | 328.5543 | 0.069656 | 0 | 0 | 0.13931 | 328.8177 | 0.070227 | 0 | 0 | 0.14045 | 328.9055 | 0.070418 | 0 | 0 | 0.14084 | 329.1689 | 0.070989 | 0 | 0 | 0.14198 | 329.4323 | 0.07156 | 0 | 0 | 0.14312 | 329.6079 | 0.071941 | 0 | 0 | 0.14388 | 329.8713 | 0.072513 | 0 | 0 | 0.14503 | 330.0469 | 0.072893 | 0 | 0 | 0.14579 | 330.2225 | 0.073274 | 0 | 0 | 0.14655
2017-12-31 11:00 | 305.716 | 0.91122 |  | 321.0216 | 0.053317 | 0 | 0 | 0.10663 | 330.0426 | 0.072884 | 0 | 0 | 0.14577 | 337.4234 | 0.088893 | 0 | 0 | 0.17779 | 337.6968 | 0.089486 | 0 | 0 | 0.17897 | 337.8791 | 0.089881 | 0 | 0 | 0.17976 | 338.1524 | 0.090474 | 0 | 0 | 0.18095 | 338.4258 | 0.091067 | 0 | 0 | 0.18213 | 338.6991 | 0.09166 | 0 | 0 | 0.18332 | 339.0636 | 0.092451 | 0 | 0 | 0.1849 | 339.337 | 0.093044 | 0 | 0 | 0.18609 | 339.5192 | 0.093439 | 0 | 0 | 0.18688 | 339.7926 | 0.094032 | 0 | 0 | 0.18806 | 339.9749 | 0.094427 | 0 | 0 | 0.18885 | 340.2482 | 0.09502 | 0 | 0 | 0.19004 | 340.5216 | 0.095613 | 0 | 0 | 0.19123 | 340.7038 | 0.096008 | 0 | 0 | 0.19202 | 340.9772 | 0.096601 | 0 | 0 | 0.1932 | 341.2506 | 0.097194 | 0 | 0 | 0.19439 | 341.3417 | 0.097392 | 0 | 0 | 0.19478 | 341.615 | 0.097985 | 0 | 0 | 0.19597 | 341.8884 | 0.098578 | 0 | 0 | 0.19716 | 342.0707 | 0.098973 | 0 | 0 | 0.19795 | 342.344 | 0.099566 | 0 | 0 | 0.19913 | 342.5263 | 0.099961 | 0 | 0 | 0.19992 | 342.7085 | 0.10036 | 0 | 0 | 0.20071
2017-12-31 12:00 | 307.1692 | 0.91555 |  | 322.5476 | 0.056627 | 0 | 0 | 0.11325 | 331.6115 | 0.076287 | 0 | 0 | 0.15257 | 339.0274 | 0.092372 | 0 | 0 | 0.18474 | 339.3021 | 0.092968 | 0 | 0 | 0.18594 | 339.4852 | 0.093365 | 0 | 0 | 0.18673 | 339.7599 | 0.093961 | 0 | 0 | 0.18792 | 340.0345 | 0.094557 | 0 | 0 | 0.18911 | 340.3092 | 0.095152 | 0 | 0 | 0.1903 | 340.6754 | 0.095947 | 0 | 0 | 0.19189 | 340.9501 | 0.096542 | 0 | 0 | 0.19308 | 341.1332 | 0.09694 | 0 | 0 | 0.19388 | 341.4078 | 0.097535 | 0 | 0 | 0.19507 | 341.591 | 0.097932 | 0 | 0 | 0.19586 | 341.8656 | 0.098528 | 0 | 0 | 0.19706 | 342.1403 | 0.099124 | 0 | 0 | 0.19825 | 342.3234 | 0.099521 | 0 | 0 | 0.19904 | 342.5981 | 0.10012 | 0 | 0 | 0.20023 | 342.8727 | 0.10071 | 0 | 0 | 0.20143 | 342.9643 | 0.10091 | 0 | 0 | 0.20182 | 343.2389 | 0.10151 | 0 | 0 | 0.20301 | 343.5136 | 0.1021 | 0 | 0 | 0.20421 | 343.6967 | 0.1025 | 0 | 0 | 0.205 | 343.9714 | 0.1031 | 0 | 0 | 0.20619 | 344.1545 | 0.10349 | 0 | 0 | 0.20699 | 344.3376 | 0.10389 | 0 | 0 | 0.20778
2017-12-31 13:00 | 308.5362 | 0.91962 |  | 323.983 | 0.059741 | 0 | 0 | 0.11948 | 333.0873 | 0.079488 | 0 | 0 | 0.15898 | 340.5362 | 0.095645 | 0 | 0 | 0.19129 | 340.8121 | 0.096243 | 0 | 0 | 0.19249 | 340.996 | 0.096642 | 0 | 0 | 0.19328 | 341.2719 | 0.09724 | 0 | 0 | 0.19448 | 341.5478 | 0.097839 | 0 | 0 | 0.19568 | 341.8237 | 0.098437 | 0 | 0 | 0.19687 | 342.1916 | 0.099235 | 0 | 0 | 0.19847 | 342.4674 | 0.099834 | 0 | 0 | 0.19967 | 342.6514 | 0.10023 | 0 | 0 | 0.20046 | 342.9273 | 0.10083 | 0 | 0 | 0.20166 | 343.1112 | 0.10123 | 0 | 0 | 0.20246 | 343.3871 | 0.10183 | 0 | 0 | 0.20366 | 343.663 | 0.10243 | 0 | 0 | 0.20485 | 343.8469 | 0.10283 | 0 | 0 | 0.20565 | 344.1228 | 0.10342 | 0 | 0 | 0.20685 | 344.3987 | 0.10402 | 0 | 0 | 0.20804 | 344.4906 | 0.10422 | 0 | 0 | 0.20844 | 344.7665 | 0.10482 | 0 | 0 | 0.20964 | 345.0424 | 0.10542 | 0 | 0 | 0.21084 | 345.2263 | 0.10582 | 0 | 0 | 0.21164 | 345.5022 | 0.10642 | 0 | 0 | 0.21283 | 345.6861 | 0.10681 | 0 | 0 | 0.21363 | 345.87 | 0.10721 | 0 | 0 | 0.21443
2017-12-31 14:00 | 310.3942 | 0.92516 |  | 325.934 | 0.063972 | 0 | 0 | 0.12794 | 335.0931 | 0.083839 | 0 | 0 | 0.16768 | 342.5869 | 0.10009 | 0 | 0 | 0.20019 | 342.8644 | 0.10069 | 0 | 0 | 0.20139 | 343.0495 | 0.1011 | 0 | 0 | 0.20219 | 343.327 | 0.1017 | 0 | 0 | 0.2034 | 343.6046 | 0.1023 | 0 | 0 | 0.2046 | 343.8821 | 0.1029 | 0 | 0 | 0.2058 | 344.2522 | 0.1037 | 0 | 0 | 0.20741 | 344.5297 | 0.10431 | 0 | 0 | 0.20861 | 344.7147 | 0.10471 | 0 | 0 | 0.20942 | 344.9923 | 0.10531 | 0 | 0 | 0.21062 | 345.1773 | 0.10571 | 0 | 0 | 0.21142 | 345.4549 | 0.10631 | 0 | 0 | 0.21263 | 345.7324 | 0.10692 | 0 | 0 | 0.21383 | 345.9175 | 0.10732 | 0 | 0 | 0.21463 | 346.195 | 0.10792 | 0 | 0 | 0.21584 | 346.4725 | 0.10852 | 0 | 0 | 0.21704 | 346.5651 | 0.10872 | 0 | 0 | 0.21744 | 346.8426 | 0.10932 | 0 | 0 | 0.21865 | 347.1202 | 0.10993 | 0 | 0 | 0.21985 | 347.3052 | 0.11033 | 0 | 0 | 0.22065 | 347.5827 | 0.11093 | 0 | 0 | 0.22186 | 347.7678 | 0.11133 | 0 | 0 | 0.22266 | 347.9528 | 0.11173 | 0 | 0 | 0.22346
2017-12-31 15:00 | 312.9755 | 0.93285 |  | 328.6446 | 0.069852 | 0 | 0 | 0.1397 | 337.8798 | 0.089883 | 0 | 0 | 0.17977 | 345.436 | 0.10627 | 0 | 0 | 0.21254 | 345.7158 | 0.10688 | 0 | 0 | 0.21376 | 345.9024 | 0.10728 | 0 | 0 | 0.21457 | 346.1822 | 0.10789 | 0 | 0 | 0.21578 | 346.4621 | 0.1085 | 0 | 0 | 0.217 | 346.742 | 0.1091 | 0 | 0 | 0.21821 | 347.1151 | 0.10991 | 0 | 0 | 0.21983 | 347.395 | 0.11052 | 0 | 0 | 0.22104 | 347.5815 | 0.11093 | 0 | 0 | 0.22185 | 347.8614 | 0.11153 | 0 | 0 | 0.22307 | 348.048 | 0.11194 | 0 | 0 | 0.22388 | 348.3278 | 0.11254 | 0 | 0 | 0.22509 | 348.6077 | 0.11315 | 0 | 0 | 0.2263 | 348.7942 | 0.11356 | 0 | 0 | 0.22711 | 349.0741 | 0.11416 | 0 | 0 | 0.22833 | 349.3539 | 0.11477 | 0 | 0 | 0.22954 | 349.4472 | 0.11497 | 0 | 0 | 0.22995 | 349.7271 | 0.11558 | 0 | 0 | 0.23116 | 350.0069 | 0.11619 | 0 | 0 | 0.23237 | 350.1935 | 0.11659 | 0 | 0 | 0.23318 | 350.4734 | 0.1172 | 0 | 0 | 0.2344 | 350.6599 | 0.1176 | 0 | 0 | 0.23521 | 350.8465 | 0.11801 | 0 | 0 | 0.23602
2017-12-31 16:00 | 313.1178 | 0.93328 |  | 328.7939 | 0.070176 | 0 | 0 | 0.14035 | 338.0334 | 0.090216 | 0 | 0 | 0.18043 | 345.593 | 0.10661 | 0 | 0 | 0.21323 | 345.8729 | 0.10722 | 0 | 0 | 0.21444 | 346.0596 | 0.10762 | 0 | 0 | 0.21525 | 346.3396 | 0.10823 | 0 | 0 | 0.21646 | 346.6196 | 0.10884 | 0 | 0 | 0.21768 | 346.8995 | 0.10945 | 0 | 0 | 0.21889 | 347.2729 | 0.11026 | 0 | 0 | 0.22051 | 347.5528 | 0.11086 | 0 | 0 | 0.22173 | 347.7395 | 0.11127 | 0 | 0 | 0.22254 | 348.0195 | 0.11188 | 0 | 0 | 0.22375 | 348.2061 | 0.11228 | 0 | 0 | 0.22456 | 348.4861 | 0.11289 | 0 | 0 | 0.22578 | 348.7661 | 0.1135 | 0 | 0 | 0.22699 | 348.9528 | 0.1139 | 0 | 0 | 0.2278 | 349.2327 | 0.11451 | 0 | 0 | 0.22901 | 349.5127 | 0.11511 | 0 | 0 | 0.23023 | 349.6061 | 0.11532 | 0 | 0 | 0.23063 | 349.886 | 0.11592 | 0 | 0 | 0.23185 | 350.166 | 0.11653 | 0 | 0 | 0.23306 | 350.3527 | 0.11694 | 0 | 0 | 0.23387 | 350.6327 | 0.11754 | 0 | 0 | 0.23509 | 350.8193 | 0.11795 | 0 | 0 | 0.2359 | 351.006 | 0.11835 | 0 | 0 | 0.23671
2017-12-31 17:00 | 314.0141 | 0.93595 |  | 329.7351 | 0.072217 | 0 | 0 | 0.14443 | 339.001 | 0.092315 | 0 | 0 | 0.18463 | 346.5822 | 0.10876 | 0 | 0 | 0.21752 | 346.863 | 0.10937 | 0 | 0 | 0.21873 | 347.0502 | 0.10977 | 0 | 0 | 0.21955 | 347.3309 | 0.11038 | 0 | 0 | 0.22076 | 347.6117 | 0.11099 | 0 | 0 | 0.22198 | 347.8925 | 0.1116 | 0 | 0 | 0.2232 | 348.2669 | 0.11241 | 0 | 0 | 0.22483 | 348.5477 | 0.11302 | 0 | 0 | 0.22604 | 348.7349 | 0.11343 | 0 | 0 | 0.22686 | 349.0157 | 0.11404 | 0 | 0 | 0.22807 | 349.2028 | 0.11444 | 0 | 0 | 0.22889 | 349.4836 | 0.11505 | 0 | 0 | 0.2301 | 349.7644 | 0.11566 | 0 | 0 | 0.23132 | 349.9516 | 0.11607 | 0 | 0 | 0.23213 | 350.2324 | 0.11668 | 0 | 0 | 0.23335 | 350.5132 | 0.11728 | 0 | 0 | 0.23457 | 350.6068 | 0.11749 | 0 | 0 | 0.23498 | 350.8876 | 0.1181 | 0 | 0 | 0.23619 | 351.1683 | 0.11871 | 0 | 0 | 0.23741 | 351.3555 | 0.11911 | 0 | 0 | 0.23822 | 351.6363 | 0.11972 | 0 | 0 | 0.23944 | 351.8235 | 0.12013 | 0 | 0 | 0.24025 | 352.0107 | 0.12053 | 0 | 0 | 0.24107
2017-12-31 18:00 | 324.0108 | 0.96575 |  | 340.2323 | 0.094985 | 0 | 0 | 0.18997 | 349.7932 | 0.11572 | 0 | 0 | 0.23145 | 357.6157 | 0.13269 | 0 | 0 | 0.26538 | 357.9054 | 0.13332 | 0 | 0 | 0.26664 | 358.0986 | 0.13374 | 0 | 0 | 0.26747 | 358.3883 | 0.13437 | 0 | 0 | 0.26873 | 358.678 | 0.13499 | 0 | 0 | 0.26999 | 358.9677 | 0.13562 | 0 | 0 | 0.27125 | 359.354 | 0.13646 | 0 | 0 | 0.27292 | 359.6438 | 0.13709 | 0 | 0 | 0.27418 | 359.8369 | 0.13751 | 0 | 0 | 0.27502 | 360.1266 | 0.13814 | 0 | 0 | 0.27627 | 360.3198 | 0.13856 | 0 | 0 | 0.27711 | 360.6095 | 0.13918 | 0 | 0 | 0.27837 | 360.8992 | 0.13981 | 0 | 0 | 0.27962 | 361.0924 | 0.14023 | 0 | 0 | 0.28046 | 361.3821 | 0.14086 | 0 | 0 | 0.28172 | 361.6718 | 0.14149 | 0 | 0 | 0.28298 | 361.7684 | 0.1417 | 0 | 0 | 0.28339 | 362.0581 | 0.14233 | 0 | 0 | 0.28465 | 362.3479 | 0.14295 | 0 | 0 | 0.28591 | 362.541 | 0.14337 | 0 | 0 | 0.28675 | 362.8307 | 0.144 | 0 | 0 | 0.288 | 363.0239 | 0.14442 | 0 | 0 | 0.28884 | 363.217 | 0.14484 | 0 | 0 | 0.28968
2017-12-31 19:00 | 320.8086 | 0.9562 |  | 336.8698 | 0.087692 | 0 | 0 | 0.17538 | 346.3362 | 0.10822 | 0 | 0 | 0.21645 | 354.0814 | 0.12502 | 0 | 0 | 0.25005 | 354.3683 | 0.12565 | 0 | 0 | 0.25129 | 354.5595 | 0.12606 | 0 | 0 | 0.25212 | 354.8464 | 0.12668 | 0 | 0 | 0.25337 | 355.1332 | 0.12731 | 0 | 0 | 0.25461 | 355.4201 | 0.12793 | 0 | 0 | 0.25586 | 355.8026 | 0.12876 | 0 | 0 | 0.25751 | 356.0894 | 0.12938 | 0 | 0 | 0.25876 | 356.2807 | 0.12979 | 0 | 0 | 0.25959 | 356.5675 | 0.13042 | 0 | 0 | 0.26083 | 356.7588 | 0.13083 | 0 | 0 | 0.26166 | 357.0456 | 0.13145 | 0 | 0 | 0.26291 | 357.3325 | 0.13208 | 0 | 0 | 0.26415 | 357.5237 | 0.13249 | 0 | 0 | 0.26498 | 357.8106 | 0.13311 | 0 | 0 | 0.26623 | 358.0974 | 0.13373 | 0 | 0 | 0.26747 | 358.1931 | 0.13394 | 0 | 0 | 0.26788 | 358.4799 | 0.13456 | 0 | 0 | 0.26913 | 358.7668 | 0.13519 | 0 | 0 | 0.27037 | 358.958 | 0.1356 | 0 | 0 | 0.2712 | 359.2449 | 0.13622 | 0 | 0 | 0.27245 | 359.4361 | 0.13664 | 0 | 0 | 0.27328 | 359.6274 | 0.13705 | 0 | 0 | 0.27411
2017-12-31 20:00 | 314.2807 | 0.93674 |  | 330.0151 | 0.072824 | 0 | 0 | 0.14565 | 339.2889 | 0.092939 | 0 | 0 | 0.18588 | 346.8765 | 0.1094 | 0 | 0 | 0.21879 | 347.1575 | 0.11001 | 0 | 0 | 0.22001 | 347.3449 | 0.11041 | 0 | 0 | 0.22083 | 347.6259 | 0.11102 | 0 | 0 | 0.22204 | 347.9069 | 0.11163 | 0 | 0 | 0.22326 | 348.1879 | 0.11224 | 0 | 0 | 0.22448 | 348.5626 | 0.11305 | 0 | 0 | 0.22611 | 348.8437 | 0.11366 | 0 | 0 | 0.22733 | 349.031 | 0.11407 | 0 | 0 | 0.22814 | 349.312 | 0.11468 | 0 | 0 | 0.22936 | 349.4994 | 0.11509 | 0 | 0 | 0.23017 | 349.7804 | 0.1157 | 0 | 0 | 0.23139 | 350.0614 | 0.1163 | 0 | 0 | 0.23261 | 350.2488 | 0.11671 | 0 | 0 | 0.23342 | 350.5298 | 0.11732 | 0 | 0 | 0.23464 | 350.8108 | 0.11793 | 0 | 0 | 0.23586 | 350.9045 | 0.11813 | 0 | 0 | 0.23627 | 351.1855 | 0.11874 | 0 | 0 | 0.23749 | 351.4666 | 0.11935 | 0 | 0 | 0.23871 | 351.6539 | 0.11976 | 0 | 0 | 0.23952 | 351.9349 | 0.12037 | 0 | 0 | 0.24074 | 352.1223 | 0.12077 | 0 | 0 | 0.24155 | 352.3096 | 0.12118 | 0 | 0 | 0.24236
2017-12-31 21:00 | 319.6373 | 0.95271 |  | 335.6399 | 0.085025 | 0 | 0 | 0.17005 | 345.0717 | 0.10548 | 0 | 0 | 0.21096 | 352.7887 | 0.12222 | 0 | 0 | 0.24444 | 353.0745 | 0.12284 | 0 | 0 | 0.24568 | 353.265 | 0.12325 | 0 | 0 | 0.24651 | 353.5508 | 0.12387 | 0 | 0 | 0.24775 | 353.8367 | 0.12449 | 0 | 0 | 0.24899 | 354.1225 | 0.12511 | 0 | 0 | 0.25023 | 354.5036 | 0.12594 | 0 | 0 | 0.25188 | 354.7894 | 0.12656 | 0 | 0 | 0.25312 | 354.9799 | 0.12697 | 0 | 0 | 0.25395 | 355.2657 | 0.12759 | 0 | 0 | 0.25519 | 355.4563 | 0.12801 | 0 | 0 | 0.25601 | 355.7421 | 0.12863 | 0 | 0 | 0.25725 | 356.0279 | 0.12925 | 0 | 0 | 0.25849 | 356.2184 | 0.12966 | 0 | 0 | 0.25932 | 356.5042 | 0.13028 | 0 | 0 | 0.26056 | 356.7901 | 0.1309 | 0 | 0 | 0.2618 | 356.8853 | 0.13111 | 0 | 0 | 0.26221 | 357.1711 | 0.13173 | 0 | 0 | 0.26345 | 357.457 | 0.13235 | 0 | 0 | 0.26469 | 357.6475 | 0.13276 | 0 | 0 | 0.26552 | 357.9333 | 0.13338 | 0 | 0 | 0.26676 | 358.1239 | 0.13379 | 0 | 0 | 0.26758 | 358.3144 | 0.13421 | 0 | 0 | 0.26841
2017-12-31 22:00 | 316.4064 | 0.94308 |  | 332.2472 | 0.077666 | 0 | 0 | 0.15533 | 341.5837 | 0.097917 | 0 | 0 | 0.19583 | 349.2226 | 0.11449 | 0 | 0 | 0.22897 | 349.5055 | 0.1151 | 0 | 0 | 0.2302 | 349.6942 | 0.11551 | 0 | 0 | 0.23102 | 349.9771 | 0.11612 | 0 | 0 | 0.23224 | 350.26 | 0.11674 | 0 | 0 | 0.23347 | 350.5429 | 0.11735 | 0 | 0 | 0.2347 | 350.9202 | 0.11817 | 0 | 0 | 0.23633 | 351.2031 | 0.11878 | 0 | 0 | 0.23756 | 351.3917 | 0.11919 | 0 | 0 | 0.23838 | 351.6746 | 0.1198 | 0 | 0 | 0.23961 | 351.8632 | 0.12021 | 0 | 0 | 0.24043 | 352.1462 | 0.12083 | 0 | 0 | 0.24165 | 352.4291 | 0.12144 | 0 | 0 | 0.24288 | 352.6177 | 0.12185 | 0 | 0 | 0.2437 | 352.9006 | 0.12246 | 0 | 0 | 0.24493 | 353.1836 | 0.12308 | 0 | 0 | 0.24615 | 353.2779 | 0.12328 | 0 | 0 | 0.24656 | 353.5608 | 0.12389 | 0 | 0 | 0.24779 | 353.8437 | 0.12451 | 0 | 0 | 0.24902 | 354.0323 | 0.12492 | 0 | 0 | 0.24984 | 354.3152 | 0.12553 | 0 | 0 | 0.25106 | 354.5039 | 0.12594 | 0 | 0 | 0.25188 | 354.6925 | 0.12635 | 0 | 0 | 0.2527
2017-12-31 23:00 | 311.3057 | 0.92788 |  | 326.8912 | 0.066049 | 0 | 0 | 0.1321 | 336.0772 | 0.085973 | 0 | 0 | 0.17195 | 343.593 | 0.10227 | 0 | 0 | 0.20455 | 343.8713 | 0.10288 | 0 | 0 | 0.20576 | 344.0569 | 0.10328 | 0 | 0 | 0.20656 | 344.3353 | 0.10388 | 0 | 0 | 0.20777 | 344.6136 | 0.10449 | 0 | 0 | 0.20898 | 344.892 | 0.10509 | 0 | 0 | 0.21018 | 345.2632 | 0.1059 | 0 | 0 | 0.21179 | 345.5415 | 0.1065 | 0 | 0 | 0.213 | 345.7271 | 0.1069 | 0 | 0 | 0.21381 | 346.0055 | 0.10751 | 0 | 0 | 0.21501 | 346.191 | 0.10791 | 0 | 0 | 0.21582 | 346.4694 | 0.10851 | 0 | 0 | 0.21703 | 346.7478 | 0.10912 | 0 | 0 | 0.21824 | 346.9333 | 0.10952 | 0 | 0 | 0.21904 | 347.2117 | 0.11012 | 0 | 0 | 0.22025 | 347.4901 | 0.11073 | 0 | 0 | 0.22146 | 347.5828 | 0.11093 | 0 | 0 | 0.22186 | 347.8612 | 0.11153 | 0 | 0 | 0.22307 | 348.1396 | 0.11214 | 0 | 0 | 0.22427 | 348.3252 | 0.11254 | 0 | 0 | 0.22508 | 348.6035 | 0.11314 | 0 | 0 | 0.22629 | 348.7891 | 0.11355 | 0 | 0 | 0.22709 | 348.9747 | 0.11395 | 0 | 0 | 0.2279
|  |  |  | 2312969.2894 | 158.131 | 0 | 0 | 316.262 | 2377966.1556 | 249.801 | 0 | 0 | 499.6019 | 2431145.4098 | 336.9981 | 0.77512 | 0.20001 | 675.1713 | 2433115.0118 | 340.4115 | 0.9459 | 0.21956 | 682.208 | 2434428.0798 | 342.6928 | 1.0615 | 0.23259 | 686.9124 | 2436397.6818 | 346.1261 | 1.2349 | 0.25213 | 693.9913 | 2438367.2838 | 349.5693 | 1.4084 | 0.27168 | 701.0902 | 2440336.8858 | 353.0219 | 1.584 | 0.30127 | 708.2303 | 2442963.0218 | 357.6406 | 1.8558 | 0.37303 | 717.8832 | 2444932.6238 | 361.1143 | 2.0854 | 0.47033 | 725.2545 | 2446245.6918 | 363.4371 | 2.2393 | 0.54768 | 730.2089 | 2448215.2939 | 366.9312 | 2.4968 | 0.6637 | 737.6866 | 2449528.3619 | 369.2645 | 2.676 | 0.74209 | 742.6892 | 2451497.9639 | 372.7711 | 2.9516 | 0.89659 | 750.287 | 2453467.5659 | 376.2842 | 3.2703 | 1.0511 | 757.9409 | 2454780.6339 | 378.6307 | 3.4875 | 1.1541 | 763.0572 | 2456750.2359 | 382.158 | 3.8213 | 1.3086 | 770.7545 | 2458719.8379 | 385.6931 | 4.166 | 1.4631 | 778.4784 | 2459376.3719 | 386.8727 | 4.2809 | 1.5177 | 781.0617 | 2461345.9739 | 390.4163 | 4.6494 | 1.7008 | 788.8836 | 2463315.5759 | 393.9692 | 5.1053 | 1.9056 | 796.8548 | 2464628.6439 | 396.3416 | 5.4358 | 2.0469 | 802.2128 | 2466598.2459 | 399.9069 | 5.9451 | 2.2667 | 810.2923 | 2467911.3139 | 402.2885 | 6.3164 | 2.4207 | 815.7349 | 2469224.3819 | 404.6751 | 6.71 | 2.5748 | 821.2097

## Altern 4 Conting Limits
Month | High Temp | L23/24 Rating | L23 | Limitation | L24 | Limitation | SC1 | Limitation | SC2 | Limitation | SC3 | Limitation | C1 | Limitation | C2 | Limitation | C3 | Limitation | T1 | Limitation | T2 | Limitation | T3 | Limitation | T8 | Limitation | T4 | Limitation | T5 | Limitation | T6 | Limitation | T7 | Limitation
|  |  |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt
Jan | -16 | 374.2612 | 296.01 | Voltage | 296.01 | Voltage | 358.6 | Voltage | 367.23 | Voltage | 367.23 | Voltage | 390.25 | Voltage | 408.4 | Voltage | 408.4 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Feb | -14 | 368.9666 | 296.01 | Voltage | 296.01 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Mar | -7 | 348.0352 | 290.9 | Thermal | 290.9 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Apr | 1 | 319.5416 | 276.03 | Thermal | 276.03 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
May | 10 | 281.657 | 250.64 | Thermal | 250.64 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jun | 16 | 252.9716 | 229.53 | Thermal | 229.53 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jul | 19 | 237.6002 | 217.47 | Thermal | 217.47 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Aug | 18 | 242.8002 | 221.74 | Thermal | 221.74 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Sep | 12 | 272.4 | 244.6 | Thermal | 244.6 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Oct | 4 | 307.5992 | 269.23 | Thermal | 269.23 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Nov | -4 | 337.9216 | 285.85 | Thermal | 285.85 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Dec | -13 | 366.205 | 296.44 | Voltage | 296.44 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Limitations
SC1/SC2/SC3 - Maximum voltage 1.05 pu, try and maximize this value, this will enable maximum VAR output from machines
Bus B13/B15 - Must be kept above 1.013 pu, can go higher but not lower