## Data Tables
Table 1 (Part 1 of 2)
Holyrood Fuel Conversion Rate
Data Used in the Regression Analysis
Month | Year | Total Unit Operating Hours | Gross Average Unit Loading (kW) | Running HeatContent (BTU/US gal) | Gross Consumption Rate (bbl/Hr)
6 | 2009 | 200.448 | 71090.7567 | 154143.3333 | 116.4487
7 | 2009 | 1e-07 | 0 | 154143.3333 | 0
8 | 2009 | 1e-07 | 0 | 154143.3333 | 0
9 | 2009 | 1e-07 | 0 | 155195 | 0
10 | 2009 | 643.7088 | 75298.0229 | 154236.6667 | 116.9914
11 | 2009 | 1440.4138 | 75700.4688 | 155105 | 115.0446
12 | 2009 | 2032.45 | 78024.0596 | 154415 | 118.6137
1 | 2010 | 2107.3056 | 81905.5385 | 152391.6667 | 128.2781
2 | 2010 | 1548.87 | 82414.9218 | 152868.3333 | 127.1659
3 | 2010 | 1802.92 | 75749.34 | 151918.3333 | 119.9837
4 | 2010 | 1247.25 | 76985.3678 | 151797.5 | 121.5738
5 | 2010 | 679.65 | 72919.8852 | 150544.1667 | 118.9131
6(1) | 2010 | 95.5 | 83246.0732 | 149171.6667 | 142.7182
7 | 2010 | 1e-07 | 0 | 0 | 0
8 | 2010 | 1e-07 | 0 | 0 | 0
9(1) | 2010 | 5.47 | 38391.2242 | 149171.6667 | 264.9498
10 | 2010 | 666.39 | 70184.1264 | 150010.8333 | 113.6475
11 | 2010 | 1303.1 | 73846.9803 | 152751.6667 | 115.3553
12 | 2010 | 1726.92 | 74294.119 | 152721.6667 | 119.2828
1 | 2011 | 2036.8 | 77675.7659 | 153231.6667 | 121.7031
2 | 2011 | 1999.67 | 85344.0818 | 153400.8333 | 131.9298
3 | 2011 | 1799.1 | 84075.371 | 155007.5 | 129.9324
4 | 2011 | 1204.65 | 75640.2274 | 156505 | 117.2026
5 | 2011 | 571.83 | 72993.7219 | 155125.8333 | 115.7859
6 | 2011 | 246.7 | 71341.7106 | 153958.3333 | 113.9371
7 | 2011 | 1e-07 | 0 | 0 | 0
8 | 2011 | 1e-07 | 0 | 0 | 0
9 | 2011 | 1e-07 | 0 | 0 | 0
10 | 2011 | 659.33 | 71769.8269 | 153824.1667 | 111.4871
11 | 2011 | 1305.7 | 81672.666 | 153938.3333 | 126.0984
12 | 2011 | 2039.98 | 80564.5153 | 154179.1667 | 122.5726
Table 1 (Part 2 of 2)
Holyrood Fuel Conversion Rate
Data Used in the Regression Analysis
Month | Year | Total Unit Operating Hours | Gross Average Unit Loading (kW) | Running HeatContent (BTU/bbl) | Gross Consumption Rate (bbl/Hr)
1 | 2012 | 2180.77 | 84167.5188 | 155070.8333 | 130.827
2 | 2012 | 1892.9 | 85815.4155 | 155043.3333 | 131.6046
3 | 2012 | 1718.02 | 88363.3485 | 154738.3333 | 136.3737
4 | 2012 | 848.09 | 82420.4978 | 154955.8333 | 129.1513
5 | 2012 | 528.55 | 79935.6731 | 153499.1667 | 128.4912
6 | 2012 | 274.53 | 80683.3497 | 153380 | 128.7329
7 | 2012 | 1e-07 | 0 | 0 | 0
8 | 2012 | 1e-07 | 0 | 115075.8333 | 0
9 | 2012 | 1e-07 | 0 | 0 | 0
10 | 2012 | 423.48 | 68480.2116 | 153380 | 111.4968
11 | 2012 | 992.02 | 87972.0167 | 154231.6667 | 135.9187
12 | 2012 | 1823.37 | 92416.7887 | 154699.1667 | 145.2204
1 | 2013 | 1684.28 | 114416.8428 | 151527.5 | 176.6946
2 | 2013 | 1344 | 116354.1667 | 152965.8333 | 180.1148
3 | 2013 | 1450.53 | 88436.6404 | 153626.6667 | 139.2659
4 | 2013 | 1146.71 | 83883.4579 | 153191.6667 | 134.1384
5 | 2013 | 536.49 | 77727.4506 | 153475.8333 | 125.3911
6 | 2013 | 372.53 | 73148.4712 | 153388.3333 | 122.5637
7 | 2013 | 1e-07 | 0 | 0 | 0
8 | 2013 | 1e-07 | 0 | 0 | 0
9(1) | 2013 | 30.38 | 67478.6041 | 153122.5 | 0
10 | 2013 | 888.08 | 66210.2513 | 153661.6667 | 108.3194
11 | 2013 | 1420.68 | 79102.9648 | 153368.3333 | 124.1824
12 | 2013 | 2055.07 | 101524.5223 | 152492.5 | 156.7898
1 | 2014 | 2052.44 | 93025.8619 | 150413.3333 | 152.0006
2 | 2014 | 1944.85 | 108111.1654 | 151743.3333 | 169.8873
3 | 2014 | 2193.62 | 98353.4067 | 150900 | 153.5405
4 | 2014 | 1526 | 83669.7248 | 148227.5 | 134.0839
5 | 2014 | 1021.28 | 84570.3431 | 149898.3333 | 137.7569
Note 1: June 2010, September 2010 and September 2013 removed from regression analysis as they were outliers.

## Conv Rate Calc
2009-2014 Linear Regression (Gross)
SUMMARY OUTPUT
Regression Statistics
| Multiple R | 0.98888
| R Square | 0.97788
| Adjusted R Square | 0.97677
| Standard Error | 2.303
| Observations | 43
ANOVA
|  | df | SS | MS | F | Significance F
| Regression | 2 | 9378.6351 | 4689.3176 | 884.1732 | 7.8626e-34
| Residual | 40 | 212.1448 | 5.3036
| Total | 42 | 9590.7799
|  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
| Intercept | 155.9173 | 33.8078 | 4.6119 | 4.0417e-05 | 87.5892 | 224.2455 | 87.5892 | 224.2455
| 116354.1667 | 0.0014327 | 3.5983e-05 | 39.8164 | 8.4258e-34 | 0.00136 | 0.0015055 | 0.00136 | 0.0015055
| 152965.8333 | -0.00094151 | 0.00021564 | -4.3661 | 8.6912e-05 | -0.0013773 | -0.00050568 | -0.0013773 | -0.00050568
Calculation of 2015 Test Year Conversion Rate:
1 | Unit net average loading (kW) | 109570
2 | Fuel Heating Content (btu/bbl) | 152400
3 | Station Service Factor | 6.61%
4 | Unit gross average loading (kW) | 117330 | Line 1/(1-Line 3)
5 | Coefficient 1 | 0.0014327 | (from regression equation)
6 | Coefficient 2 | -0.00094151 | (from regression equation)
7 | Intercept | 155.9173 | (from regression equation)
8 | Fuel consumption rate (bbls/hour) | 180.5334 | Line 7 + (Line 4 x Line 5) + (Line 2 x Line 6)
9 | Net fuel conversion factor (kWh/bbl) | 607 | Line 1/Line 8

## Chart
Year | Month | Avg Unit Load (kWc) | Heat Content (BTUs/gal) | Actual Bbl/Hour | 2009-2014 Linear Regression (Gross) | Month | Year | Avg Unit Load (kWc) | Heat Content (BTUs/gal) | Actual kWh/Bbl | 2009-2014 Linear Regression (Gross)
Feb | 2013 | 116354.1667 | 152965.8333 | 180.1148 | 178.6026 | Feb | 2013 | 116354.1667 | 152965.8333 | 646 | 651.4697 | 2009-2014 Linear Regression (Gross)
Jan | 2013 | 114416.8428 | 151527.5 | 176.6946 | 177.1811 | Jan | 2013 | 114416.8428 | 151527.5 | 647.54 | 645.762 | SUMMARY OUTPUT
Feb | 2014 | 108111.1654 | 151743.3333 | 169.8873 | 167.9436 | Feb | 2014 | 108111.1654 | 151743.3333 | 636.37 | 643.7349
Dec | 2013 | 101524.5223 | 152492.5 | 156.7898 | 157.8014 | Dec | 2013 | 101524.5223 | 152492.5 | 647.52 | 643.369 | Regression Statistics
Mar | 2014 | 98353.4067 | 150900 | 153.5405 | 154.7574 | Mar | 2014 | 98353.4067 | 150900 | 640.57 | 635.5328 | Multiple R | 0.98888
Jan | 2014 | 93025.8619 | 150413.3333 | 152.0006 | 147.5827 | Jan | 2014 | 93025.8619 | 150413.3333 | 612.01 | 630.3304 | R Square | 0.97788
Dec | 2012 | 92416.7887 | 154699.1667 | 145.2204 | 142.6749 | Dec | 2012 | 92416.7887 | 154699.1667 | 636.39 | 647.7438 | Adjusted R Square | 0.97677
Mar | 2013 | 88436.6404 | 153626.6667 | 139.2659 | 137.9822 | Mar | 2013 | 88436.6404 | 153626.6667 | 635.02 | 640.9278 | Standard Error | 2.303
Mar | 2012 | 88363.3485 | 154738.3333 | 136.3737 | 136.8306 | Mar | 2012 | 88363.3485 | 154738.3333 | 647.95 | 645.7866 | Observations | 43
Nov | 2012 | 87972.0167 | 154231.6667 | 135.9187 | 136.7469 | Nov | 2012 | 87972.0167 | 154231.6667 | 647.24 | 643.3199
Feb | 2012 | 85815.4155 | 155043.3333 | 131.6046 | 132.8929 | Feb | 2012 | 85815.4155 | 155043.3333 | 652.07 | 645.7486 | ANOVA
Feb | 2011 | 85344.0818 | 153400.8333 | 131.9298 | 133.764 | Feb | 2011 | 85344.0818 | 153400.8333 | 646.89 | 638.0196 |  | df | SS | MS | F | Significance F
May | 2014 | 84570.3431 | 149898.3333 | 137.7569 | 135.9531 | May | 2014 | 84570.3431 | 149898.3333 | 613.91 | 622.0552 | Regression | 2 | 9378.6351 | 4689.3176 | 884.1732 | 7.8626e-34
Jan | 2012 | 84167.5188 | 155070.8333 | 130.827 | 130.506 | Jan | 2012 | 84167.5188 | 155070.8333 | 643.35 | 644.932 | Residual | 40 | 212.1448 | 5.3036
Mar | 2011 | 84075.371 | 155007.5 | 129.9324 | 130.4336 | Mar | 2011 | 84075.371 | 155007.5 | 647.07 | 644.5835 | Total | 42 | 9590.7799
Apr | 2013 | 83883.4579 | 153191.6667 | 134.1384 | 131.8683 | Apr | 2013 | 83883.4579 | 153191.6667 | 625.35 | 636.1154
Apr | 2014 | 83669.7248 | 148227.5 | 134.0839 | 136.2359 | Apr | 2014 | 83669.7248 | 148227.5 | 624.01 | 614.1534 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
Apr | 2012 | 82420.4978 | 154955.8333 | 129.1513 | 128.1113 | Apr | 2012 | 82420.4978 | 154955.8333 | 638.17 | 643.3507 | Intercept | 155.9173 | 33.8078 | 4.6119 | 4.0417e-05 | 87.5892 | 224.2455 | 87.5892 | 224.2455
Feb | 2010 | 82414.9218 | 152868.3333 | 127.1659 | 130.0687 | Feb | 2010 | 82414.9218 | 152868.3333 | 648.09 | 633.626 | 116354.1667 | 0.0014327 | 3.5983e-05 | 39.8164 | 8.4258e-34 | 0.00136 | 0.0015055 | 0.00136 | 0.0015055
Jan | 2010 | 81905.5385 | 152391.6667 | 128.2781 | 129.7877 | Jan | 2010 | 81905.5385 | 152391.6667 | 638.5 | 631.0733 | 152965.8333 | -0.00094151 | 0.00021564 | -4.3661 | 8.6912e-05 | -0.0013773 | -0.00050568 | -0.0013773 | -0.00050568
Nov | 2011 | 81672.666 | 153938.3333 | 126.0984 | 127.9978 | Nov | 2011 | 81672.666 | 153938.3333 | 647.69 | 638.0784
Jun | 2012 | 80683.3497 | 153380 | 128.7329 | 127.1061 | Jun | 2012 | 80683.3497 | 153380 | 626.75 | 634.7717
Dec | 2011 | 80564.5153 | 154179.1667 | 122.5726 | 126.1834 | Dec | 2011 | 80564.5153 | 154179.1667 | 657.28 | 638.4715
May | 2012 | 79935.6731 | 153499.1667 | 128.4912 | 125.9227 | May | 2012 | 79935.6731 | 153499.1667 | 622.11 | 634.7996 | RESIDUAL OUTPUT
Nov | 2013 | 79102.9648 | 153368.3333 | 124.1824 | 124.8528 | Nov | 2013 | 79102.9648 | 153368.3333 | 636.99 | 633.5697
Dec | 2009 | 78024.0596 | 154415 | 118.6137 | 122.3216 | Dec | 2009 | 78024.0596 | 154415 | 657.8 | 637.86 | Observation | Predicted 180.114809068126 | Residuals
May | 2013 | 77727.4506 | 153475.8333 | 125.3911 | 122.7809 | May | 2013 | 77727.4506 | 153475.8333 | 619.88 | 633.0583 | 1 | 177.1811 | -0.48649
Jan | 2011 | 77675.7659 | 153231.6667 | 121.7031 | 122.9367 | Jan | 2011 | 77675.7659 | 153231.6667 | 638.24 | 631.8354 | 2 | 167.9436 | 1.9437
Apr | 2010 | 76985.3678 | 151797.5 | 121.5738 | 123.2978 | Apr | 2010 | 76985.3678 | 151797.5 | 633.24 | 624.3854 | 3 | 157.8014 | -1.0116
Mar | 2010 | 75749.34 | 151918.3333 | 119.9837 | 121.4132 | Mar | 2010 | 75749.34 | 151918.3333 | 631.33 | 623.8972 | 4 | 154.7574 | -1.217
Nov | 2009 | 75700.4688 | 155105 | 115.0446 | 118.3429 | Nov | 2009 | 75700.4688 | 155105 | 658.01 | 639.6706 | 5 | 147.5827 | 4.4179
Apr | 2011 | 75640.2274 | 156505 | 117.2026 | 116.9385 | Apr | 2011 | 75640.2274 | 156505 | 645.38 | 646.8378 | 6 | 142.6749 | 2.5455
Oct | 2009 | 75298.0229 | 154236.6667 | 116.9914 | 118.5838 | Oct | 2009 | 75298.0229 | 154236.6667 | 643.62 | 634.9771 | 7 | 137.9822 | 1.2837
Dec | 2010 | 74294.119 | 152721.6667 | 119.2828 | 118.5719 | Dec | 2010 | 74294.119 | 152721.6667 | 622.84 | 626.5744 | 8 | 136.8306 | -0.45685
Nov | 2010 | 73846.9803 | 152751.6667 | 115.3553 | 117.903 | Nov | 2010 | 73846.9803 | 152751.6667 | 640.17 | 626.3366 | 9 | 136.7469 | -0.82822
Jun | 2013 | 73148.4712 | 153388.3333 | 122.5637 | 116.3028 | Jun | 2013 | 73148.4712 | 153388.3333 | 596.82 | 628.9483 | 10 | 132.8929 | -1.2883
May | 2011 | 72993.7219 | 155125.8333 | 115.7859 | 114.4452 | May | 2011 | 72993.7219 | 155125.8333 | 630.42 | 637.8047 | 11 | 133.764 | -1.8342
May | 2010 | 72919.8852 | 150544.1667 | 118.9131 | 118.6531 | May | 2010 | 72919.8852 | 150544.1667 | 613.22 | 614.5635 | 12 | 135.9531 | 1.8038
Oct | 2011 | 71769.8269 | 153824.1667 | 111.4871 | 113.9173 | Oct | 2011 | 71769.8269 | 153824.1667 | 643.75 | 630.0171 | 13 | 130.506 | 0.32092
Jun | 2011 | 71341.7106 | 153958.3333 | 113.9371 | 113.1776 | Jun | 2011 | 71341.7106 | 153958.3333 | 626.15 | 630.352 | 14 | 130.4336 | -0.50122
Jun | 2009 | 71090.7567 | 154143.3333 | 116.4487 | 112.6439 | Jun | 2009 | 71090.7567 | 154143.3333 | 610.49 | 631.1108 | 15 | 131.8683 | 2.2701
Oct | 2010 | 70184.1264 | 150010.8333 | 113.6475 | 115.2357 | Oct | 2010 | 70184.1264 | 150010.8333 | 617.56 | 609.0486 | 16 | 136.2359 | -2.1519
Oct | 2012 | 68480.2116 | 153380 | 111.4968 | 109.6223 | Oct | 2012 | 68480.2116 | 153380 | 614.19 | 624.6921 | 17 | 128.1113 | 1.04
Oct | 2013 | 66210.2513 | 153661.6667 | 108.3194 | 106.1049 | Oct | 2013 | 66210.2513 | 153661.6667 | 611.25 | 624.0074 | 18 | 130.0687 | -2.9028
[12 empty] | 19 | 129.7877 | -1.5096
[12 empty] | 20 | 127.9978 | -1.8995
[12 empty] | 21 | 127.1061 | 1.6268
[12 empty] | 22 | 126.1834 | -3.6108
[12 empty] | 23 | 125.9227 | 2.5685
[12 empty] | 24 | 124.8528 | -0.6704
[12 empty] | 25 | 122.3216 | -3.708
[12 empty] | 26 | 122.7809 | 2.6102
[12 empty] | 27 | 122.9367 | -1.2336
[12 empty] | 28 | 123.2978 | -1.7241
[12 empty] | 29 | 121.4132 | -1.4294
[12 empty] | 30 | 118.3429 | -3.2983
[12 empty] | 31 | 116.9385 | 0.26415
[12 empty] | 32 | 118.5838 | -1.5924
[12 empty] | 33 | 118.5719 | 0.71093
[12 empty] | 34 | 117.903 | -2.5478
[12 empty] | 35 | 116.3028 | 6.2609
[12 empty] | 36 | 114.4452 | 1.3406
[12 empty] | 37 | 118.6531 | 0.25995
[12 empty] | 38 | 113.9173 | -2.4302
[12 empty] | 39 | 113.1776 | 0.75951
[12 empty] | 40 | 112.6439 | 3.8048
[12 empty] | 41 | 115.2357 | -1.5882
[12 empty] | 42 | 109.6223 | 1.8744
[12 empty] | 43 | 106.1049 | 2.2145

## Data Sort Sheet
Month | Year | Average | Running Heat | Consumption Rate (Bbl/Hr)
|  | Unit Load (KW) - Gross | Content (BTU/bbl) |  | Note June 2010, September 2010 and September 2013 removed from regression analysis
Feb | 2013 | 116354.1667 | 152965.8333 | 180.1148
Jan | 2013 | 114416.8428 | 151527.5 | 176.6946
Feb | 2014 | 108111.1654 | 151743.3333 | 169.8873
Dec | 2013 | 101524.5223 | 152492.5 | 156.7898
Mar | 2014 | 98353.4067 | 150900 | 153.5405
Jan | 2014 | 93025.8619 | 150413.3333 | 152.0006
Dec | 2012 | 92416.7887 | 154699.1667 | 145.2204
Mar | 2013 | 88436.6404 | 153626.6667 | 139.2659
Mar | 2012 | 88363.3485 | 154738.3333 | 136.3737
Nov | 2012 | 87972.0167 | 154231.6667 | 135.9187
Feb | 2012 | 85815.4155 | 155043.3333 | 131.6046
Feb | 2011 | 85344.0818 | 153400.8333 | 131.9298
May | 2014 | 84570.3431 | 149898.3333 | 137.7569
Jan | 2012 | 84167.5188 | 155070.8333 | 130.827
Mar | 2011 | 84075.371 | 155007.5 | 129.9324
Apr | 2013 | 83883.4579 | 153191.6667 | 134.1384
Apr | 2014 | 83669.7248 | 148227.5 | 134.0839
Apr | 2012 | 82420.4978 | 154955.8333 | 129.1513
Feb | 2010 | 82414.9218 | 152868.3333 | 127.1659
Jan | 2010 | 81905.5385 | 152391.6667 | 128.2781
Nov | 2011 | 81672.666 | 153938.3333 | 126.0984
Jun | 2012 | 80683.3497 | 153380 | 128.7329
Dec | 2011 | 80564.5153 | 154179.1667 | 122.5726
May | 2012 | 79935.6731 | 153499.1667 | 128.4912
Nov | 2013 | 79102.9648 | 153368.3333 | 124.1824
Dec | 2009 | 78024.0596 | 154415 | 118.6137
May | 2013 | 77727.4506 | 153475.8333 | 125.3911
Jan | 2011 | 77675.7659 | 153231.6667 | 121.7031
Apr | 2010 | 76985.3678 | 151797.5 | 121.5738
Mar | 2010 | 75749.34 | 151918.3333 | 119.9837
Nov | 2009 | 75700.4688 | 155105 | 115.0446
Apr | 2011 | 75640.2274 | 156505 | 117.2026
Oct | 2009 | 75298.0229 | 154236.6667 | 116.9914
Dec | 2010 | 74294.119 | 152721.6667 | 119.2828
Nov | 2010 | 73846.9803 | 152751.6667 | 115.3553
Jun | 2013 | 73148.4712 | 153388.3333 | 122.5637
May | 2011 | 72993.7219 | 155125.8333 | 115.7859
May | 2010 | 72919.8852 | 150544.1667 | 118.9131
Oct | 2011 | 71769.8269 | 153824.1667 | 111.4871
Jun | 2011 | 71341.7106 | 153958.3333 | 113.9371
Jun | 2009 | 71090.7567 | 154143.3333 | 116.4487
Oct | 2010 | 70184.1264 | 150010.8333 | 113.6475
Oct | 2012 | 68480.2116 | 153380 | 111.4968
Oct | 2013 | 66210.2513 | 153661.6667 | 108.3194