## Sheet1
|  |  | 2016 | [5 empty] | 2017 |  |  |  | 2018
Unit # | Asset # | Blade # | Depth | Area (in) | Notes | WO# |  |  | Depth | Area (in) | Notes | WO# | Depth | Area (in) | Notes | WO#
BDE Unit 1 | 58429 | 1 | 3/16" | 2x4 | Blade #1 marked | 1179956 |  |  | 1/4" | 3x3 | Blade #1 marked. Cavitation approaching leading edge | 1273335 | 7/16" | 3x3 | Cavitation very close to leading edge | 1337259
|  | 2 | 1/4" | 1.5x2.5 |  |  |  |  | 1/4" | 3x4 | Cavitation approaching leading edge |  | 5/16" | 3x4 | Cavitation approaching leading edge
|  | 3 | 3/16" | 2x4 |  |  |  |  | 1/8" | 2x3 |  |  | 1/4" | 3x4 | Cavitation approaching leading edge
|  | 4 | 3/16" | 2x4 |  |  |  |  | 3/16" | 2x3 |  |  | 1/4" | 2x3 | Cavitation approaching leading edge
|  | 5 | 1/4" | 2x3 |  |  |  |  | 1/4" | 2x3 | Cavitation approaching leading edge |  | 3/8" | 2.5x3.5 | Cavitation approaching leading edge
|  | 6 | 1/4" | 2x4 |  |  |  |  | 1/4" | 2x4 |  |  | 1/4" | 2.5x4
|  | 7 | 5/16" | 2x5 |  |  |  |  | 1/8" | 2x3 |  |  | 1/8" | 2.5x3.5
|  | 8 | 3/16" | 1.5x3 |  |  |  |  | 1/4" | 3x4 | Cavitation approaching leading edge |  | 1/4" | 3x4.5 | Cavitation very close to leading edge
|  | 9 | 1/4" | 2x4 |  |  |  |  | 3/16" | 3x4 |  |  | 1/4" | 3x4
|  | 10 | 5/16" | 2x5 |  |  |  |  | 1/4" | 3x4 |  |  | 1/4" | 3x4
|  | 11 |  |  | Unable to reach |  |  |  | 1/8" | 2x3 |  |  | 3/16" | 2x3 | Cavitation approaching leading edge
|  | 12 | 5/16" | 3x4 |  |  |  |  | 1/8" | 3x3 |  |  | 3/16" | 3x4
|  | 13 | 1/4" | 3x4 |  |  |  |  | 3/16" | 3x3 | Cavitation approaching leading edge |  | 1/4" | 3x4 | Cavitation very close to leading edge
BDE Unit 2 | 59072 | 1 | [6 empty] | 1/8" | 3x3 | Blade #1 marked | 1266366
|  | 2 | [6 empty] | 1/8" | 3x3
|  | 3 | [6 empty] | 1/8" | 2x3 | Runner to Lower Band height .060"
|  | 4 |  |  | No Inspection Conducted 2016 |  |  |  | 3/16" | 3x3
|  | 5 | [6 empty] | 3/16" | 3x3
|  | 6 | [6 empty] | 1/16" | 2x2
|  | 7 | [6 empty] | 3/16" | 3x4
|  | 8 | [6 empty] | 1/16" | 2x2
|  | 9 | [6 empty] | 1/8" | 1.5x2
|  | 10 | [6 empty] | 1/16" | 3x4
|  | 11 | [6 empty] | 1/8" | 3x3
|  | 12 | [6 empty] | 1/16" | 2x3
|  | 13 | [6 empty] | 1/32" | 2x2
BDE Unit 3 | 59278 | 1 | 1/2" | 3x4 |  | 1189137 |  |  |  |  | Runner repaired 2017 |  | None | 2x3 | Heavy frosting | 1347652
|  | 2 | 3/8" | 3x4 | [8 empty] | 1/8" | 1x2
|  | 3 | 1/2" | 4x5 | [8 empty] | 1/8" | 2x3
|  | 4 | 1/2" | 3x4 | [8 empty] | 1/8" | 1x3 | Cavitation approaching leading edge
|  | 5 | 1/2" | 2x4 | [8 empty] | 1/8" | 2x3
|  | 6 | 1/2" | 3x4 | Cavitation approaching leading edge | [7 empty] | 1/4" | 2x3
|  | 7 | 3/8" | 2x4 | [8 empty] | None | 1x2 | Frosting
|  | 8 | 3/8" | 2x3 | Cavitation approaching leading edge | [7 empty] | None | 2x3 | Heavy frosting
|  | 9 | 7/16" | 3x4 | [8 empty] | None | 1x3 | Heavy frosting
|  | 10 | 1/4" | 2x4 | Cavitation approaching leading edge | [7 empty] | 1/8" | 2x4 | Cavitation approaching leading edge
|  | 11 | 3/8" | 4x4 | [8 empty] | 1/8" | 2x3 | Cavitation approaching leading edge
|  | 12 | 3/8" | 4x4 | [8 empty] | None | 1x2 | Heavy frosting
|  | 13 | 7/16" | 3x4 | [8 empty] | 1/4" | 2x3
BDE Unit 4 | 59273 | 1 | 1/16" | 1x2 | Runner repaired 2016 | 1189139 |  |  |  | 1x1 to 2x3 all blades | Blade 1 marked | 1256332 | None | 2x2 | Frosting | 1347653
|  | 2 | 1/8" | 1x2 | [8 empty] | None | 1x1 | Frosting
|  | 3 | 1/8" | 1x2 | [8 empty] | None | 1x1 | Frosting
|  | 4 | 1/8" | 1x2 | [6 empty] | All blades light frosting on high pressure |  | None | 1x1 | Frosting
|  | 5 | 3/16" | 2x2 | [6 empty] | side. No measurable depth or pitting. |  | None | 1x1 | Frosting
|  | 6 | 1/4" | 2x2 | [8 empty] | None | 1x1 | Frosting
|  | 7 | 1/16" | 1x2 | [8 empty] | None | 1x1 | Heavy frosting
|  | 8 | 3/16" | 2x2 | [8 empty] | None | 1/2x1/2 | Frosting
|  | 9 | 1/16" | 2x2 | [8 empty] | None | 1x2 | Frosting
|  | 10 | 1/8" | 2x3 | [8 empty] | None | 1x2 | Frosting
|  | 11 | 1/8" | 2x3 | [8 empty] | None | 1x2 | Heavy frosting
|  | 12 | 3/16" | 2x3 | [8 empty] | None | 1x1 | Frosting
|  | 13 | 1/8" | 2x2 | [8 empty] | None | 1x1 | Frosting
BDE Unit 5 | 59675 | 1 | 1/8" | 1.5x1.5 |  | 1183530 |  |  | 1/8" | 2x3 |  | 1254135
|  | 2 | 1/4" | 1.5x2.5 |  |  |  |  | 1/4" | 2x3
|  | 3 | 5/16" | .5x3 |  |  |  |  | 5/16" | 3x4
|  | 4 | 1/4" | 2x2 |  |  |  |  | 1/4" | 2x4 | Blade 4 marked "0"
|  | 5 | 3/16" | 2x2 | Signs of debris ingestion on multiple |  |  |  | 3/16" | 2x4
|  | 6 | 1/16" | 2x2 | blade faces and leading edges |  |  |  | 1/8" | 2x2
|  | 7 | 1/16" | 2x2 |  |  |  |  | 1/8" | 2x3
|  | 8 | 1/16" | 2x2 |  |  |  |  | 1/8" | 3x4
|  | 9 | 1/4" | 2x3 | Blade 9 marked |  |  |  | 1/4" | 2x4 | Blade 9 marked
|  | 10 | 3/16" | 2x2 |  |  |  |  | 3/16" | 3x4
|  | 11 | 1/16" | 1.5x1.5 |  |  |  |  | 1/16" | 2x3 | Signs of debris ingestion on multiple
|  | 12 | 1/16" | 1x1.5 |  |  |  |  | 1/8" | 2x3 | blade faces and leading edges. No change
|  | 13 | 1/16" | .5x2 |  |  |  |  | 1/8" | 2x3 | From 2016.
BDE Unit 6 | 59906 | 1 | 1/8" | 2x2 | Blade marked "X" | 1185967 |  |  | 1/4" | 2x3 | Blade marked "X" | 1252945
|  | 2 | 3/16" | 2x3 |  |  |  |  | 5/16" | 3x4
|  | 3 | 1/8" | 2x2 |  |  |  |  | 3/16" | 2x3
|  | 4 | 1/8" | 1.5x2 |  |  |  |  | 3/16" | 2x2
|  | 5 | 5/16" | 3x3 | Cavitation extends to leading edge |  |  |  | 5/16" | 3x3 | Cavitation extends to leading edge
|  | 6 | 1/8" | 2x3 |  |  |  |  | 1/2" | 3x4
|  | 7 | 5/16" | 3x3 | Cavitation extends to leading edge |  |  |  | 3/8" | 3x4 | Cavitation extends to leading edge
|  | 8 | 5/16" | 3x3 |  |  |  |  | 3/8" | 4x4
|  | 9 | 3/8" | 2x3 | Cavitation approaching leading edge |  |  |  | 3/8" | 3x4 | Cavitation approaching leading edge
|  | 10 | 3/16" | 2x3 |  |  |  |  | 3/16" | 4x4
|  | 11 | 3/8" | 3x3 |  |  |  |  | 3/8" | 3x4
|  | 12 | 1/4" | 2x2 |  |  |  |  | 5/16" | 2x3
|  | 13 |  |  | Unable to reach |  |  |  | 5/16" | 3x4
BDE Unit 7 | 60092 | 1 | 1.5", 1" | Multiple | Heavy pitting on all blades. Stainless | 1192734 |  |  | Frosting |  |  | 1275394 |  |  |  | 1348486
|  | 2 | 1.5" | 4x5 | layer corroded through with severe, | [5 empty] | Light cavitation/frosting on all blades.
|  | 3 | 1", 1.25" | Multiple | extensive pitting in underlaying mild
|  | 4 | 1/2" | 4x6 | steel.
|  | 5 | 3/4", 1" | Multiple
|  | 6 | 1", 1/2" | Multiple
|  | 7 | 1.5", 1/2" | Multiple | Runner repaired 2016
|  | 8 | 3/4", 1/2" | Multiple
|  | 9 | 1/2", 1" | Multiple
|  | 10 | 3x4" | Multiple
|  | 11 | 3x4" | Multiple
|  | 12 | 1" | Multiple
|  | 13 | 1" | 6x8
|  | 14 | 3/4" | 6x8
|  | 15 |  |  | Unable to reach
Unit # | Asset # | Blade # | Depth | Area (in) | Notes | WO#
HLK | 58486 | 1 | 0.375 | 2x3 | All blades little change from last | 1212736 | [5 empty] | 1284204
|  | 2 | 0.25 | 1x2 | inspection
|  | 3 | 0.125 | 3/4x2
|  | 4 | 0.125 | 1x2
|  | 5 | 0.125 | 2x3
|  | 6 | 0.1875 | 2x3
|  | 7 | 5/8, 1/8 | 1x2, 2x3
|  | 8 | 0.125 | 3/4x1
|  | 9 | 0.0625 | 2x3
|  | 10 | 0.625 | 2x3
|  | 11 | 0.375 | 2x2
|  | 12 | 0.0625 | 1.5x2.5
|  | 13 | 0.125 | 1x1
|  | 14 | 0.1875 | 1.5x2 | Pitting approaching leading edge
|  | 15 | 0.125 | 2x3
|  | 16 | 0.0625 | 2x3
Unit # | Asset # | Blade # | Depth | Area (in) | Notes | WO#
SLK | 361922 | 1 |  |  | No cavitation or frosting on high | 1218308
|  | 2 |  |  | pressure side
3
|  | 4 |  |  | Minor frosting at blade roots near
|  | 5 |  |  | discharge cone
6
7
8
9
10
11
12
13
[6 empty] | Unit # | Asset # | Blade #
[6 empty] | USL | 61777/ 61677 | 1 |  | 6" x 18" all blades | Blade 11 marked | 1275403
2
[8 empty] | 3 |  |  | Large Frosted area present on all blades
[8 empty] | 4 |  |  | near root. No pitting from cavitation.
5
[8 empty] | 6 |  |  | Frosting can been seen on low pressure side
[8 empty] | 7 |  |  | of runner but no additional marking.
[8 empty] | 8 |  |  | Runner overall in excellent shape.
9
10
11
12
13
14