## Table of Contents
Modelling Assumptions - Novemer 2019 RRA
Table of Contents
1. Economic Inputs
1.1. Economic Inputs
1.2. Escalation Factors
1.3. Projected Life of Plant
2. Annual Fuel Price Projection
2.1. Annual Fuel Oil No 2 Price
2.2. Annual Fuel Oil No 6 Price
3. Yearly Peak Demand (MW)/Net Energy
3.1. Peak Demand
3.1A. Peak Demand Sensitivities
3.2. Energy
3.2A. Energy Sensitivities
4. Existing Units
4.1. Firm Capacity
4.2. Forced Outage Rates/Maintenance Rates
4.3 LIL Near Term Assumptions
4.4 Loss Equations
4.5 Station Service Loads
5. Hydrology
5.1 Available Energy - Daily Limitations
5.2 Available Energy - Monthly Limitations
6. Yearly Planned New Entry and Planned Retirement
6.1. Specific New Additions by Year
6.2. Specific Retirements by Year
7. Capacity Expansion Options
7.1. Thermal Expansion Options
7.2. Hydro Expansion Options
7.3. Renewable Expansion Options
7.4. Battery Expansion

## Model Process (hidden)
Vista Model
Inflows
Economic Inputs
Load Forecast
Weather Data

## 1.1 Economic Inputs
1.1 Economic Inputs |  |  | Return to Table of Contents
Source: | Nalcor Energy Corporate Assumptions (September 2019)
Date: | 2019-09-16
Discount Rate1: |  | 6.5%
1Based on long term WACC

## 1.2 Escalation Factors
1.2 Escalation Factors | [6 empty] | Return to Table of Contents
Source: | Nalcor Energy Corporate Assumptions (September 2019)
Date: | 2019-10-09
Year | GDP Implicit Price Deflator | CPI | CT Escalation | CCCT Escalation | Hydraulic Plant Escalation | O+M Escalation1
2018 | 1 | 1 | 1 | 1 | 1 | 1
2019 | 1.014 | 1.023 | 1.023 | 1.023 | 1.021 | 1.022
2020 | 1.036 | 1.044 | 1.054 | 1.054 | 1.051 | 1.049
2021 | 1.058 | 1.065 | 1.084 | 1.084 | 1.079 | 1.075
2022 | 1.079 | 1.086 | 1.115 | 1.115 | 1.109 | 1.102
2023 | 1.1 | 1.108 | 1.147 | 1.147 | 1.139 | 1.13
2024 | 1.123 | 1.13 | 1.18 | 1.18 | 1.17 | 1.158
2025 | 1.145 | 1.152 | 1.214 | 1.214 | 1.201 | 1.187
2026 | 1.168 | 1.175 | 1.249 | 1.249 | 1.234 | 1.217
2027 | 1.191 | 1.198 | 1.285 | 1.285 | 1.267 | 1.247
2028 | 1.215 | 1.222 | 1.321 | 1.321 | 1.301 | 1.278
2029 | 1.24 | 1.246 | 1.359 | 1.359 | 1.337 | 1.31
1Based on same materials/same labour

## 1.3 Projected Life of Plant
1.3 Projected Life of Plant |  | Return to Table of Contents
Source: | 2012 Depreciation Methodology Application (Except as Noted)
Date: | 2018-10-01
Plant Type | Assumed Service Life (years)
Combustion Turbine1 | 35
Hydro Plant1 | 60
Diesel Plant1 | 25
Wind2 | 20
Battery3 | 20
Solar4 | 25
1Based on the 2012 Depreciation Methodology Application (Except as Noted)
2Based on the service life of existing wind farms @ FER & STL
3Based on information from consultant
4Based on NREL low lifespan estimate

## 2.1 #2 Fuel Price
2.1. Annual Fuel Oil No 2 Price |  |  |  | Return to Table of Contents
Source: | Nalcor Energy Corporate Assumptions + Fuel Conversion Spreadsheet
Date: | 2019-09-16
| Holyrood & Hardwoods | Stephenville | Happy Valley
Year | $CDN/L | $CDN/L | $CDN/L
2019 | 0.84 | 0.907 | 1.225
2020 | 0.933 | 1.001 | 1.318
2021 | 0.865 | 0.933 | 1.25
2022 | 0.81 | 0.878 | 1.195
2023 | 0.77 | 0.838 | 1.155
2024 | 0.78 | 0.848 | 1.165
2025 | 0.81 | 0.878 | 1.205
2026 | 0.825 | 0.893 | 1.225
2027 | 0.84 | 0.908 | 1.25
2028 | 0.855 | 0.923 | 1.27
2029 | 0.87 | 0.938 | 1.295

## 2.2 #6 Fuel Price
2.2. Annual Fuel Oil No 6 Price |  | Return to Table of Contents
Source: | Nalcor Energy Corporate Assumptions + Fuel Conversion Spreadsheet
Date: | 2019-09-16
Holyrood #6
$CDN/BBL
2019 | 85.6
2020 | 105.1
2021 | 90.7
2022 | 83.5
2023 | 76.4
2024 | 75.8
2025 | 78.5

## 3.1 Peak Demand
3.1 Peak Demand |  |  |  |  | Return to Table of Contents
Source: | Load forecast from System Planning
Date: | 2019-09-30
[6 empty] | Coincident Paeks | [5 empty] | Contribution to Provincial Peak
| Island Interconnected1,2,3 | Lab East1,2 | Lab West Utility1,2 | Lab West Industrial1,2 |  | Island Interconnected | Lab West Utility | Lab West Industrial | Lab West Total | Lab East | Lab Total | Island Interconnected | Lab East | Lab West Utility | Lab West Industrial | Total
| MW | MW | MW | MW |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW
2019 | 1665 | 83.554 | 77 | 295 |  | 1651.68 | 70.3512 | 267.0782 | 337.4295 | 70.868 | 428.4338 | 1651.68 | 70.868 | 70.3512 | 267.0782 | 2059.9774 | 98.4%
2020 | 1659 | 83.6 | 77 | 317 |  | 1645.728 | 70.3512 | 286.9959 | 357.3472 | 70.907 | 449.3748 | 1645.728 | 70.907 | 70.3512 | 286.9959 | 2073.9822 | 98.37%
2021 | 1657 | 79.1 | 77 | 317 |  | 1643.744 | 70.3512 | 286.9959 | 357.3472 | 67.0902 | 445.3698 | 1643.744 | 67.0902 | 70.3512 | 286.9959 | 2068.1814 | 98.37%
2022 | 1668 | 79.4 | 77.2 | 317 |  | 1654.656 | 70.5339 | 286.9959 | 357.5299 | 67.3447 | 445.8285 | 1654.656 | 67.3447 | 70.5339 | 286.9959 | 2079.5306 | 98.38%
2023 | 1678 | 79.7 | 77.3 | 317 |  | 1664.576 | 70.6253 | 286.9959 | 357.6212 | 67.5991 | 446.1914 | 1664.576 | 67.5991 | 70.6253 | 286.9959 | 2089.7964 | 98.38%
2024 | 1688 | 80 | 77.4 | 317 |  | 1674.496 | 70.7167 | 286.9959 | 357.7126 | 67.8536 | 446.5543 | 1674.496 | 67.8536 | 70.7167 | 286.9959 | 2100.0622 | 98.38%
2025 | 1695 | 80.4 | 77.9 | 317 |  | 1681.44 | 71.1735 | 286.9959 | 358.1694 | 68.1929 | 447.3896 | 1681.44 | 68.1929 | 71.1735 | 286.9959 | 2107.8023 | 98.39%
2026 (Test Year) | 1704 | 80.9 | 78 | 317 |  | 1690.368 | 71.2649 | 286.9959 | 358.2608 | 68.617 | 447.9305 | 1690.368 | 68.617 | 71.2649 | 286.9959 | 2117.2458 | 98.39%
2027 | 1716 | 81.8 | 78.2 | 317 |  | 1702.272 | 71.4476 | 286.9959 | 358.4435 | 69.3803 | 448.9232 | 1702.272 | 69.3803 | 71.4476 | 286.9959 | 2130.0958 | 98.39%
2028 | 1724 | 82.5 | 78.4 | 317 |  | 1710.208 | 71.6303 | 286.9959 | 358.6263 | 69.974 | 449.738 | 1710.208 | 69.974 | 71.6303 | 286.9959 | 2138.8083 | 98.39%
2029 | 1735 | 83.2 | 78.6 | 317 |  | 1721.12 | 71.813 | 286.9959 | 358.809 | 70.5677 | 450.5527 | 1721.12 | 70.5677 | 71.813 | 286.9959 | 2150.4967 | 98.4%
LIS Coincidence @ NLIS Peak |  | 95.3%
Coincidence @ LIS Peak |  | 89% | 95.87% | 95%
Coincidence @ NLIS Peak | 99.2% | 84.82% | 91.37% | 90.53%
1Peaks are regionally coincident
2Excludes NLH bulk transmission losses and station service
3Based on mitigated rate load case, with rates held to inflation

## 3.1A Peak Demand Sensitivities
3.1A Peak Demand Sensitivities |  |  |  |  | Return to Table of Contents
Source: | Load forecast from System Planning
Date: | 2019-10-28
IIS Low Growth | [5 empty] | Coincident Paeks | [5 empty] | Contribution to Provincial Peak
| Island Interconnected1,2 | Lab East1,2 | Lab West Utility1,2 | Lab West Industrial1,2 |  | Island Interconnected | Lab West Utility | Lab West Industrial | Lab West Total | Lab East | Lab Total | Island Interconnected | Lab East | Lab West Utility | Lab West Industrial | Total
| MW | MW | MW | MW |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW
2019 | 1664.5 | 83.554 | 77 | 295 |  | 1651.184 | 70.3512 | 267.0782 | 337.4295 | 70.868 | 428.4338 | 1651.184 | 70.868 | 70.3512 | 267.0782 | 2059.4814 | 98.4%
2020 | 1661.5 | 83.6 | 77 | 317 |  | 1648.208 | 70.3512 | 286.9959 | 357.3472 | 70.907 | 449.3748 | 1648.208 | 70.907 | 70.3512 | 286.9959 | 2076.4622 | 98.37%
2021 | 1663.8 | 79.1 | 77 | 317 |  | 1650.4896 | 70.3512 | 286.9959 | 357.3472 | 67.0902 | 445.3698 | 1650.4896 | 67.0902 | 70.3512 | 286.9959 | 2074.927 | 98.38%
2022 | 1648.7 | 79.4 | 77.2 | 317 |  | 1635.5104 | 70.5339 | 286.9959 | 357.5299 | 67.3447 | 445.8285 | 1635.5104 | 67.3447 | 70.5339 | 286.9959 | 2060.385 | 98.37%
2023 | 1646.9 | 79.7 | 77.3 | 317 |  | 1633.7248 | 70.6253 | 286.9959 | 357.6212 | 67.5991 | 446.1914 | 1633.7248 | 67.5991 | 70.6253 | 286.9959 | 2058.9452 | 98.37%
2024 | 1644.9 | 80 | 77.4 | 317 |  | 1631.7408 | 70.7167 | 286.9959 | 357.7126 | 67.8536 | 446.5543 | 1631.7408 | 67.8536 | 70.7167 | 286.9959 | 2057.307 | 98.37%
2025 | 1640.5 | 80.4 | 77.9 | 317 |  | 1627.376 | 71.1735 | 286.9959 | 358.1694 | 68.1929 | 447.3896 | 1627.376 | 68.1929 | 71.1735 | 286.9959 | 2053.7383 | 98.36%
2026 | 1645.4 | 80.9 | 78 | 317 |  | 1632.2368 | 71.2649 | 286.9959 | 358.2608 | 68.617 | 447.9305 | 1632.2368 | 68.617 | 71.2649 | 286.9959 | 2059.1146 | 98.37%
2027 | 1653.3 | 81.8 | 78.2 | 317 |  | 1640.0736 | 71.4476 | 286.9959 | 358.4435 | 69.3803 | 448.9232 | 1640.0736 | 69.3803 | 71.4476 | 286.9959 | 2067.8974 | 98.37%
2028 | 1658.7 | 82.5 | 78.4 | 317 |  | 1645.4304 | 71.6303 | 286.9959 | 358.6263 | 69.974 | 449.738 | 1645.4304 | 69.974 | 71.6303 | 286.9959 | 2074.0307 | 98.37%
2029 | 1665.3 | 83.2 | 78.6 | 317 |  | 1651.9776 | 71.813 | 286.9959 | 358.809 | 70.5677 | 450.5527 | 1651.9776 | 70.5677 | 71.813 | 286.9959 | 2081.3543 | 98.37%
IIS High Growth | [5 empty] | Coincident Paeks | [5 empty] | Contribution to Provincial Peak
| Island Interconnected1,2 | Lab East1,2 | Lab West Utility1,2 | Lab West Industrial1,2 |  | Island Interconnected | Lab West Utility | Lab West Industrial | Lab West Total | Lab East | Lab Total | Island Interconnected | Lab East | Lab West Utility | Lab West Industrial | Total
| MW | MW | MW | MW |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW
2019 | 1664.5 | 83.554 | 77 | 295 |  | 1651.184 | 70.3512 | 267.0782 | 337.4295 | 70.868 | 428.4338 | 1651.184 | 70.868 | 70.3512 | 267.0782 | 2059.4814 | 98.4%
2020 | 1662.3 | 83.6 | 77 | 317 |  | 1649.0016 | 70.3512 | 286.9959 | 357.3472 | 70.907 | 449.3748 | 1649.0016 | 70.907 | 70.3512 | 286.9959 | 2077.2558 | 98.37%
2021 | 1667.4 | 79.1 | 77 | 317 |  | 1654.0608 | 70.3512 | 286.9959 | 357.3472 | 67.0902 | 445.3698 | 1654.0608 | 67.0902 | 70.3512 | 286.9959 | 2078.4982 | 98.38%
2022 | 1670.7 | 79.4 | 77.2 | 317 |  | 1657.3344 | 70.5339 | 286.9959 | 357.5299 | 67.3447 | 445.8285 | 1657.3344 | 67.3447 | 70.5339 | 286.9959 | 2082.209 | 98.38%
2023 | 1682.6 | 79.7 | 77.3 | 317 |  | 1669.1392 | 70.6253 | 286.9959 | 357.6212 | 67.5991 | 446.1914 | 1669.1392 | 67.5991 | 70.6253 | 286.9959 | 2094.3596 | 98.38%
2024 | 1704.5 | 80 | 77.4 | 317 |  | 1690.864 | 70.7167 | 286.9959 | 357.7126 | 67.8536 | 446.5543 | 1690.864 | 67.8536 | 70.7167 | 286.9959 | 2116.4302 | 98.39%
2025 | 1713.3 | 80.4 | 77.9 | 317 |  | 1699.5936 | 71.1735 | 286.9959 | 358.1694 | 68.1929 | 447.3896 | 1699.5936 | 68.1929 | 71.1735 | 286.9959 | 2125.9559 | 98.39%
2026 | 1723.6 | 80.9 | 78 | 317 |  | 1709.8112 | 71.2649 | 286.9959 | 358.2608 | 68.617 | 447.9305 | 1709.8112 | 68.617 | 71.2649 | 286.9959 | 2136.689 | 98.4%
2027 | 1742 | 81.8 | 78.2 | 317 |  | 1728.064 | 71.4476 | 286.9959 | 358.4435 | 69.3803 | 448.9232 | 1728.064 | 69.3803 | 71.4476 | 286.9959 | 2155.8878 | 98.4%
2028 | 1752.2 | 82.5 | 78.4 | 317 |  | 1738.1824 | 71.6303 | 286.9959 | 358.6263 | 69.974 | 449.738 | 1738.1824 | 69.974 | 71.6303 | 286.9959 | 2166.7827 | 98.4%
2029 | 1764.7 | 83.2 | 78.6 | 317 |  | 1750.5824 | 71.813 | 286.9959 | 358.809 | 70.5677 | 450.5527 | 1750.5824 | 70.5677 | 71.813 | 286.9959 | 2179.9591 | 98.41%
LIS Labrador Industrial Growth | [5 empty] | Coincident Paeks | [5 empty] | Contribution to Provincial Peak
| Island Interconnected1,2 | Lab East1,2 | Lab West Utility1,2 | Lab West Industrial1,2 |  | Island Interconnected | Lab West Utility | Lab West Industrial | Lab West Total | Lab East | Lab Total | Island Interconnected | Lab East | Lab West Utility | Lab West Industrial | Total
| MW | MW | MW | MW |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW
2019 | 1665 | 83.554 | 77 | 295 |  | 1651.68 | 70.3512 | 267.0782 | 337.4295 | 70.868 | 428.4338 | 1651.68 | 70.868 | 70.3512 | 267.0782 | 2059.9774 | 98.4%
2020 | 1659 | 83.6 | 77 | 317 |  | 1645.728 | 70.3512 | 286.9959 | 357.3472 | 70.907 | 449.3748 | 1645.728 | 70.907 | 70.3512 | 286.9959 | 2073.9822 | 98.37%
2021 | 1657 | 94.1 | 77 | 317 |  | 1643.744 | 70.3512 | 286.9959 | 357.3472 | 79.8128 | 458.7198 | 1643.744 | 79.8128 | 70.3512 | 286.9959 | 2080.9039 | 98.35%
2022 | 1668 | 94.4 | 77.2 | 317 |  | 1654.656 | 70.5339 | 286.9959 | 357.5299 | 80.0672 | 459.1785 | 1654.656 | 80.0672 | 70.5339 | 286.9959 | 2092.2531 | 98.36%
2023 | 1678 | 94.7 | 77.3 | 317 |  | 1664.576 | 70.6253 | 286.9959 | 357.6212 | 80.3217 | 459.5414 | 1664.576 | 80.3217 | 70.6253 | 286.9959 | 2102.5189 | 98.36%
2024 | 1688 | 95 | 77.4 | 317 |  | 1674.496 | 70.7167 | 286.9959 | 357.7126 | 80.5761 | 459.9043 | 1674.496 | 80.5761 | 70.7167 | 286.9959 | 2112.7848 | 98.36%
2025 | 1695 | 95.4 | 77.9 | 317 |  | 1681.44 | 71.1735 | 286.9959 | 358.1694 | 80.9154 | 460.7396 | 1681.44 | 80.9154 | 71.1735 | 286.9959 | 2120.5249 | 98.37%
2026 | 1704 | 95.9 | 78 | 317 |  | 1690.368 | 71.2649 | 286.9959 | 358.2608 | 81.3395 | 461.2805 | 1690.368 | 81.3395 | 71.2649 | 286.9959 | 2129.9683 | 98.37%
2027 | 1716 | 96.8 | 78.2 | 317 |  | 1702.272 | 71.4476 | 286.9959 | 358.4435 | 82.1029 | 462.2732 | 1702.272 | 82.1029 | 71.4476 | 286.9959 | 2142.8184 | 98.37%
2028 | 1724 | 97.5 | 78.4 | 317 |  | 1710.208 | 71.6303 | 286.9959 | 358.6263 | 82.6966 | 463.088 | 1710.208 | 82.6966 | 71.6303 | 286.9959 | 2151.5308 | 98.37%
2029 | 1735 | 98.2 | 78.6 | 317 |  | 1721.12 | 71.813 | 286.9959 | 358.809 | 83.2903 | 463.9027 | 1721.12 | 83.2903 | 71.813 | 286.9959 | 2163.2193 | 98.38%
LIS Coincidence @ NLIS Peak |  | 95.3%
Coincidence @ LIS Peak |  | 89% | 95.87% | 95%
Coincidence @ NLIS Peak | 99.2% | 84.82% | 91.37% | 90.53%
1Peaks are regionally coincident
2Excludes NLH bulk transmission losses and station service

## 3.2 Energy
3.2 Energy Forecast |  |  |  |  | Return to Table of Contents
Source: | Load forecast from System Planning
Date: | 2019-09-16
| Island Interconnected1,2 | Lab East1,2 | Lab West Utility1,2 | Lab West Industrial1,2 |  | Total
| GWh | GWh | GWh | GWh |  | GWh
2019 | 8082.1503 | 353 | 389.9 | 1962.3 |  | 10787.3503
2020 | 8118.7364 | 355.5 | 430.5 | 2074.3 |  | 10979.0364
2021 | 8108.5861 | 346.4 | 431.6 | 2074.3 |  | 10960.8861
2022 | 8175.2065 | 347.5 | 378.3 | 2074.3 |  | 10975.3065
2023 | 8197.8299 | 348.6 | 378.7 | 2074.3 |  | 10999.4299
2024 | 8249.4487 | 350.3 | 380.7 | 2074.3 |  | 11054.7487
2025 | 8314.5659 | 352.3 | 381.2 | 2074.3 |  | 11122.3659
2026 | 8356.8663 | 355.7 | 381.7 | 2074.3 |  | 11168.5663
2027 | 8402.4637 | 358.4 | 382.2 | 2074.3 |  | 11217.3637
2028 | 8447.8567 | 361 | 382.7 | 2074.3 |  | 11265.8567
2029 | 8495.457 | 363.4 | 383.2 | 2074.3 |  | 11316.357
1. Excludes NLH bulk transmission and station service
2. Based on mitigated rate load case, with rates held to inflation

## 3.3 Sensitivities (hidden)
3.3 Forecast Sensitivities |  |  |  |  | Return to Table of Contents
Source: | Load forecast from System Planning
Date: | 2018-09-10
Peak Forecast
| Island Interconnected |  |  | Lab West Industrial | Lab East Industrial
| High Growth4 | Medium Rate5 | High Rate6 | High Load3 | High Load3
| MW | MW | MW | MW | MW
2018 | 1680 | 1680 | 1680 | 263.88 | 88.444
2019 | 1671 | 1670 | 1671 | 279.7 | 83.554
2020 | 1664 | 1662 | 1662 | 289.6 | 92.479
2021 | 1659 | 1656 | 1655 | 297.52 | 92.772
2022 | 1662 | 1645 | 1641 | 297.52 | 93.044
2023 | 1668 | 1637 | 1628 | 297.52 | 93.313
2024 | 1678 | 1625 | 1611 | 297.52 | 93.856
2025 | 1699 | 1618 | 1597 | 297.52 | 94.379
2026 | 1714 | 1620 | 1574 | 297.52 | 94.902
2027 | 1729 | 1626 | 1557 | 297.52 | 95.422
2028 | 1748 | 1632 | 1558 | 297.52 | 95.942
2029 | 1767 | 1638 | 1559 | 297.52 | 96.443
2030 | 1785 | 1644 | 1561 | 297.52 | 96.925
2031 | 1804 | 1650 | 1562 | 297.52 | 97.407
2032 | 1822 | 1656 | 1563 | 297.52 | 97.887
2033 | 1835 | 1663 | 1564 | 297.52 | 98.367
2034 | 1847 | 1668 | 1565 | 297.52 | 98.828
2035 | 1858 | 1674 | 1567 | 297.52 | 99.272
2036 | 1872 | 1680 | 1567 | 297.52 | 99.715
2037 | 1887 | 1686 | 1568 | 297.52 | 100.157
Energy Forecast
| Island Interconnected |  |  | Lab West Industrial | Lab East Industrial
| High Growth4 | Medium Rate5 | High Rate6 | High Load3 | High Load3
| GWh | GWh | GWh | GWh | GWh
2018 | 8301 | 8301 | 8301 | 1776.14 | 363.6272
2019 | 8308 | 8301 | 8301 | 1899.18 | 378.6048
2020 | 8216 | 8207 | 8206 | 1985.88 | 369.3757
2021 | 8201 | 8119 | 8095 | 2076.984 | 394.1733
2022 | 8189 | 8033 | 7986 | 2098.008 | 395.2593
2023 | 8219 | 7946 | 7875 | 2098.008 | 396.3325
2024 | 8310 | 7864 | 7763 | 2098.008 | 398.3034
2025 | 8388 | 7890 | 7650 | 2098.008 | 400.1871
2026 | 8451 | 7918 | 7544 | 2098.008 | 402.0607
2027 | 8546 | 7950 | 7558 | 2098.008 | 403.9243
2028 | 8663 | 7976 | 7565 | 2098.008 | 405.778
2029 | 8750 | 8003 | 7574 | 2098.008 | 407.547
2030 | 8841 | 8035 | 7587 | 2098.008 | 409.2325
2031 | 8918 | 8065 | 7599 | 2098.008 | 410.9099
2032 | 8961 | 8097 | 7613 | 2098.008 | 412.5791
2033 | 8999 | 8127 | 7625 | 2098.008 | 414.2403
2034 | 9043 | 8145 | 7627 | 2098.008 | 415.8206
2035 | 9126 | 8174 | 7638 | 2098.008 | 417.321
2036 | 9208 | 8203 | 7649 | 2098.008 | 418.815
2037 | 9268 | 8230 | 7660 | 2098.008 | 420.3028
Assumptions:
1. Peaks are non-coincident
2. Excludes NLH bulk transmission and station service
3. High Labrador Load is the combination of Tacora Mine and DND Boiler
4. High Island Growth Based on 17 cent load case, with rates held to inflation, and high oil price
5. Medium Island Rate Case Based on 22 cent load case, with rates held to inflation
6. High Island Rate Case Based on 24 cent load case, with rates held to inflation

## 3.2A Energy Sensitivities
3.2A Energy Forecast Sensitivities |  |  |  |  | Return to Table of Contents
Source: | Load forecast from System Planning
Date: | 2019-09-16
IIS Low Growth
| Island Interconnected1 | Lab East1 | Lab West Utility1 | Lab West Industrial1 |  | Total
| GWh | GWh | GWh | GWh |  | GWh
2019 | 8082 | 353 | 389.9 | 1962.3 |  | 10787.2
2020 | 8130 | 355.5 | 430.5 | 2074.3 |  | 10990.3
2021 | 8025 | 346.4 | 431.6 | 2074.3 |  | 10877.3
2022 | 8010 | 347.5 | 378.3 | 2074.3 |  | 10810.1
2023 | 7971 | 348.6 | 378.7 | 2074.3 |  | 10772.6
2024 | 7961 | 350.3 | 380.7 | 2074.3 |  | 10766.3
2025 | 8013 | 352.3 | 381.2 | 2074.3 |  | 10820.8
2026 | 8042 | 355.7 | 381.7 | 2074.3 |  | 10853.7
2027 | 8075 | 358.4 | 382.2 | 2074.3 |  | 10889.9
2028 | 8109 | 361 | 382.7 | 2074.3 |  | 10927
2029 | 8145 | 363.4 | 383.2 | 2074.3 |  | 10965.9
IIS High Growth
| Island Interconnected1 | Lab East1 | Lab West Utility1 | Lab West Industrial1 |  | Total
| GWh | GWh | GWh | GWh |  | GWh
2019 | 8082 | 353 | 389.9 | 1962.3 |  | 10787.2
2020 | 8140 | 355.5 | 430.5 | 2074.3 |  | 11000.3
2021 | 8136 | 346.4 | 431.6 | 2074.3 |  | 10988.3
2022 | 8185 | 347.5 | 378.3 | 2074.3 |  | 10985.1
2023 | 8246 | 348.6 | 378.7 | 2074.3 |  | 11047.6
2024 | 8368 | 350.3 | 380.7 | 2074.3 |  | 11173.3
2025 | 8448 | 352.3 | 381.2 | 2074.3 |  | 11255.8
2026 | 8492 | 355.7 | 381.7 | 2074.3 |  | 11303.7
2027 | 8574 | 358.4 | 382.2 | 2074.3 |  | 11388.9
2028 | 8629 | 361 | 382.7 | 2074.3 |  | 11447
2029 | 8720 | 363.4 | 383.2 | 2074.3 |  | 11540.9
LIS Labrador Industrial Growth
| Island Interconnected1 | Lab East1 | Lab West Utility1 | Lab West Industrial1 |  | Total
| GWh | GWh | GWh | GWh |  | GWh
2019 | 8082.1503 | 353 | 389.9 | 1962.3 |  | 10787.3503
2020 | 8118.7364 | 374 | 430.5 | 2074.3 |  | 10997.5364
2021 | 8108.5861 | 408 | 431.6 | 2074.3 |  | 11022.4861
2022 | 8175.2065 | 409.1 | 378.3 | 2074.3 |  | 11036.9065
2023 | 8197.8299 | 410.2 | 378.7 | 2074.3 |  | 11061.0299
2024 | 8249.4487 | 411.9 | 380.7 | 2074.3 |  | 11116.3487
2025 | 8314.5659 | 413.9 | 381.2 | 2074.3 |  | 11183.9659
2026 | 8356.8663 | 417.3 | 381.7 | 2074.3 |  | 11230.1663
2027 | 8402.4637 | 420 | 382.2 | 2074.3 |  | 11278.9637
2028 | 8447.8567 | 422.7 | 382.7 | 2074.3 |  | 11327.5567
2029 | 8495.457 | 425.1 | 383.2 | 2074.3 |  | 11378.057
1. Excludes NLH bulk transmission and station service

## 4.1 Firm Capacity
4.1 Firm Capacity |  |  |  | Return to Table of Contents
Source: | (T-093) Island Generation Supply Gross Continuous Unit Ratings - ECC (Except where noted)
Date: | 2019-10-11
| Rated Capacity | Firm Capacity | Firm Capacity @ 2026 Test Year
Unit | MW | MW | MW
Island Generation Capacity
Bay D'Espoir - Unit 1 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 2 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 3 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 4 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 5 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 6 | 76.5 | 76.5 | 76.5
Bay D'Espoir - Unit 7 | 154.4 | 154.4 | 154.4
Cat Arm - Unit 1 | 68.5 | 67 | 67
Cat Arm - Unit 2 | 68.5 | 67 | 67
Granite Canal | 40 | 40 | 40
Hinds Lake | 75 | 75 | 75
Paradise River | 8 | 8 | 8
Upper Salmon | 84 | 84 | 84
Holyrood Thermal - Unit 1 | 170 | 170 | - | Note 8
Holyrood Thermal - Unit 2 | 170 | 170 | - | Note 8
Holyrood Thermal - Unit 3 | 150 | 150 | - | Note 8
Newfoundland Power - Avalon Hydro | 94.2 | 43.946 | 43.946 | Note 1
Newfoundland Power - Off-Avalon Hydro |  | 27.6 | 27.6 | Note 1
Newfoundland Power - Thermal | 39 | 39 | 39
Hardwoods GT | 50 | 50 | -
Hawkes Bay Diesels | 5 | 5 | 5
Holyrood Diesels | 12 | 8.5 | 8.5 | Note 2
Holyrood GT | 123.5 | 123.5 | 123.5
St. Anthony Diesels | 9.7 | 9.7 | 9.7
Stephenville GT | 50 | 50 | -
Deer Lake - Units | 104 | 104 | 104
Bishop's Falls - Unit 1-6 | 14.4 | 9.6306 | 9.66
Bishop's Falls - Unit 7 | 2.5 | 1.672 | 1.67
Grand Falls - Beeton | 31 | 20.7325 | 20.73
Grand Falls - Unit 4 | 29.5 | 19.7293 | 19.73
Grand Falls - Unit 5/6 | 8.6 | 5.7516 | 5.76
Grand Falls - Unit 7 | 3.9 | 2.6083 | 2.61
Grand Falls - Unit 8 | 4.3 | 2.8758 | 2.88
Corner Brook CoGen | 15.3 | 8 | -
Fermeuse Wind | 27 | 6 | 6 | Note 3
Rattle Brook | 4 | - | -
St. Lawrence Wind | 27 | 6 | 6 | Note 3
Star Lake | 18 | 18 | 18
Total Island Generation Capacity | 2120.3 | 2006.646 | 1408.686
Muskrat Falls Generation Capacity
Muskrat Falls - Unit 1 | 204.65 | 196.15 | 196.15 | Note 6,7
Muskrat Falls - Unit 2 | 204.65 | 196.15 | 196.15 | Note 6,7
Muskrat Falls - Unit 3 | 204.65 | 196.15 | 196.15 | Note 6,7
Muskrat Falls - Unit 4 | 204.65 | 196.15 | 196.15 | Note 6,7
Labrador Generation Capacity | 818.6 | 784.6 | 784.6
Labrador Generation Capacity
Happy Valley CT | 25 | 25 | 25
Recall Block | 306.9 | 306.9 | 306.9
TwinCo Block | 225 | 225 | 225
Labrador Generation Capacity | 556.9 | 556.9 | 556.9
Capacity Assistance Capacity
CBPP Capacity Assistance | 100.4 | 100.4 | -
Vale Capacity Assistance | 7.6 | 7.6 | -
NP Capacity Assistance | 9.9 | 9.9 | 9.9
Capacity Assistance Capacity | 117.9 | 117.9 | 9.9
LIL Capacity | 900 | 826.4 | 826.4 | Note 4
ML Capacity | 500 | 158 | 158 | Note 5
Island Generation Capacity |  |  | 1418.586
Island Capacity |  |  | 2086.986
Provincial Generation Capacity |  |  | 2750.186
Provincial Capacity |  |  | 2602.086
1Based on analysis of NP generation requests
2Based on environmental restrictions
3Based on ELCC study
4LIL Capacity based on available labrador capacity less transmission losses, corona losses and soldiers pond station serivice
5Based on Emera Block Deliveries adjusted for losses over LTA, LIL and Island Transmission. Capacity measured at Bottom Brook.
6Based on assumed winter capacity of 790 MW
7Derated for 5.4 MW of Station Service Load and Corona Losses at Muskrat Falls
8Modelled as net generation in Production and Expansion models

## 4.2 Outage Rates
4.2 FOR and Maintenance |  |  |  | Return to Table of Contents
Source: | Forced Outage Methodology (Except Where Noted)
Date: | 2019-09-16
| ST Forced Outage Rate | LT Forced Outage Rate | Maintenance Rate
Unit | % | % | Weeks
Island
Bay D'Espoir - Unit 1 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 2 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 3 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 4 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 5 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 6 | 2.77 | 1.92 | 3
Bay D'Espoir - Unit 7 | 2.77 | 1.92 | 3
Cat Arm - Unit 1 | 2.77 | 1.92 | 3
Cat Arm - Unit 2 | 2.77 | 1.92 | 3
Granite Canal | 2.77 | 1.92 | 3
Hinds Lake | 2.77 | 1.92 | 3
Paradise River | 2.77 | 1.92 | 2
Upper Salmon | 2.77 | 1.92 | 3
Holyrood Thermal - Unit 1 | 15 | - | - | Note 1,4
Holyrood Thermal - Unit 2 | 15 | - | - | Note 1,4
Holyrood Thermal - Unit 3 | 15 | - | - | Note 1,4
Newfoundland Power - Avalon Hydro | 5.72 | 5.72 | 2
Newfoundland Power - Off-Avalon Hydro | 5.72 | 5.72 | 2
Newfoundland Power - Thermal | 13.55 | 13.55 | 4
Hardwoods CT | 30 | - | 4
Hawkes Bay Diesels | 6.23 | 6.23 | 4
Holyrood CT | 1.68 | 1.68 | 4
Holyrood Diesels | 6.23 | 6.23 | 4
St. Anthony Diesels | 6.23 | 6.23 | 4
Stephenville CT | 30 | - | 4
Deer Lake - Units | 5.72 | 5.72 | 3
Bishop's Falls - Unit 1-6 | 2.77 | 1.92 | 3
Bishop's Falls - Unit 7 | 2.77 | 1.92 | 3
Grand Falls - Beeton | 2.77 | 1.92 | 3
Grand Falls - Unit 4 | 2.77 | 1.92 | 3
Grand Falls - Unit 5/6 | 2.77 | 1.92 | 3
Grand Falls - Unit 7 | 2.77 | 1.92 | 3
Grand Falls - Unit 8 | 2.77 | 1.92 | 3
Corner Brook CoGen | 15.8 | - | 2
Fermuse Wind | - | - | - | Note 2
Rattle Brook | 5.72 | 5.72 | 2
St. Lawrence Wind | - | - | - | Note 2
Star Lake | 2.77 | 1.92 | 3
Muskrat Falls
Muskrat Falls - Unit 1 | 2.77 | 1.92 | 3
Muskrat Falls - Unit 2 | 2.77 | 1.92 | 3
Muskrat Falls - Unit 3 | 2.77 | 1.92 | 3
Muskrat Falls - Unit 4 | 2.77 | 1.92 | 3
Labrador
Happy Valley CT | 9.77 | 9.7 | 4
Recall Block | - | - | - | Note 3
TwinCo Block | - | - | - | Note 3
Transmission
Labrador Island Link A | See 4.3 | 0.556 | -
Labrador Island Link B | See 4.3 | 0.556 | -
Bipole | See 4.3 | 0.011416 | -
1Maintenance assumed to be completed during downtime in the summer
2Forced outage rate and maintenance included in probability distribution
3Assumed to be always available
415% FOR for Holyrood is the base case. FORs of 18% and 20% are examined as a part of the Near Term Analysis

## 4.3 LIL Near Term Assumptions
4.3 LIL Near Term Assumptions |  | Return to Table of Contents
Source: | Muskrat Falls Project Assumptions
Date: | 2018-08-18
Monopole Forced Outage Rate
Start Date | %
2020-01-01 | 10
2021-01-01 | 2.5
2022-01-01 | 1
2023-01-01 | 0.556
Capacity
Start Date | MW
2020-01-01 | 0
2020-06-01 | 225
2020-07-01 | 675
2020-08-01 | 900

## 4.4 Loss Equations
4.4 Loss Equations |  |  | Return to Table of Contents
Source: | TP-TN-073 (Except as noted)
Date: | 2019-10-16
Line | Constant | Linear | Quadratic
Avalon Load (Long Term) | -3.94 | 0.020195 | 0 | Note 1
Avalon Load (Near Term Production) | -4.94 | 0.020195 | 0 | Note 2
Avalon Load (Near Term Reliability) | 19.06 | 0.020195 | 0 | Note 3
Off-Avalon Load | -4.3835 | 0.020195 | 0
Avalon -> Off-Avalon | 0 | 0.008209 | 0.000156
CF -> Lab East | 0 | -0.0032276 | 0.00029269 | Note 4
CF -> Lab West | -5.8782 | 0.08174 | 0
CF Load -> MF | 0.0291 | -0.0012 | 5e-05
CFLCo -> Quebec Market | 0 | 0 | 0
Labrador Island Link | 3.19 | -0.0076 | 0.00016 | Note 5,6
Maritime Link | 1.417 | 0.019042 | 0.0002874 | Note 7,8
1Includes 1 MW of HRD station service losses
2For production plan Holyrood is modelled as net generation
3Includes 24 MW of HRD station service losses
4Updated to include MF - HVGB interconnection
5Includes 6.9 MW of SOP converter station losses
6Loss equations for each pole
7Includes 0.8 MW of BBK converter station losses
8Combined Equation for Line and Island Losses

## 4.5 Station Service Loads
4.5 Station Service Loads |  |  | Return to Table of Contents
Source: | As noted
Date: | 2019-10-23
Line | Node | Load (MW)
Holyrood Station Service (3 Units Operating) | Avalon Gen-> Avalon Load | 24 | Note 1
Holyrood Station Service (Synchronous Condenser Mode) | Avalon Gen-> Avalon Load | 1 | Note 2
Soldiers Pond Transformer Losses | Labrador Island Link A/B | 0.3 | Note 3
Soldiers Pond Synchronous Condenser Losses | Labrador Island Link A/B | 1.6 | Note 3
Soldiers Pond Station Service (Synchronous Condensers) | Labrador Island Link A/B | 2 | Note 3
Soldiers Pond Station Service | Labrador Island Link A/B | 3 | Note 3
Total Soldiers Pond |  | 6.9
Muskrat Falls Corona Losses | - | 2.4 | Note 3,4
Muskrat Falls Station Service Losses | - | 3 | Note 3,4
Total Muskrat Falls |  | 5.4
Bottom Brook | Maritime Link | 0.8 | Note 5
1Based on Hydro's planning assumptions
2Based on email from J. Vincent June 7, 2019
3Based on TP-TN-036
4Modelled as a subtraction from Muskrat Falls capacity
5Based on email from R. Collett Sept 23, 2019

## 5.1 Daily Energy Limitations
5.1 Daily Energy Limitations | [7 empty] | Return to Table of Contents
Source: | As Noted
Date: | 2019-10-16
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Paradise River1 | 0.10323 | 0.1 | 0.11613 | 0.15 | 0.12258 | 0.063333 | 0.041935 | 0.048387 | 0.06 | 0.096774 | 0.12667 | 0.12258
NP Hydro - Avalon2 | 0.69937 | 0.79123 | 0.75149 | 0.98815 | 0.86176 | 0.62336 | 0.4355 | 0.34492 | 0.42858 | 0.37188 | 0.43581 | 0.61915
NP Hydro - Off-Avalon2 | 0.28721 | 0.37279 | 0.45736 | 0.55884 | 0.65805 | 0.52083 | 0.48531 | 0.37386 | 0.33872 | 0.33653 | 0.38378 | 0.33932
Rattle Brook1 | 0.022581 | 0.017857 | 0.019355 | 0.053333 | 0.083871 | 0.053333 | 0.025806 | 0.025806 | 0.04 | 0.051613 | 0.06 | 0.035484
Muskrat Falls3,4 | 14.3657 | 15.0212 | 13.3527 | 12.8462 | 12.3704 | 14.5273 | 14.7033 | 14.3043 | 13.2903 | 11.2347 | 12.9096 | 13.4755
1Source: 2017 GRA Evidence R5, Schedule 3-IV
2Source: Historical NP Generation 2015-2017
3Source: Vista run. See email From Joanna Barnard July 17, 2019
4Daily energy limitation used only in the expansion/production model

## 5.2 Monthly Energy Limitations
5.2 Monthly Hydro Limitations | [7 empty] | Return to Table of Contents
Source: | As Noted
Date: | 2019-10-16
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Deer Lake1 | 63.6986 | 57.5343 | 63.6986 | 61.6438 | 63.6986 | 61.6438 | 63.6986 | 63.6986 | 61.6438 | 63.6986 | 61.6438 | 63.6986 | 750
Exploits2 | 54 | 48.7 | 53.7 | 55.7 | 59 | 48.3 | 52.8 | 54.8 | 50 | 39.5 | 45.4 | 53 | 614.9
Star Lake2 | 12.5 | 11.3 | 12.5 | 12.4 | 12.8 | 12 | 13 | 13 | 6.5 | 12.9 | 11.5 | 11.7 | 142.1
Island Pond3 | 19.5 | 18.3 | 19.2 | 20.8 | 19.2 | 13.9 | 12.1 | 14.1 | 11 | 16.3 | 21.8 | 21.8 | 208
Portland Creek4 | 8 | 7.1 | 8.2 | 12.9 | 15.9 | 15.8 | 16.2 | 14.1 | 12 | 11.7 | 11.3 | 8.4 | 141.6
Round Pond5 | 15.2 | 13.8 | 15.2 | 12.5 | 9.2 | 9.1 | 8.5 | 8.7 | 6.7 | 9.7 | 12.2 | 15.2 | 136
Exploits Expansion6 | 36.1 | 32.6 | 35.7 | 37.8 | 38.4 | 31.2 | 35.6 | 35.4 | 31.4 | 25.3 | 31.5 | 37 | 408
1Based on an average annual generation of 750 GWh and a constant generation profile
2Source: 2017 GRA Evidence R5, Schedule 3-IV
3Based on annual generation of 208 GWh from original report and Granite Canal monthly profile
4Based on monthly generation profile from original report
5Based on annual generation of 136 GWh from original report and Upper Salmon monthly profile
6Based on annual generation of 408 GWh from original report and Exploits monthly profile

## 6.1 Additions Per Year
6.1 Specific Additions Per Year | [5 empty] | Return to Table of Contents
Source: | Various
Date: | 2019-09-17
Year | Month | Day | Plant Name | Firm Capacity
2019 | 12 | 9 | Muskrat Falls Unit 1 | 206 MW | Note 1
2020 | 2 | 21 | Muskrat Falls Unit 2 | 206 MW | Note 1
2020 | 5 | 6 | Muskrat Falls Unit 3 | 206 MW | Note 1
2020 | 7 | 20 | Muskrat Falls Unit 4 | 206 MW | Note 1
2020 | 7 | 1 | Emera | 158 MW | Note 2
2020 | 7 | 1 | Supplemental | 0 MW | Note 3
1Based on corporate assumptions (M7 Forecast)
2Firm capacity at Bottom Brook. Based on contracted amount at Muskrat Falls less transmission losses on LTA, LIL and Island Transmission
3Not modelled in the reliability model as it is a non-firm contract

## 6.2 Retirements Per Year
6.2 Specific Retirements Per Year | [6 empty] | Return to Table of Contents
Source: | Various
Date: | 2019-09-17
Year | Month | Day | Plant Name | Firm Capacity | Units
2023 | 2 | 1 | CBPP Cogen | 8 | MW | Note 1
2021 | 6 | 1 | Holyrood Thermal | 490 | MW | Note 2
2021 | 6 | 1 | Stephenville CT | 50 | MW
2021 | 6 | 1 | Hardwoods CT | 50 | MW
2029 | 5 | 31 | St. Lawrence Wind | 6 | MW | Note 1
2029 | 6 | 30 | Fermuse Wind | 6 | MW | Note 1
2022 | 5 | 1 | CBPP Capacity Assistance | 100.4 | MW | Note 3
2025 | 7 | 1 | Supplemental Block | 0 | MW | Note 4
2023 | 10 | 23 | Rattle Brook | 0 | MW | Note 5
1Based on Email From J Bernard - August 21, 2018
2Based on corporate assumptions (M7 Forecast)
3Based on P.U. 40(2018)

## 7.1 Thermal Expansion
7.1 Thermal Expansion | [7 empty] | Return to Table of Contents
Source: | Engineering Services (M. Khalifa)
Date: | 2019-10-29
Construction Costs1
Plant Name | Firm Capacity | Min Capacity | Heat Rate @ Max | Heat Rate @ Min | Year 1 | Year 2 | Year 3 | Fixed O&M1 | Variable O&M1 | Start Cost | Forced Outage Rate2 | Maintenance Rate
| MW | MW | GJ/MWh | GJ/MWh | $/kW | $/kW | $/kW | $/kW/year | $/MWh | $/start | % | weeks/year
Bremigans Pond 1x66 MW CT | 58.5 | 29 | 8.813 | 10.46 | 1008.5811 | 1873.0791 | 0 | 10.3 | 10.6 | 0 | 5.03 | 4
Sugarloaf Pond 2x66 MW CT | 117 | 29 | 8.813 | 10.46 | 890.2812 | 1653.3793 | 0 | 10 | 8.5 | 0 | 5.03 | 4
Paddy's Pond 4x66 MW CT | 234 | 29 | 8.813 | 10.46 | 852.0859 | 1278.1288 | 710.0716 | 10 | 7.13 | 0 | 5.03 | 4
170 MW CCCT | 167.2 | 81.6 | 7.264 | 7.31 | 993.773 | 1490.6595 | 828.1442 | 10 | 7.13 | 0 | 5.03 | 4
1All costs are in 2018 dollars
2Based on a 5 year average DAUFOP of units between 0-10 years old

## 7.2 Hydro Expansion
7.2 Hydro Expansion | [7 empty] | Return to Table of Contents
Source: | Engineering Services (M. Leonard)
Date: | 2019-10-29
Construction Costs
Plant Name | Firm Capacity | Min Capacity | Firm Annual energy | Average Annual Energy | Year 1 | Year 2 | Year 3 | Year 4 | Fixed O&M1 | Variable O&M1 | Forced Outage Rate | Maintenance Rate
| MW | MW | GWh | GWh | $/kW | $/kW | $/kW | $/kW | $/kW/year | $/MWh | % | weeks/year
Portland Creek | 23 | 2.3 | 99 | 142 | 434.8385 | 2759.2893 | 8168.589 | 20.4898 | 117.5368 | 5.7 | 1.92 | 3
Island Pond | 36 | 7.2 | 172 | 186 | 255.8972 | 2848.8378 | 4150.9696 | 4067.1802 | 91.4492 | 5.7 | 1.92 | 3
Round Pond | 18 | 3.6 | 108 | 139 | 1049.616 | 7148.9595 | 5535.9669 | 39.946 | 72.3618 | 5.7 | 1.92 | 3
Exploits | 66 | 4.4 | 310 | 422 | 446.9457 | 3284.079 | 4809.524 | 1175.6614 | 81.69 | 5.7 | 1.92 | 3
BDE Unit 8 | 154.4 | - | - | - | 169.77 | 733.74 | 774.85 | 740.03 | 17.5259 | 5.7 | 1.92 | 3
Cat Arm Unit 3 | 68.2 | 13.6 | - | - | 741.6521 | 3205.3738 | 3384.9762 | 3232.8424 | 74.9891 | 5.7 | 1.92 | 3

## 7.3 Renewable Expansion
7.3 Renewable Expansion | [6 empty] | Return to Table of Contents
Source: | Engineering Services (A. Guilbeault)
Date: | 2019-10-29
Construction Costs
Plant Name | Rated Capacity | Firm Capacity | Average Annual Energy | Year 1 | Year 2 | Year 3 | Year 4 | Fixed O&M1 | Variable O&M1 | Forced Outage Rate | Maintenance Rate
| MW | MW | GWh | k$ | k$ | k$ | k$ | $/kW/year | $/MWh | % | weeks/year
Wind 12 MW | 12.6 | 2.8 | 44 | 27.9 | 224.41 | 2847.22 | 0 | 70 | 0 | 5 | 1
Wind 100 MW | 100.8 | 22.2 | 353 | 7.4 | 11.1 | 524.1 | 1302.9 | 60 | 0 | 5 | 1
Solar | 7.49 | 0 | 12.52 | 27.9 | 224.41 | 2847.22 | 0 | 22 | 1 | 0.5 | 1

## 7.4 Battery Expansion
7.4 Battery Expansion | [5 empty] | Return to Table of Contents
Source: | Engineering Services (A. Guilbeault)
Date: | 2019-10-29
Construction Costs
Plant Name | Rated Capacity | Firm Capacity | Year 1 | Year 2 | Year 3 | Fixed O&M1 | Variable O&M1 | Forced Outage Rate | Maintenance Rate | Efficiency | Storage Capacity
| MW | MW | k$ | k$ | k$ | $/kW/year | $/MWh | % | weeks/year | % | MWh
Battery | 20 | 20 | 2.4215 | 347.089 | 1427.5873 | 4.95 | 46.19 | 0.5 | 1 | 85% | 40

## Template
1.1 Economic Inputs |  | Return to Table of Contents
Source: | Nalcor Energy Corporate Assumptions
Date: